## DHQ
Annex-1 | [13 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of April-2020
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2020 |  |  |  | Reliability for cumulative period from Apr-20 to Apr-20
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 9:40 | 9:40 | 521:49 | 346:04 | 867:53 | 867:53 | 877:33 | 28:18 | 96.1116 | 96.0683 | 877:33 | 28:18 | 96.1116 | 96.0683
2 | Gadag | 16 | 16 | 0:00 | 0:00 | 90:46 | 73:40 | 164:26 | 164:26 | 164:26 | 10:17 | 98.5726 | 98.5726 | 164:26 | 10:17 | 98.5726 | 98.5726
3 | Haveri | 7 | 7 | 11:05 | 11:05 | 41:25 | 31:25 | 72:50 | 72:50 | 83:55 | 11:59 | 98.5549 | 98.335 | 83:55 | 11:59 | 98.5549 | 98.335
4 | Karwar | 10 | 10 | 7:30 | 7:30 | 73:05 | 65:00 | 138:05 | 138:05 | 145:35 | 14:34 | 98.0822 | 97.978 | 145:35 | 14:34 | 98.0822 | 97.978
5 | Belagavi | 68 | 68 | 113:41 | 113:41 | 304:17 | 168:22 | 472:39 | 472:39 | 586:20 | 8:37 | 99.0346 | 98.8024 | 586:20 | 8:37 | 99.0346 | 98.8024
6 | Vijayapur | 35 | 35 | 20:00 | 20:00 | 118:00 | 418:54 | 536:54 | 536:54 | 556:54 | 15:55 | 97.8694 | 97.7901 | 556:54 | 15:55 | 97.8694 | 97.7901
7 | Bagalkot | 11 | 11 | 26:04 | 26:04 | 110:52 | 78:55 | 189:47 | 189:47 | 215:51 | 19:37 | 97.6037 | 97.2746 | 215:51 | 19:37 | 97.6037 | 97.2746
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of May-2020
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2020 |  |  |  | Reliability for cumulative period from Apr-20 to May-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 0:00 | 9:40 | 655:13 | 439:07 | 1094:20 | 1962:13 | 1094:20 | 35:18 | 95.2552 | 95.2552 | 1971:53 | 63:37 | 95.6764 | 95.6551
2 | Gadag | 16 | 16 | 0:00 | 0:00 | 97:36 | 42:01 | 139:37 | 304:03 | 139:37 | 8:44 | 98.8271 | 98.8271 | 304:03 | 19:00 | 98.702 | 98.702
3 | Haveri | 7 | 7 | 0:00 | 11:05 | 20:30 | 30:25 | 50:55 | 123:45 | 50:55 | 7:16 | 99.0223 | 99.0223 | 134:50 | 19:16 | 98.7924 | 98.6843
4 | Karwar | 10 | 10 | 42:48 | 50:18 | 93:12 | 79:25 | 172:37 | 310:42 | 215:25 | 21:32 | 97.6799 | 97.1046 | 361:00 | 36:06 | 97.8777 | 97.5342
5 | Belagavi | 67 | 67 | 16:59 | 130:40 | 158:22 | 169:30 | 327:52 | 800:31 | 344:51 | 5:09 | 99.3423 | 99.3082 | 931:11 | 13:54 | 99.1839 | 99.0507
6 | Vijayapur | 35 | 35 | 226:48 | 246:48 | 155:37 | 452:57 | 608:34 | 1145:28 | 835:22 | 23:52 | 97.663 | 96.792 | 1392:16 | 39:47 | 97.7645 | 97.2829
7 | Bagalkot | 11 | 11 | 41:44 | 67:48 | 148:37 | 77:49 | 226:26 | 416:13 | 268:10 | 24:23 | 97.2332 | 96.7233 | 484:01 | 44:00 | 97.4154 | 96.9944
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of June-2020
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2020 |  |  |  | Reliability for cumulative period from Apr-20 to June-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 4:00 | 13:40 | 584:32 | 152:55 | 737:27 | 2699:40 | 741:27 | 23:55 | 96.696 | 96.6781 | 2713:20 | 87:32 | 96.0125 | 95.9924
2 | Gadag | 16 | 16 | 0:00 | 0:00 | 115:24 | 54:51 | 170:15 | 474:18 | 170:15 | 10:38 | 98.5221 | 98.5221 | 474:18 | 29:39 | 98.6427 | 98.6427
3 | Haveri | 7 | 7 | 0:00 | 11:05 | 89:55 | 31:15 | 121:10 | 244:55 | 121:10 | 17:19 | 97.5959 | 97.5959 | 256:00 | 36:34 | 98.398 | 98.3255
4 | Karwar | 10 | 10 | 8:42 | 59:00 | 113:55 | 122:40 | 236:35 | 547:17 | 245:17 | 24:32 | 96.7141 | 96.5933 | 606:17 | 60:38 | 97.4941 | 97.224
5 | Belagavi | 68 | 68 | 149:47 | 280:27 | 749:16 | 640:01 | 1389:17 | 2189:48 | 1539:04 | 22:38 | 97.1624 | 96.8565 | 2470:15 | 36:20 | 98.5255 | 98.3367
6 | Vijayapur | 35 | 35 | 66:29 | 313:17 | 173:57 | 290:20 | 464:17 | 1609:45 | 530:46 | 15:10 | 98.1576 | 97.8938 | 1923:02 | 54:57 | 97.8941 | 97.4843
7 | Bagalkot | 11 | 11 | 48:53 | 116:41 | 118:09 | 77:56 | 196:05 | 612:18 | 244:58 | 22:16 | 97.5242 | 96.907 | 728:59 | 66:16 | 97.4513 | 96.9656
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of JULY-2020
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2020 |  |  |  | Reliability for cumulative period from Apr-20 to July-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 0:00 | 13:40 | 517:18 | 135:02 | 652:20 | 3352:00 | 652:20 | 21:03 | 97.1716 | 97.1716 | 3365:40 | 108:34 | 96.3071 | 96.292
2 | Gadag | 16 | 16 | 0:00 | 0:00 | 83:15 | 33:59 | 117:14 | 591:32 | 117:14 | 7:20 | 99.0152 | 99.0152 | 591:32 | 36:58 | 98.7373 | 98.7373
3 | Haveri | 7 | 7 | 0:00 | 11:05 | 89:55 | 31:15 | 121:10 | 366:05 | 121:10 | 17:19 | 97.6735 | 97.6735 | 377:10 | 53:53 | 98.2139 | 98.1598
4 | Karwar | 10 | 10 | 11:10 | 70:10 | 94:11 | 77:15 | 171:26 | 718:43 | 182:36 | 18:16 | 97.6958 | 97.5457 | 788:53 | 78:53 | 97.5454 | 97.3057
5 | Belagavi | 68 | 68 | 125:02 | 405:29 | 469:44 | 152:45 | 622:29 | 2812:17 | 747:31 | 11:00 | 98.7696 | 98.5225 | 3217:46 | 47:19 | 98.5875 | 98.3839
6 | Vijayapur | 35 | 35 | 0:38 | 313:55 | 203:16 | 207:29 | 410:45 | 2020:30 | 411:23 | 11:45 | 98.4226 | 98.4202 | 2334:25 | 66:42 | 98.0284 | 97.7221
7 | Bagalkot | 11 | 11 | 0:00 | 116:41 | 76:09 | 53:32 | 129:41 | 741:59 | 129:41 | 11:47 | 98.4154 | 98.4154 | 858:40 | 78:04 | 97.6963 | 97.334
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of AUGUST-2020
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of August-2020 |  |  |  | Reliability for cumulative period from Apr-20 to August-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 0:00 | 13:40 | 548:21 | 271:00 | 819:21 | 4171:21 | 819:21 | 26:26 | 96.4475 | 96.4475 | 4185:01 | 135:00 | 96.3355 | 96.3235
2 | Gadag | 16 | 16 | 0:00 | 0:00 | 89:32 | 51:44 | 141:16 | 732:48 | 141:16 | 8:50 | 98.8133 | 98.8133 | 732:48 | 45:48 | 98.7527 | 98.7527
3 | Haveri | 7 | 7 | 3:50 | 14:55 | 227:22 | 34:05 | 261:27 | 627:32 | 265:17 | 37:54 | 94.9798 | 94.9062 | 642:27 | 91:47 | 97.5586 | 97.5006
4 | Karwar | 10 | 10 | 40:34 | 110:44 | 95:24 | 164:45 | 260:09 | 978:52 | 300:43 | 30:04 | 96.5034 | 95.9581 | 1089:36 | 108:58 | 97.3342 | 97.0327
5 | Belagavi | 68 | 68 | 135:49 | 541:18 | 642:41 | 470:35 | 1113:16 | 3925:33 | 1249:05 | 18:22 | 97.7995 | 97.5311 | 4466:51 | 65:41 | 98.4279 | 98.2111
6 | Vijayapur | 36 | 36 | 17:36 | 331:31 | 275:16 | 849:47 | 1125:03 | 3145:33 | 1142:39 | 31:44 | 95.7995 | 95.7338 | 3477:04 | 96:35 | 97.6205 | 97.3697
7 | Bagalkot | 11 | 11 | 11:42 | 128:23 | 115:44 | 45:53 | 161:37 | 903:36 | 173:19 | 15:45 | 98.0252 | 97.8822 | 1031:59 | 93:49 | 97.7629 | 97.4451
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of SEPTEMBER-2020
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of September-2020 |  |  |  | Reliability for cumulative period from Apr-20 to September-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 0:00 | 13:40 | 526:58 | 160:15 | 687:13 | 4858:34 | 687:13 | 22:10 | 96.9211 | 96.9211 | 4872:14 | 157:10 | 96.4315 | 96.4215
2 | Gadag | 16 | 16 | 22:26 | 22:26 | 94:30 | 39:30 | 134:00 | 866:48 | 156:26 | 9:47 | 98.8368 | 98.6421 | 889:14 | 55:35 | 98.7665 | 98.7346
3 | Haveri | 7 | 7 | 0:00 | 14:55 | 24:50 | 17:31 | 42:21 | 669:53 | 42:21 | 6:03 | 99.1597 | 99.1597 | 684:48 | 97:50 | 97.8211 | 97.7726
4 | Karwar | 10 | 10 | 40:12 | 150:56 | 81:39 | 91:46 | 173:25 | 1152:17 | 213:37 | 21:22 | 97.5914 | 97.0331 | 1303:13 | 130:19 | 97.3764 | 97.0327
5 | Belagavi | 69 | 69 | 192:00 | 733:18 | 541:48 | 166:33 | 708:20 | 4633:53 | 900:21 | 13:03 | 98.5742 | 98.1877 | 5367:12 | 77:47 | 98.4709 | 98.2289
6 | Vijayapur | 36 | 36 | 65:53 | 397:24 | 233:22 | 981:09 | 1214:31 | 4360:04 | 1280:24 | 35:34 | 95.3144 | 95.0602 | 4757:28 | 132:09 | 97.2424 | 96.9911
7 | Bagalkot | 11 | 11 | 31:37 | 160:00 | 105:39 | 51:26 | 157:05 | 1060:41 | 188:42 | 17:09 | 98.0166 | 97.6174 | 1220:41 | 110:58 | 97.8045 | 97.4733
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of OCTOBER-2020
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of October-2020 |  |  |  | Reliability for cumulative period from Apr-20 to October-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 0:00 | 13:40 | 467:31 | 222:04 | 689:35 | 5548:09 | 689:35 | 22:15 | 97.0101 | 97.0101 | 5561:49 | 179:25 | 96.5153 | 96.5067
2 | Gadag | 16 | 16 | 17:38 | 40:04 | 88:00 | 26:33 | 114:33 | 981:21 | 132:11 | 8:16 | 99.0377 | 98.8896 | 1021:25 | 63:50 | 98.8058 | 98.757
3 | Haveri | 7 | 7 | 7:00 | 21:55 | 22:05 | 23:10 | 45:15 | 715:08 | 52:15 | 7:28 | 99.1311 | 98.9967 | 737:03 | 105:18 | 98.0109 | 97.9499
4 | Karwar | 10 | 10 | 62:40 | 213:36 | 71:37 | 57:59 | 129:36 | 1281:53 | 192:16 | 19:14 | 98.2581 | 97.4158 | 1495:29 | 149:33 | 97.5041 | 97.0882
5 | Belagavi | 69 | 69 | 105:53 | 839:11 | 453:09 | 196:28 | 649:37 | 5283:30 | 755:30 | 10:57 | 98.7346 | 98.5283 | 6122:42 | 88:44 | 98.5091 | 98.2723
6 | Vijayapur | 36 | 36 | 80:48 | 478:12 | 182:39 | 996:27 | 1179:06 | 5539:10 | 1259:54 | 35:00 | 95.5977 | 95.2961 | 6017:22 | 167:09 | 97.0042 | 96.7455
7 | Bagalkot | 11 | 11 | 40:00 | 200:00 | 69:32 | 70:34 | 140:06 | 1200:47 | 180:06 | 16:22 | 98.2881 | 97.7994 | 1400:47 | 127:21 | 97.8746 | 97.5206
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of NOVEMBER-2020
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of November-2020 |  |  |  | Reliability for cumulative period from Apr-20 to November-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 10:15 | 23:55 | 512:36 | 93:15 | 605:51 | 6154:00 | 616:06 | 19:52 | 97.2856 | 97.2397 | 6177:55 | 199:17 | 96.61 | 96.5969
2 | Gadag | 16 | 16 | 18:12 | 58:16 | 63:57 | 28:11 | 92:08 | 1073:29 | 110:20 | 6:54 | 99.2002 | 99.0422 | 1131:45 | 70:44 | 98.8543 | 98.7921
3 | Haveri | 7 | 7 | 1:00 | 22:55 | 27:20 | 9:00 | 36:20 | 751:28 | 37:20 | 5:20 | 99.2791 | 99.2593 | 774:23 | 110:38 | 98.1668 | 98.1109
4 | Karwar | 10 | 10 | 117:42 | 331:18 | 60:31 | 36:20 | 96:51 | 1378:44 | 214:33 | 21:27 | 98.6549 | 97.0201 | 1710:02 | 171:00 | 97.6456 | 97.0799
5 | Belagavi | 71 | 71 | 26:30 | 865:41 | 461:30 | 101:53 | 563:23 | 5846:53 | 589:53 | 8:18 | 98.8979 | 98.8461 | 6712:35 | 94:33 | 98.5937 | 98.3855
6 | Vijayapur | 37 | 37 | 5:30 | 483:42 | 163:23 | 251:06 | 414:29 | 5953:39 | 419:59 | 11:21 | 98.4441 | 98.4235 | 6437:21 | 173:59 | 97.2522 | 97.029
7 | Bagalkot | 11 | 11 | 13:00 | 213:00 | 56:53 | 26:24 | 83:17 | 1284:04 | 96:17 | 8:45 | 98.9484 | 98.7843 | 1497:04 | 136:06 | 98.0066 | 97.6759
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of DECEMBER-2020
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of December-2020 |  |  |  | Reliability for cumulative period from Apr-20 to December-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 2:35 | 26:30 | 586:27 | 33:00 | 619:27 | 6773:27 | 622:02 | 20:04 | 97.3142 | 97.303 | 6799:57 | 219:21 | 96.6894 | 96.6765
2 | Gadag | 16 | 16 | 16:05 | 74:21 | 66:19 | 27:21 | 93:40 | 1167:09 | 109:45 | 6:52 | 99.2131 | 99.078 | 1241:30 | 77:36 | 98.8947 | 98.8243
3 | Haveri | 7 | 7 | 0:00 | 22:55 | 11:15 | 8:19 | 19:34 | 771:02 | 19:34 | 2:48 | 99.6243 | 99.6243 | 793:57 | 113:25 | 98.3311 | 98.2815
4 | Karwar | 10 | 10 | 7:00 | 338:18 | 42:12 | 35:51 | 78:03 | 1456:47 | 85:03 | 8:30 | 98.9509 | 98.8569 | 1795:05 | 179:31 | 97.7928 | 97.2802
5 | Belagavi | 71 | 71 | 64:03 | 929:44 | 367:01 | 205:05 | 572:06 | 6418:59 | 636:09 | 8:58 | 98.917 | 98.7957 | 7348:44 | 103:30 | 98.6302 | 98.4318
6 | Vijayapur | 37 | 37 | 116:05 | 599:47 | 189:49 | 199:56 | 389:45 | 6343:24 | 505:50 | 13:40 | 98.5842 | 98.1625 | 6943:11 | 187:39 | 97.4024 | 97.1568
7 | Bagalkot | 11 | 11 | 0:00 | 213:00 | 42:49 | 12:46 | 55:35 | 1339:39 | 55:35 | 5:03 | 99.3208 | 99.3208 | 1552:39 | 141:09 | 98.1548 | 97.8614
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of JANUARY-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of January-2021 |  |  |  | Reliability for cumulative period from Apr-20 to January-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 7:05 | 33:35 | 537:21 | 156:35 | 693:56 | 7467:23 | 701:01 | 22:37 | 96.9913 | 96.9606 | 7500:58 | 241:58 | 96.72 | 96.7052
2 | Gadag | 16 | 16 | 18:45 | 93:06 | 50:19 | 32:05 | 82:24 | 1249:33 | 101:09 | 6:19 | 99.3078 | 99.1503 | 1342:39 | 83:55 | 98.9366 | 98.8574
3 | Haveri | 7 | 7 | 6:00 | 28:55 | 22:00 | 24:30 | 46:30 | 817:32 | 52:30 | 7:30 | 99.1071 | 98.9919 | 846:27 | 120:55 | 98.4097 | 98.3535
4 | Karwar | 10 | 10 | 48:00 | 386:18 | 62:41 | 71:20 | 134:01 | 1590:48 | 182:01 | 18:12 | 98.1987 | 97.5535 | 1977:06 | 197:43 | 97.8339 | 97.3079
5 | Belagavi | 74 | 74 | 141:51 | 1071:35 | 754:10 | 195:00 | 949:10 | 7368:09 | 1091:01 | 14:45 | 98.276 | 98.0184 | 8439:45 | 114:03 | 98.6442 | 98.447
6 | Vijayapur | 37 | 37 | 101:17 | 701:04 | 78:21 | 68:07 | 146:28 | 6489:52 | 247:45 | 6:42 | 99.4679 | 99.1 | 7190:56 | 194:21 | 97.6116 | 97.3536
7 | Bagalkot | 11 | 11 | 116:30 | 329:30 | 49:14 | 41:09 | 90:23 | 1430:02 | 206:53 | 18:48 | 98.8956 | 97.4721 | 1759:32 | 159:57 | 98.2298 | 97.8219
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of FEBRUARY-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of February-2021 |  |  |  | Reliability for cumulative period from Apr-20 to Feb-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 0:00 | 33:35 | 1016:16 | 113:41 | 1129:57 | 8597:20 | 1129:57 | 35:19 | 94.7454 | 94.7454 | 8630:55 | 269:43 | 96.6484 | 96.6353
2 | Gadag | 16 | 16 | 18:45 | 111:51 | 92:02 | 25:07 | 117:09 | 1366:42 | 135:54 | 8:30 | 98.9104 | 98.736 | 1478:33 | 92:25 | 98.9344 | 98.8472
3 | Haveri | 7 | 7 | 17:45 | 46:40 | 85:00 | 13:10 | 98:10 | 915:42 | 115:55 | 16:34 | 97.9131 | 97.5358 | 962:22 | 137:29 | 98.3681 | 98.2849
4 | Karwar | 10 | 10 | 4:12 | 390:30 | 44:17 | 51:00 | 95:17 | 1686:05 | 99:29 | 9:57 | 98.5821 | 98.5196 | 2076:35 | 207:40 | 97.8966 | 97.4095
5 | Belagavi | 75 | 75 | 84:26 | 1156:01 | 525:12 | 75:53 | 601:05 | 7969:14 | 685:31 | 9:08 | 98.8074 | 98.6398 | 9125:16 | 121:40 | 98.6744 | 98.4822
6 | Vijayapur | 37 | 37 | 43:48 | 744:52 | 122:12 | 81:51 | 204:03 | 6693:55 | 247:51 | 6:42 | 99.1793 | 99.0032 | 7438:47 | 201:03 | 97.7431 | 97.4919
7 | Bagalkot | 11 | 11 | 20:30 | 350:00 | 179:27 | 13:24 | 192:51 | 1622:53 | 213:21 | 19:24 | 97.3911 | 97.1138 | 1972:53 | 179:21 | 98.1595 | 97.7626
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of MARCH-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of March-2021 |  |  |  | Reliability for cumulative period from Apr-20 to Mar-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 2:30 | 36:05 | 583:56 | 130:33 | 714:29 | 9311:49 | 716:59 | 22:24 | 96.999 | 96.9885 | 9347:54 | 292:07 | 96.6781 | 96.6653
2 | Gadag | 16 | 16 | 11:05 | 122:56 | 242:15 | 24:10 | 266:25 | 1633:07 | 277:30 | 17:21 | 97.762 | 97.6689 | 1756:03 | 109:45 | 98.8348 | 98.7471
3 | Haveri | 7 | 7 | 10:30 | 57:10 | 15:35 | 11:45 | 27:20 | 943:02 | 37:50 | 5:24 | 99.4752 | 99.2736 | 1000:12 | 142:53 | 98.4621 | 98.3689
4 | Karwar | 10 | 10 | 56:42 | 447:12 | 86:01 | 79:50 | 165:51 | 1851:56 | 222:33 | 22:15 | 97.7708 | 97.0087 | 2299:08 | 229:55 | 97.8859 | 97.3754
5 | Belagavi | 75 | 75 | 128:47 | 1284:48 | 222:15 | 103:05 | 325:20 | 8294:34 | 454:07 | 6:03 | 99.417 | 99.1862 | 9579:23 | 127:44 | 98.7375 | 98.542
6 | Vijayapur | 37 | 37 | 5:27 | 750:19 | 170:54 | 202:27 | 373:21 | 7067:16 | 378:48 | 10:14 | 98.6437 | 98.6239 | 7817:35 | 211:17 | 97.8196 | 97.5881
7 | Bagalkot | 11 | 11 | 35:10 | 385:10 | 50:17 | 18:54 | 69:11 | 1692:04 | 104:21 | 9:29 | 99.1547 | 98.725 | 2077:14 | 188:50 | 98.244 | 97.8443
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]

## URBAN
Annex-II | [13 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of April-2020
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2020 |  |  |  | Reliability for cumulative period from Apr-20 to Apr-20
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 13:52 | 13:52 | 121:52 | 261:21 | 383:13 | 383:13 | 397:05 | 5:02 | 99.3263 | 99.3019 | 397:05 | 5:02 | 99.3263 | 99.3019
2 | Dharwad(R) | 19 | 19 | 6:56 | 6:56 | 184:24 | 261:21 | 445:45 | 445:45 | 452:41 | 23:50 | 96.7416 | 96.6909 | 452:41 | 23:50 | 96.7416 | 96.6909
3 | Kundagol | 1 | 1 | 8:05 | 8:05 | 9:45 | 8:30 | 18:15 | 18:15 | 26:20 | 26:20 | 97.4653 | 96.3426 | 26:20 | 26:20 | 97.4653 | 96.3426
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 2:49 | 7:47 | 10:36 | 10:36 | 10:36 | 10:36 | 98.5278 | 98.5278 | 10:36 | 10:36 | 98.5278 | 98.5278
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 8:10 | 11:10 | 19:20 | 19:20 | 19:20 | 19:20 | 97.3148 | 97.3148 | 19:20 | 19:20 | 97.3148 | 97.3148
6 | Kalghatagi | 2 | 2 | 2:20 | 2:20 | 37:20 | 36:35 | 73:55 | 73:55 | 76:15 | 38:08 | 94.8669 | 94.7049 | 76:15 | 38:08 | 94.8669 | 94.7049
7 | Alnavar | 1 | 1 | 6:20 | 6:20 | 9:10 | 10:45 | 19:55 | 19:55 | 26:15 | 26:15 | 97.2338 | 96.3542 | 26:15 | 26:15 | 97.2338 | 96.3542
8 | Naragund | 2 | 2 | 2:50 | 2:50 | 21:00 | 43:55 | 64:55 | 64:55 | 67:45 | 33:52 | 95.4919 | 95.2951 | 67:45 | 33:52 | 95.4919 | 95.2951
9 | Shirahatti | 3 | 3 | 0:00 | 0:00 | 25:45 | 5:50 | 31:35 | 31:35 | 31:35 | 10:32 | 98.5378 | 98.5378 | 31:35 | 10:32 | 98.5378 | 98.5378
10 | Laxmeshwar | 5 | 5 | 0:00 | 0:00 | 28:10 | 21:25 | 49:35 | 49:35 | 49:35 | 9:55 | 98.6227 | 98.6227 | 49:35 | 9:55 | 98.6227 | 98.6227
11 | Naregal | 1 | 1 | 0:00 | 0:00 | 12:25 | 9:00 | 21:25 | 21:25 | 21:25 | 21:25 | 97.0255 | 97.0255 | 21:25 | 21:25 | 97.0255 | 97.0255
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 21:25 | 12:45 | 34:10 | 34:10 | 34:10 | 17:05 | 97.6273 | 97.6273 | 34:10 | 17:05 | 97.6273 | 97.6273
13 | Ron | 3 | 3 | 0:00 | 0:00 | 19:20 | 29:30 | 48:50 | 48:50 | 48:50 | 16:17 | 97.7392 | 97.7392 | 48:50 | 16:17 | 97.7392 | 97.7392
14 | Mundaragi | 3 | 3 | 24:20 | 24:20 | 6:15 | 49:10 | 55:25 | 55:25 | 79:45 | 26:35 | 97.4344 | 96.3079 | 79:45 | 26:35 | 97.4344 | 96.3079
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 11:15 | 14:20 | 25:35 | 25:35 | 25:35 | 25:35 | 96.4468 | 96.4468 | 25:35 | 25:35 | 96.4468 | 96.4468
16 | G.C.T.M | 1 | 1 | 18:15 | 18:15 | 21:30 | 5:55 | 27:25 | 27:25 | 45:40 | 45:40 | 96.1921 | 93.6574 | 45:40 | 45:40 | 96.1921 | 93.6574
17 | F.C.S.M | 2 | 2 | 33:10 | 33:10 | 39:35 | 12:15 | 51:50 | 51:50 | 85:00 | 42:30 | 96.4005 | 94.0972 | 85:00 | 42:30 | 96.4005 | 94.0972
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 11:21 | 7:41 | 19:02 | 19:02 | 19:02 | 19:02 | 97.3565 | 97.3565 | 19:02 | 19:02 | 97.3565 | 97.3565
19 | Hole-Alur | 1 | 1 | 9:20 | 9:20 | 22:15 | 4:35 | 26:50 | 26:50 | 36:10 | 36:10 | 96.2731 | 94.9769 | 36:10 | 36:10 | 96.2731 | 94.9769
20 | Savanur | 2 | 2 | 9:30 | 9:30 | 17:00 | 22:25 | 39:25 | 39:25 | 48:55 | 24:28 | 97.2627 | 96.603 | 48:55 | 24:28 | 97.2627 | 96.603
21 | Shiggaon | 2 | 2 | 15:50 | 15:50 | 25:50 | 12:25 | 38:15 | 38:15 | 54:05 | 27:02 | 97.3438 | 96.2442 | 54:05 | 27:02 | 97.3438 | 96.2442
22 | Bankapur | 1 | 1 | 16:12 | 16:12 | 5:09 | 6:27 | 11:36 | 11:36 | 27:48 | 27:48 | 98.3889 | 96.1389 | 27:48 | 27:48 | 98.3889 | 96.1389
23 | Hangal | 2 | 2 | 10:30 | 10:30 | 25:40 | 35:40 | 61:20 | 61:20 | 71:50 | 35:55 | 95.7407 | 95.0116 | 71:50 | 35:55 | 95.7407 | 95.0116
24 | Ranebennur | 16 | 16 | 27:30 | 27:30 | 95:37 | 56:58 | 152:35 | 152:35 | 180:05 | 11:15 | 98.6755 | 98.4368 | 180:05 | 11:15 | 98.6755 | 98.4368
25 | Halageri | 2 | 2 | 14:00 | 14:00 | 12:20 | 2:25 | 14:45 | 14:45 | 28:45 | 14:22 | 98.9757 | 98.0035 | 28:45 | 14:22 | 98.9757 | 98.0035
26 | Tuminakatti | 2 | 2 | 1:20 | 1:20 | 20:10 | 10:10 | 30:20 | 30:20 | 31:40 | 15:50 | 97.8935 | 97.8009 | 31:40 | 15:50 | 97.8935 | 97.8009
27 | Kahanderayanahalli | 1 | 1 | 1:20 | 1:20 | 10:50 | 22:50 | 33:40 | 33:40 | 35:00 | 35:00 | 95.3241 | 95.1389 | 35:00 | 35:00 | 95.3241 | 95.1389
28 | Rattihalli | 1 | 1 | 3:20 | 3:20 | 8:00 | 6:30 | 14:30 | 14:30 | 17:50 | 17:50 | 97.9861 | 97.5231 | 17:50 | 17:50 | 97.9861 | 97.5231
29 | Hirekerur | 2 | 2 | 13:30 | 13:30 | 24:45 | 7:15 | 32:00 | 32:00 | 45:30 | 22:45 | 97.7778 | 96.8403 | 45:30 | 22:45 | 97.7778 | 96.8403
30 | Byadagi | 6 | 6 | 25:45 | 25:45 | 39:45 | 73:45 | 113:30 | 113:30 | 139:15 | 23:12 | 97.3727 | 96.7766 | 139:15 | 23:12 | 97.3727 | 96.7766
31 | Sirsi | 5 | 5 | 2:30 | 2:30 | 11:10 | 25:05 | 36:15 | 36:15 | 38:45 | 7:45 | 98.9931 | 98.9236 | 38:45 | 7:45 | 98.9931 | 98.9236
32 | Yellapur | 3 | 3 | 62:10 | 62:10 | 5:50 | 6:30 | 12:20 | 12:20 | 74:30 | 24:50 | 99.429 | 96.5509 | 74:30 | 24:50 | 99.429 | 96.5509
33 | Mundagod | 3 | 3 | 64:30 | 64:30 | 55:35 | 45:30 | 101:05 | 101:05 | 165:35 | 55:12 | 95.3202 | 92.3341 | 165:35 | 55:12 | 95.3202 | 92.3341
34 | Siddapur | 2 | 2 | 24:10 | 24:10 | 2:30 | 16:05 | 18:35 | 18:35 | 42:45 | 21:22 | 98.7095 | 97.0312 | 42:45 | 21:22 | 98.7095 | 97.0312
35 | Dandeli | 8 | 8 | 50:36 | 50:36 | 60:50 | 124:22 | 185:12 | 185:12 | 235:48 | 29:28 | 96.7847 | 95.9062 | 235:48 | 29:28 | 96.7847 | 95.9062
36 | Haliyal | 3 | 3 | 0:42 | 0:42 | 28:01 | 22:03 | 50:04 | 50:04 | 50:46 | 16:55 | 97.6821 | 97.6497 | 50:46 | 16:55 | 97.6821 | 97.6497
37 | Ankola | 3 | 3 | 24:20 | 24:20 | 19:59 | 2:18 | 22:17 | 22:17 | 46:37 | 15:32 | 98.9684 | 97.8418 | 46:37 | 15:32 | 98.9684 | 97.8418
38 | Kumta | 3 | 3 | 1:27 | 1:27 | 26:08 | 15:15 | 41:23 | 41:23 | 42:50 | 14:17 | 98.0841 | 98.017 | 42:50 | 14:17 | 98.0841 | 98.017
39 | Gokarna | 1 | 1 | 9:30 | 9:30 | 0:30 | 5:20 | 5:50 | 5:50 | 15:20 | 15:20 | 99.1898 | 97.8704 | 15:20 | 15:20 | 99.1898 | 97.8704
40 | Kasarkod | 1 | 1 | 0:00 | 0:00 | 2:25 | 0:30 | 2:55 | 2:55 | 2:55 | 2:55 | 99.5949 | 99.5949 | 2:55 | 2:55 | 99.5949 | 99.5949
41 | Honnavar | 3 | 3 | 33:45 | 33:45 | 25:05 | 11:37 | 36:42 | 36:42 | 70:27 | 23:29 | 98.3009 | 96.7384 | 70:27 | 23:29 | 98.3009 | 96.7384
42 | Murdeshwar | 4 | 4 | 48:08 | 48:08 | 46:01 | 22:07 | 68:08 | 68:08 | 116:16 | 29:04 | 97.6343 | 95.963 | 116:16 | 29:04 | 97.6343 | 95.963
43 | Bhatkal | 3 | 3 | 0:00 | 0:00 | 24:25 | 12:22 | 36:47 | 36:47 | 36:47 | 12:16 | 98.2971 | 98.2971 | 36:47 | 12:16 | 98.2971 | 98.2971
44 | Khanapur | 2 | 2 | 20:20 | 20:20 | 25:30 | 16:35 | 42:05 | 42:05 | 62:25 | 31:13 | 97.0775 | 95.6655 | 62:25 | 31:13 | 97.0775 | 95.6655
45 | Bailhongal | 3 | 3 | 0:30 | 0:30 | 41:25 | 13:10 | 54:35 | 54:35 | 55:05 | 18:22 | 97.473 | 97.4498 | 55:05 | 18:22 | 97.473 | 97.4498
46 | Soundatti | 3 | 3 | 0:00 | 0:00 | 19:16 | 14:11 | 33:27 | 33:27 | 33:27 | 11:09 | 98.4514 | 98.4514 | 33:27 | 11:09 | 98.4514 | 98.4514
47 | Ramdurg | 2 | 2 | 3:50 | 3:50 | 27:00 | 15:00 | 42:00 | 42:00 | 45:50 | 22:55 | 97.0833 | 96.8171 | 45:50 | 22:55 | 97.0833 | 96.8171
48 | Gokak | 8 | 8 | 2:35 | 2:35 | 27:10 | 30:05 | 57:15 | 57:15 | 59:50 | 7:29 | 99.0061 | 98.9612 | 59:50 | 7:29 | 99.0061 | 98.9612
49 | Mudalagi | 2 | 2 | 7:30 | 7:30 | 13:15 | 7:55 | 21:10 | 21:10 | 28:40 | 14:20 | 98.5301 | 98.0093 | 28:40 | 14:20 | 98.5301 | 98.0093
50 | Konnur | 1 | 1 | 0:00 | 0:00 | 10:55 | 0:40 | 11:35 | 11:35 | 11:35 | 11:35 | 98.3912 | 98.3912 | 11:35 | 11:35 | 98.3912 | 98.3912
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 11:58 | 10:41 | 22:39 | 22:39 | 22:39 | 22:39 | 96.8542 | 96.8542 | 22:39 | 22:39 | 96.8542 | 96.8542
52 | Kudachi | 1 | 1 | 0:00 | 0:00 | 5:30 | 5:35 | 11:05 | 11:05 | 11:05 | 11:05 | 98.4606 | 98.4606 | 11:05 | 11:05 | 98.4606 | 98.4606
53 | Athani | 6 | 6 | 43:54 | 43:54 | 51:45 | 101:27 | 153:12 | 153:12 | 197:06 | 32:51 | 96.4537 | 95.4375 | 197:06 | 32:51 | 96.4537 | 95.4375
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 5:00 | 11:35 | 16:35 | 16:35 | 16:35 | 8:18 | 98.8484 | 98.8484 | 16:35 | 8:18 | 98.8484 | 98.8484
55 | Nippani | 5 | 5 | 51:40 | 51:40 | 17:00 | 56:15 | 73:15 | 73:15 | 124:55 | 24:59 | 97.9653 | 96.5301 | 124:55 | 24:59 | 97.9653 | 96.5301
56 | Sadalaga | 1 | 1 | 4:58 | 4:58 | 15:55 | 9:40 | 25:35 | 25:35 | 30:33 | 30:33 | 96.4468 | 95.7569 | 30:33 | 30:33 | 96.4468 | 95.7569
57 | Muddebihal | 2 | 2 | 3:43 | 3:43 | 36:17 | 15:53 | 52:10 | 52:10 | 55:53 | 27:56 | 96.3773 | 96.1192 | 55:53 | 27:56 | 96.3773 | 96.1192
58 | Talikoti | 1 | 1 | 0:50 | 0:50 | 18:30 | 7:05 | 25:35 | 25:35 | 26:25 | 26:25 | 96.4468 | 96.331 | 26:25 | 26:25 | 96.4468 | 96.331
59 | B.Bagewadi | 1 | 1 | 4:45 | 4:45 | 9:35 | 6:50 | 16:25 | 16:25 | 21:10 | 21:10 | 97.7199 | 97.0602 | 21:10 | 21:10 | 97.7199 | 97.0602
60 | Indi | 1 | 1 | 1:32 | 1:32 | 16:36 | 5:32 | 22:08 | 22:08 | 23:40 | 23:40 | 96.9259 | 96.713 | 23:40 | 23:40 | 96.9259 | 96.713
61 | Sindagi | 2 | 2 | 5:20 | 5:20 | 11:45 | 3:50 | 15:35 | 15:35 | 20:55 | 10:28 | 98.9178 | 98.5475 | 20:55 | 10:28 | 98.9178 | 98.5475
62 | Guledgudda | 1 | 1 | 0:00 | 0:00 | 5:45 | 4:42 | 10:27 | 10:27 | 10:27 | 10:27 | 98.5486 | 98.5486 | 10:27 | 10:27 | 98.5486 | 98.5486
63 | Ilkal | 8 | 8 | 26:32 | 26:32 | 36:12 | 128:41 | 164:53 | 164:53 | 191:25 | 23:56 | 97.1374 | 96.6768 | 191:25 | 23:56 | 97.1374 | 96.6768
64 | Kerur | 2 | 2 | 0:00 | 0:00 | 12:04 | 9:37 | 21:41 | 21:41 | 21:41 | 10:50 | 98.4942 | 98.4942 | 21:41 | 10:50 | 98.4942 | 98.4942
65 | Hungund | 4 | 4 | 5:30 | 5:30 | 36:32 | 29:35 | 66:07 | 66:07 | 71:37 | 17:54 | 97.7043 | 97.5133 | 71:37 | 17:54 | 97.7043 | 97.5133
66 | Gaddankeri | 4 | 4 | 6:52 | 6:52 | 20:40 | 20:34 | 41:14 | 41:14 | 48:06 | 12:01 | 98.5683 | 98.3299 | 48:06 | 12:01 | 98.5683 | 98.3299
67 | Rampur | 1 | 1 | 1:27 | 1:27 | 3:33 | 0:12 | 3:45 | 3:45 | 5:12 | 5:12 | 99.4792 | 99.2778 | 5:12 | 5:12 | 99.4792 | 99.2778
68 | Kaladagi | 2 | 2 | 0:00 | 0:00 | 23:03 | 17:33 | 40:36 | 40:36 | 40:36 | 20:18 | 97.1806 | 97.1806 | 40:36 | 20:18 | 97.1806 | 97.1806
69 | Achanur | 1 | 1 | 3:27 | 3:27 | 5:33 | 20:24 | 25:57 | 25:57 | 29:24 | 29:24 | 96.3958 | 95.9167 | 29:24 | 29:24 | 96.3958 | 95.9167
70 | Shirur | 1 | 1 | 0:00 | 0:00 | 10:39 | 0:15 | 10:54 | 10:54 | 10:54 | 10:54 | 98.4861 | 98.4861 | 10:54 | 10:54 | 98.4861 | 98.4861
71 | Badami | 1 | 1 | 0:00 | 0:00 | 8:52 | 12:17 | 21:09 | 21:09 | 21:09 | 21:09 | 97.0625 | 97.0625 | 21:09 | 21:09 | 97.0625 | 97.0625
72 | Kulageri | 1 | 1 | 2:00 | 2:00 | 3:30 | 0:55 | 4:25 | 4:25 | 6:25 | 6:25 | 99.3866 | 99.1088 | 6:25 | 6:25 | 99.3866 | 99.1088
73 | Jamkhandi | 5 | 5 | 21:40 | 21:40 | 32:15 | 7:00 | 39:15 | 39:15 | 60:55 | 12:11 | 98.9097 | 98.3079 | 60:55 | 12:11 | 98.9097 | 98.3079
74 | Mahalingapur | 3 | 3 | 9:18 | 9:18 | 22:26 | 19:37 | 42:03 | 42:03 | 51:21 | 17:07 | 98.0532 | 97.6227 | 51:21 | 17:07 | 98.0532 | 97.6227
75 | Rabakavi | 2 | 2 | 2:40 | 2:40 | 14:05 | 6:15 | 20:20 | 20:20 | 23:00 | 11:30 | 98.588 | 98.4028 | 23:00 | 11:30 | 98.588 | 98.4028
76 | Banahatti | 2 | 2 | 9:20 | 9:20 | 61:20 | 1:40 | 63:00 | 63:00 | 72:20 | 36:10 | 95.625 | 94.9769 | 72:20 | 36:10 | 95.625 | 94.9769
77 | Terdal | 1 | 1 | 8:40 | 8:40 | 11:10 | 5:45 | 16:55 | 16:55 | 25:35 | 25:35 | 97.6505 | 96.4468 | 25:35 | 25:35 | 97.6505 | 96.4468
78 | Mudhol | 4 | 4 | 0:00 | 0:00 | 77:54 | 18:38 | 96:32 | 96:32 | 96:32 | 24:08 | 96.6481 | 96.6481 | 96:32 | 24:08 | 96.6481 | 96.6481
79 | Bilagi | 1 | 1 | 0:00 | 0:00 | 6:35 | 2:40 | 9:15 | 9:15 | 9:15 | 9:15 | 98.7153 | 98.7153 | 9:15 | 9:15 | 98.7153 | 98.7153
80 | Lokapur | 2 | 2 | 3:40 | 3:40 | 66:35 | 9:00 | 75:35 | 75:35 | 79:15 | 39:38 | 94.7512 | 94.4965 | 79:15 | 39:38 | 94.7512 | 94.4965
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of May-2020
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2020 |  |  |  | Reliability for cumulative period from Apr-20 to May-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 20:03 | 33:55 | 212:37 | 274:23 | 487:00 | 870:13 | 507:03 | 6:25 | 99.1714 | 99.1373 | 904:08 | 11:27 | 99.2476 | 99.2183
2 | Dharwad(R) | 19 | 19 | 14:50 | 21:46 | 289:53 | 288:35 | 578:28 | 1024:13 | 593:18 | 31:14 | 95.9078 | 95.8029 | 1045:59 | 55:03 | 96.3179 | 96.2396
3 | Kundagol | 1 | 1 | 20:35 | 28:40 | 8:10 | 4:15 | 12:25 | 30:40 | 33:00 | 33:00 | 98.3311 | 95.5645 | 59:20 | 59:20 | 97.9053 | 95.9472
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 16:07 | 7:47 | 23:54 | 34:30 | 23:54 | 23:54 | 96.7876 | 96.7876 | 34:30 | 34:30 | 97.6434 | 97.6434
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 16:15 | 20:25 | 36:40 | 56:00 | 36:40 | 36:40 | 95.0717 | 95.0717 | 56:00 | 56:00 | 96.1749 | 96.1749
6 | Kalghatagi | 2 | 2 | 0:00 | 2:20 | 71:00 | 54:35 | 125:35 | 199:30 | 125:35 | 62:48 | 91.5603 | 91.5603 | 201:50 | 100:55 | 93.1865 | 93.1068
7 | Alnavar | 1 | 1 | 6:30 | 12:50 | 17:35 | 0:30 | 18:05 | 38:00 | 24:35 | 24:35 | 97.5694 | 96.6958 | 50:50 | 50:50 | 97.4044 | 96.5278
8 | Naragund | 2 | 2 | 7:00 | 9:50 | 25:10 | 66:15 | 91:25 | 156:20 | 98:25 | 49:12 | 93.8564 | 93.386 | 166:10 | 83:05 | 94.6607 | 94.3249
9 | Shirahatti | 3 | 3 | 0:00 | 0:00 | 30:25 | 70:05 | 100:30 | 132:05 | 100:30 | 33:30 | 95.4973 | 95.4973 | 132:05 | 44:02 | 96.9926 | 96.9926
10 | Laxmeshwar | 5 | 5 | 0:00 | 0:00 | 114:49 | 63:22 | 178:11 | 227:46 | 178:11 | 35:38 | 95.2101 | 95.2101 | 227:46 | 45:33 | 96.8884 | 96.8884
11 | Naregal | 1 | 1 | 0:00 | 0:00 | 12:15 | 19:55 | 32:10 | 53:35 | 32:10 | 32:10 | 95.6765 | 95.6765 | 53:35 | 53:35 | 96.3399 | 96.3399
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 35:55 | 28:55 | 64:50 | 99:00 | 64:50 | 32:25 | 95.6429 | 95.6429 | 99:00 | 49:30 | 96.6189 | 96.6189
13 | Ron | 3 | 3 | 0:00 | 0:00 | 51:20 | 56:25 | 107:45 | 156:35 | 107:45 | 35:55 | 95.1725 | 95.1725 | 156:35 | 52:12 | 96.4348 | 96.4348
14 | Mundaragi | 3 | 3 | 13:10 | 37:30 | 34:20 | 77:10 | 111:30 | 166:55 | 124:40 | 41:33 | 95.0045 | 94.4146 | 204:25 | 68:08 | 96.1995 | 95.3457
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 31:53 | 33:48 | 65:41 | 91:16 | 65:41 | 65:41 | 91.1716 | 91.1716 | 91:16 | 91:16 | 93.7659 | 93.7659
16 | G.C.T.M | 1 | 1 | 15:10 | 33:25 | 55:50 | 24:00 | 79:50 | 107:15 | 95:00 | 95:00 | 89.2697 | 87.2312 | 140:40 | 140:40 | 92.6742 | 90.3916
17 | F.C.S.M | 2 | 2 | 28:30 | 61:40 | 21:40 | 41:50 | 63:30 | 115:20 | 92:00 | 46:00 | 95.7325 | 93.8172 | 177:00 | 88:30 | 96.061 | 93.9549
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 9:10 | 21:47 | 30:57 | 49:59 | 30:57 | 30:57 | 95.8401 | 95.8401 | 49:59 | 49:59 | 96.5858 | 96.5858
19 | Hole-Alur | 1 | 1 | 20:25 | 29:45 | 20:15 | 5:10 | 25:25 | 52:15 | 45:50 | 45:50 | 96.5838 | 93.8396 | 82:00 | 82:00 | 96.431 | 94.3989
20 | Savanur | 2 | 2 | 0:00 | 9:30 | 24:40 | 39:20 | 64:00 | 103:25 | 64:00 | 32:00 | 95.6989 | 95.6989 | 112:55 | 56:28 | 96.468 | 96.1436
21 | Shiggaon | 2 | 2 | 11:35 | 27:25 | 33:45 | 79:15 | 113:00 | 151:15 | 124:35 | 62:18 | 92.4059 | 91.6275 | 178:40 | 89:20 | 94.8344 | 93.898
22 | Bankapur | 1 | 1 | 50:20 | 66:32 | 33:45 | 29:30 | 63:15 | 74:51 | 113:35 | 113:35 | 91.4987 | 84.7334 | 141:23 | 141:23 | 94.8873 | 90.3427
23 | Hangal | 2 | 2 | 2:40 | 13:10 | 34:00 | 20:15 | 54:15 | 115:35 | 56:55 | 28:28 | 96.3542 | 96.175 | 128:45 | 64:23 | 96.0525 | 95.6028
24 | Ranebennur | 16 | 16 | 2:25 | 29:55 | 221:18 | 102:04 | 323:22 | 475:57 | 325:47 | 20:22 | 97.2835 | 97.2632 | 505:52 | 31:37 | 97.9681 | 97.8404
25 | Halageri | 2 | 2 | 66:10 | 80:10 | 56:55 | 7:15 | 64:10 | 78:55 | 130:20 | 65:10 | 95.6877 | 91.241 | 159:05 | 79:32 | 97.3048 | 94.5668
26 | Tuminakatti | 2 | 2 | 0:30 | 1:50 | 10:45 | 2:50 | 13:35 | 43:55 | 14:05 | 7:02 | 99.0871 | 99.0535 | 45:45 | 22:52 | 98.5001 | 98.4375
27 | Kahanderayanahalli | 1 | 1 | 0:20 | 1:40 | 28:10 | 39:15 | 67:25 | 101:05 | 67:45 | 67:45 | 90.9386 | 90.8938 | 102:45 | 102:45 | 93.0954 | 92.9816
28 | Rattihalli | 1 | 1 | 0:35 | 3:55 | 11:05 | 11:55 | 23:00 | 37:30 | 23:35 | 23:35 | 96.9086 | 96.8302 | 41:25 | 41:25 | 97.4385 | 97.171
29 | Hirekerur | 2 | 2 | 14:12 | 27:42 | 33:45 | 24:20 | 58:05 | 90:05 | 72:17 | 36:08 | 96.0966 | 95.1422 | 117:47 | 58:54 | 96.9234 | 95.9773
30 | Byadagi | 7 | 7 | 44:05 | 69:50 | 110:50 | 225:23 | 336:13 | 449:43 | 380:18 | 54:20 | 93.5442 | 92.6978 | 519:33 | 74:13 | 95.6117 | 94.9302
31 | Sirsi | 5 | 5 | 2:30 | 5:00 | 11:10 | 25:05 | 36:15 | 72:30 | 38:45 | 7:45 | 99.0255 | 98.9583 | 77:30 | 15:30 | 99.0096 | 98.9413
32 | Yellapur | 3 | 3 | 35:55 | 98:05 | 25:25 | 23:15 | 48:40 | 61:00 | 84:35 | 28:12 | 97.8196 | 96.2104 | 159:05 | 53:02 | 98.6111 | 96.3779
33 | Mundagod | 3 | 3 | 192:03 | 256:33 | 186:30 | 100:20 | 286:50 | 387:55 | 478:53 | 159:38 | 87.149 | 78.5447 | 644:28 | 214:49 | 91.1677 | 85.3264
34 | Siddapur | 2 | 2 | 63:20 | 87:30 | 28:35 | 27:50 | 56:25 | 75:00 | 119:45 | 59:52 | 96.2086 | 91.9523 | 162:30 | 81:15 | 97.4385 | 94.4501
35 | Dandeli | 8 | 8 | 42:08 | 92:44 | 91:12 | 32:59 | 124:11 | 309:23 | 166:19 | 20:47 | 97.9136 | 97.2057 | 402:07 | 50:16 | 97.3584 | 96.5666
36 | Haliyal | 3 | 3 | 6:18 | 7:00 | 25:03 | 29:48 | 54:51 | 104:55 | 61:09 | 20:23 | 97.5426 | 97.2603 | 111:55 | 37:18 | 97.6112 | 97.4518
37 | Ankola | 3 | 3 | 44:19 | 68:39 | 11:20 | 8:07 | 19:27 | 41:44 | 63:46 | 21:15 | 99.1286 | 97.1431 | 110:23 | 36:48 | 99.0498 | 97.4867
38 | Kumta | 3 | 3 | 8:21 | 9:48 | 25:51 | 19:01 | 44:52 | 86:15 | 53:13 | 17:44 | 97.9898 | 97.6157 | 96:03 | 32:01 | 98.0362 | 97.8131
39 | Gokarna | 1 | 1 | 23:23 | 32:53 | 7:19 | 3:04 | 10:23 | 16:13 | 33:46 | 33:46 | 98.6044 | 95.4615 | 49:06 | 49:06 | 98.8923 | 96.6462
40 | Kasarkod | 1 | 1 | 38:21 | 38:21 | 9:05 | 2:10 | 11:15 | 14:10 | 49:36 | 49:36 | 98.4879 | 93.3333 | 52:31 | 52:31 | 99.0323 | 96.4128
41 | Honnavar | 3 | 3 | 21:18 | 55:03 | 20:32 | 13:04 | 33:36 | 70:18 | 54:54 | 18:18 | 98.4946 | 97.5403 | 125:21 | 41:47 | 98.3994 | 97.1459
42 | Murdeshwar | 4 | 4 | 68:20 | 116:28 | 35:41 | 11:02 | 46:43 | 114:51 | 115:03 | 28:46 | 98.4302 | 96.1341 | 231:19 | 57:50 | 98.0388 | 96.0499
43 | Bhatkal | 3 | 3 | 31:18 | 31:18 | 42:27 | 18:02 | 60:29 | 97:16 | 91:47 | 30:36 | 97.2902 | 95.8878 | 128:34 | 42:51 | 97.7854 | 97.0727
44 | Khanapur | 2 | 2 | 1:10 | 21:30 | 13:10 | 11:55 | 25:05 | 67:10 | 26:15 | 13:08 | 98.3143 | 98.2359 | 88:40 | 44:20 | 97.7061 | 96.9718
45 | Bailhongal | 3 | 3 | 0:00 | 0:30 | 28:35 | 9:40 | 38:15 | 92:50 | 38:15 | 12:45 | 98.2863 | 98.2863 | 93:20 | 31:07 | 97.8863 | 97.8749
46 | Soundatti | 3 | 3 | 15:00 | 15:00 | 41:53 | 26:20 | 68:13 | 101:40 | 83:13 | 27:44 | 96.9437 | 96.2717 | 116:40 | 38:53 | 97.6852 | 97.3437
47 | Ramdurg | 2 | 2 | 1:40 | 5:30 | 20:30 | 12:10 | 32:40 | 74:40 | 34:20 | 17:10 | 97.8047 | 97.6927 | 80:10 | 40:05 | 97.4499 | 97.2621
48 | Gokak | 11 | 11 | 46:46 | 49:21 | 165:53 | 49:20 | 215:13 | 272:28 | 261:59 | 23:49 | 97.3703 | 96.7988 | 321:49 | 29:15 | 98.3081 | 98.0016
49 | Mudalagi | 2 | 2 | 10:50 | 18:20 | 23:40 | 24:15 | 47:55 | 69:05 | 58:45 | 29:23 | 96.7798 | 96.0517 | 87:25 | 43:43 | 97.6406 | 97.0145
50 | Konnur | 1 | 1 | 1:45 | 1:45 | 16:35 | 5:40 | 22:15 | 33:50 | 24:00 | 24:00 | 97.0094 | 96.7742 | 35:35 | 35:35 | 97.689 | 97.5694
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 16:46 | 8:41 | 25:27 | 48:06 | 25:27 | 25:27 | 96.5793 | 96.5793 | 48:06 | 48:06 | 96.7145 | 96.7145
52 | Kudachi | 1 | 1 | 0:00 | 0:00 | 15:40 | 14:15 | 29:55 | 41:00 | 29:55 | 29:55 | 95.9789 | 95.9789 | 41:00 | 41:00 | 97.1995 | 97.1995
53 | Athani | 6 | 6 | 54:58 | 98:52 | 98:11 | 13:57 | 112:08 | 265:20 | 167:06 | 27:51 | 97.488 | 96.2567 | 364:12 | 60:42 | 96.9793 | 95.8538
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 22:45 | 12:55 | 35:40 | 52:15 | 35:40 | 17:50 | 97.603 | 97.603 | 52:15 | 26:08 | 98.2155 | 98.2155
55 | Nippani | 5 | 5 | 9:10 | 60:50 | 85:30 | 41:50 | 127:20 | 200:35 | 136:30 | 27:18 | 96.5771 | 96.3306 | 261:25 | 52:17 | 97.2598 | 96.4287
56 | Sadalaga | 1 | 1 | 1:00 | 5:58 | 17:20 | 1:35 | 18:55 | 44:30 | 19:55 | 19:55 | 97.4574 | 97.323 | 50:28 | 50:28 | 96.9604 | 96.5528
57 | Muddebihal | 2 | 2 | 3:40 | 7:23 | 27:50 | 16:45 | 44:35 | 96:45 | 48:15 | 24:08 | 97.0038 | 96.7574 | 104:08 | 52:04 | 96.6957 | 96.4435
58 | Talikoti | 1 | 1 | 1:20 | 2:10 | 13:05 | 36:20 | 49:25 | 75:00 | 50:45 | 50:45 | 93.358 | 93.1788 | 77:10 | 77:10 | 94.877 | 94.7291
59 | B.Bagewadi | 1 | 1 | 5:29 | 10:14 | 4:35 | 6:25 | 11:00 | 27:25 | 16:29 | 16:29 | 98.5215 | 97.7845 | 37:39 | 37:39 | 98.1273 | 97.4283
60 | Indi | 2 | 2 | 0:11 | 1:43 | 21:51 | 8:25 | 30:16 | 52:24 | 30:27 | 15:14 | 97.9659 | 97.9536 | 54:07 | 27:04 | 98.2104 | 98.1518
61 | Sindagi | 2 | 2 | 16:30 | 21:50 | 28:10 | 22:30 | 50:40 | 66:15 | 67:10 | 33:35 | 96.595 | 95.4861 | 88:05 | 44:02 | 97.7374 | 96.9917
62 | Guledgudda | 1 | 1 | 12:15 | 12:15 | 7:38 | 5:32 | 13:10 | 23:37 | 25:25 | 25:25 | 98.2303 | 96.5838 | 35:52 | 35:52 | 98.3868 | 97.5501
63 | Ilkal | 8 | 8 | 20:35 | 47:07 | 135:18 | 210:10 | 345:28 | 510:21 | 366:03 | 45:45 | 94.1958 | 93.85 | 557:28 | 69:41 | 95.6425 | 95.2402
64 | Kerur | 2 | 2 | 2:50 | 2:50 | 22:05 | 13:38 | 35:43 | 57:24 | 38:33 | 19:16 | 97.5997 | 97.4093 | 60:14 | 30:07 | 98.0396 | 97.9429
65 | Hungund | 4 | 4 | 9:00 | 14:30 | 73:09 | 78:25 | 151:34 | 217:41 | 160:34 | 40:08 | 94.907 | 94.6046 | 232:11 | 58:03 | 96.2827 | 96.0351
66 | Gaddankeri | 4 | 4 | 54:54 | 61:46 | 8:44 | 12:43 | 21:27 | 62:41 | 76:21 | 19:05 | 99.2792 | 97.4345 | 124:27 | 31:07 | 98.9296 | 97.8748
67 | Rampur | 1 | 1 | 15:27 | 16:54 | 8:12 | 2:09 | 10:21 | 14:06 | 25:48 | 25:48 | 98.6089 | 96.5323 | 31:00 | 31:00 | 99.0369 | 97.8825
68 | Kaladagi | 2 | 2 | 0:00 | 0:00 | 16:18 | 45:21 | 61:39 | 102:15 | 61:39 | 30:50 | 95.8569 | 95.8569 | 102:15 | 51:08 | 96.5079 | 96.5079
69 | Achanur | 1 | 1 | 3:27 | 6:54 | 33:18 | 18:54 | 52:12 | 78:09 | 55:39 | 55:39 | 92.9839 | 92.5202 | 85:03 | 85:03 | 94.6619 | 94.1906
70 | Shirur | 1 | 1 | 15:03 | 15:03 | 11:51 | 6:57 | 18:48 | 29:42 | 33:51 | 33:51 | 97.4731 | 95.4503 | 44:45 | 44:45 | 97.9713 | 96.9433
71 | Badami | 1 | 1 | 11:39 | 11:39 | 12:30 | 14:12 | 26:42 | 47:51 | 38:21 | 38:21 | 96.4113 | 94.8454 | 59:30 | 59:30 | 96.7316 | 95.9358
72 | Kulageri | 1 | 1 | 3:43 | 5:43 | 6:55 | 0:20 | 7:15 | 11:40 | 10:58 | 10:58 | 99.0255 | 98.526 | 17:23 | 17:23 | 99.2031 | 98.8126
73 | Jamkhandi | 5 | 5 | 8:45 | 30:25 | 59:00 | 21:40 | 80:40 | 119:55 | 89:25 | 17:53 | 97.8315 | 97.5963 | 150:20 | 30:04 | 98.3618 | 97.9463
74 | Mahalingapur | 3 | 3 | 6:30 | 15:48 | 45:40 | 21:59 | 67:39 | 109:42 | 74:09 | 24:43 | 96.9691 | 96.6779 | 125:30 | 41:50 | 97.5023 | 97.1425
75 | Rabakavi | 2 | 2 | 1:25 | 4:05 | 12:15 | 6:55 | 19:10 | 39:30 | 20:35 | 10:18 | 98.7119 | 98.6167 | 43:35 | 21:48 | 98.651 | 98.5115
76 | Banahatti | 2 | 2 | 3:35 | 12:55 | 52:30 | 5:20 | 57:50 | 120:50 | 61:25 | 30:42 | 96.1134 | 95.8725 | 133:45 | 66:52 | 95.8732 | 95.432
77 | Terdal | 1 | 1 | 11:05 | 19:45 | 66:15 | 10:20 | 76:35 | 93:30 | 87:40 | 87:40 | 89.7065 | 88.2168 | 113:15 | 113:15 | 93.6134 | 92.2643
78 | Mudhol | 4 | 4 | 1:26 | 1:26 | 53:47 | 19:09 | 72:56 | 169:28 | 74:22 | 18:36 | 97.5493 | 97.5011 | 170:54 | 42:44 | 97.1061 | 97.0816
79 | Bilagi | 1 | 1 | 0:40 | 0:40 | 8:40 | 7:00 | 15:40 | 24:55 | 16:20 | 16:20 | 97.8943 | 97.8047 | 25:35 | 25:35 | 98.298 | 98.2525
80 | Lokapur | 2 | 2 | 3:47 | 7:27 | 54:05 | 13:15 | 67:20 | 142:55 | 71:07 | 35:34 | 95.4749 | 95.2207 | 150:22 | 75:11 | 95.119 | 94.8645
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of June-2020
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2020 |  |  |  | Reliability for cumulative period from Apr-20 to June-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 20:03 | 53:58 | 364:08 | 276:50 | 640:58 | 1511:11 | 661:01 | 8:22 | 98.8731 | 98.8379 | 1565:09 | 19:49 | 99.1241 | 99.0929
2 | Dharwad(R) | 19 | 19 | 0:00 | 21:46 | 235:26 | 183:17 | 418:43 | 1442:56 | 418:43 | 22:02 | 96.9392 | 96.9392 | 1464:42 | 77:05 | 96.5227 | 96.4703
3 | Kundagol | 1 | 1 | 10:10 | 38:50 | 7:35 | 8:15 | 15:50 | 46:30 | 26:00 | 26:00 | 97.8009 | 96.3889 | 85:20 | 85:20 | 97.8709 | 96.0928
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 19:57 | 12:09 | 32:06 | 66:36 | 32:06 | 32:06 | 95.5417 | 95.5417 | 66:36 | 66:36 | 96.9505 | 96.9505
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 18:30 | 11:50 | 30:20 | 86:20 | 30:20 | 30:20 | 95.787 | 95.787 | 86:20 | 86:20 | 96.047 | 96.047
6 | Kalghatagi | 2 | 2 | 0:00 | 2:20 | 10:05 | 29:35 | 39:40 | 239:10 | 39:40 | 19:50 | 97.2454 | 97.2454 | 241:30 | 120:45 | 94.5246 | 94.4712
7 | Alnavar | 1 | 1 | 2:25 | 15:15 | 17:15 | 3:15 | 20:30 | 58:30 | 22:55 | 22:55 | 97.1528 | 96.8171 | 73:45 | 73:45 | 97.3214 | 96.6232
8 | Naragund | 2 | 2 | 4:40 | 14:30 | 36:20 | 43:40 | 80:00 | 236:20 | 84:40 | 42:20 | 94.4444 | 94.1204 | 250:50 | 125:25 | 94.5894 | 94.2575
9 | Shirahatti | 4 | 4 | 18:50 | 18:50 | 35:53 | 92:20 | 128:13 | 260:18 | 147:03 | 36:46 | 95.548 | 94.8941 | 279:08 | 69:47 | 97.0204 | 96.8048
10 | Laxmeshwar | 5 | 5 | 0:00 | 0:00 | 41:11 | 46:56 | 88:07 | 315:53 | 88:07 | 17:37 | 97.5523 | 97.5523 | 315:53 | 63:11 | 97.1073 | 97.1073
11 | Naregal | 1 | 1 | 12:50 | 12:50 | 30:10 | 7:15 | 37:25 | 91:00 | 50:15 | 50:15 | 94.8032 | 93.0208 | 103:50 | 103:50 | 95.8333 | 95.2457
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 22:05 | 12:10 | 34:15 | 133:15 | 34:15 | 17:08 | 97.6215 | 97.6215 | 133:15 | 66:38 | 96.9494 | 96.9494
13 | Ron | 3 | 3 | 20:15 | 20:15 | 56:30 | 55:25 | 111:55 | 268:30 | 132:10 | 44:03 | 94.8187 | 93.8812 | 288:45 | 96:15 | 95.902 | 95.5929
14 | Mundaragi | 3 | 3 | 9:05 | 46:35 | 19:55 | 38:30 | 58:25 | 225:20 | 67:30 | 22:30 | 97.2955 | 96.875 | 271:55 | 90:38 | 96.5608 | 95.8499
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 26:32 | 22:24 | 48:56 | 140:12 | 48:56 | 48:56 | 93.2037 | 93.2037 | 140:12 | 140:12 | 93.5806 | 93.5806
16 | G.C.T.M | 1 | 1 | 19:25 | 52:50 | 55:40 | 4:20 | 60:00 | 167:15 | 79:25 | 79:25 | 91.6667 | 88.9699 | 220:05 | 220:05 | 92.342 | 89.9229
17 | F.C.S.M | 2 | 2 | 34:45 | 96:25 | 19:05 | 5:25 | 24:30 | 139:50 | 59:15 | 29:38 | 98.2986 | 95.8854 | 236:15 | 118:08 | 96.7987 | 94.5913
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 20:57 | 10:25 | 31:22 | 81:21 | 31:22 | 31:22 | 95.6435 | 95.6435 | 81:21 | 81:21 | 96.2752 | 96.2752
19 | Hole-Alur | 1 | 1 | 8:40 | 38:25 | 15:25 | 2:50 | 18:15 | 70:30 | 26:55 | 26:55 | 97.4653 | 96.2616 | 108:55 | 108:55 | 96.772 | 95.013
20 | Savanur | 2 | 2 | 15:10 | 24:40 | 35:45 | 42:00 | 77:45 | 181:10 | 92:55 | 46:28 | 94.6007 | 93.5475 | 205:50 | 102:55 | 95.8524 | 95.2877
21 | Shiggaon | 2 | 2 | 24:55 | 52:20 | 15:45 | 17:00 | 32:45 | 184:00 | 57:40 | 28:50 | 97.7257 | 95.9954 | 236:20 | 118:10 | 95.7875 | 94.5894
22 | Bankapur | 1 | 1 | 18:50 | 85:22 | 19:55 | 12:05 | 32:00 | 106:51 | 50:50 | 50:50 | 95.5556 | 92.9398 | 192:13 | 192:13 | 95.1076 | 91.1989
23 | Hangal | 2 | 2 | 1:15 | 14:25 | 23:20 | 21:25 | 44:45 | 160:20 | 46:00 | 23:00 | 96.8924 | 96.8056 | 174:45 | 87:23 | 96.3294 | 95.9993
24 | Ranebennur | 16 | 16 | 3:50 | 33:45 | 155:18 | 59:55 | 215:13 | 691:10 | 219:03 | 13:41 | 98.1318 | 98.0985 | 724:55 | 45:18 | 98.0221 | 97.9255
25 | Halageri | 2 | 2 | 40:30 | 120:40 | 8:30 | 10:10 | 18:40 | 97:35 | 59:10 | 29:35 | 98.7037 | 95.8912 | 218:15 | 109:08 | 97.7659 | 95.0034
26 | Tuminakatti | 2 | 2 | 1:05 | 2:55 | 7:55 | 5:35 | 13:30 | 57:25 | 14:35 | 7:17 | 99.0625 | 98.9873 | 60:20 | 30:10 | 98.6855 | 98.6187
27 | Kahanderayanahalli | 1 | 1 | 0:35 | 2:15 | 10:00 | 20:45 | 30:45 | 131:50 | 31:20 | 31:20 | 95.7292 | 95.6481 | 134:05 | 134:05 | 93.9637 | 93.8607
28 | Rattihalli | 1 | 1 | 0:30 | 4:25 | 11:50 | 9:50 | 21:40 | 59:10 | 22:10 | 22:10 | 96.9907 | 96.9213 | 63:35 | 63:35 | 97.2909 | 97.0887
29 | Hirekerur | 2 | 2 | 6:35 | 34:17 | 57:15 | 14:05 | 71:20 | 161:25 | 77:55 | 38:58 | 95.0463 | 94.5891 | 195:42 | 97:51 | 96.3046 | 95.5197
30 | Byadagi | 7 | 7 | 25:00 | 94:50 | 105:40 | 117:30 | 223:10 | 672:53 | 248:10 | 35:27 | 95.5721 | 95.0761 | 767:43 | 109:40 | 95.5986 | 94.9783
31 | Sirsi | 5 | 5 | 24:10 | 29:10 | 19:40 | 24:50 | 44:30 | 117:00 | 68:40 | 13:44 | 98.7639 | 98.0926 | 146:10 | 29:14 | 98.9286 | 98.6615
32 | Yellapur | 3 | 3 | 16:00 | 114:05 | 8:00 | 8:45 | 16:45 | 77:45 | 32:45 | 10:55 | 99.2245 | 98.4838 | 191:50 | 63:57 | 98.8133 | 97.0721
33 | Mundagod | 3 | 3 | 192:03 | 448:36 | 26:10 | 25:30 | 51:40 | 439:35 | 243:43 | 81:14 | 97.608 | 88.7168 | 888:11 | 296:04 | 93.2909 | 86.4441
34 | Siddapur | 2 | 2 | 63:40 | 151:10 | 8:40 | 17:10 | 25:50 | 100:50 | 89:30 | 44:45 | 98.206 | 93.7847 | 252:00 | 126:00 | 97.6915 | 94.2308
35 | Dandeli | 8 | 8 | 7:40 | 100:24 | 34:30 | 179:34 | 214:04 | 523:27 | 221:44 | 27:43 | 96.2836 | 96.1505 | 623:51 | 77:59 | 97.0041 | 96.4294
36 | Haliyal | 3 | 3 | 5:49 | 12:49 | 28:41 | 30:03 | 58:44 | 163:39 | 64:33 | 21:31 | 97.2809 | 97.0116 | 176:28 | 58:49 | 97.5023 | 97.3067
37 | Ankola | 3 | 3 | 83:36 | 152:15 | 25:06 | 24:16 | 49:22 | 91:06 | 132:58 | 44:19 | 97.7145 | 93.8441 | 243:21 | 81:07 | 98.6096 | 96.2859
38 | Kumta | 3 | 3 | 12:12 | 22:00 | 24:03 | 31:46 | 55:49 | 142:04 | 68:01 | 22:40 | 97.4159 | 96.8511 | 164:04 | 54:41 | 97.8317 | 97.4959
39 | Gokarna | 1 | 1 | 22:46 | 55:39 | 10:00 | 3:10 | 13:10 | 29:23 | 35:56 | 35:56 | 98.1713 | 95.0093 | 85:02 | 85:02 | 98.6546 | 96.1065
40 | Kasarkod | 1 | 1 | 0:00 | 38:21 | 2:25 | 0:30 | 2:55 | 17:05 | 2:55 | 2:55 | 99.5949 | 99.5949 | 55:26 | 55:26 | 99.2178 | 97.4618
41 | Honnavar | 3 | 3 | 11:54 | 66:57 | 33:43 | 44:23 | 78:06 | 148:24 | 90:00 | 30:00 | 96.3843 | 95.8333 | 215:21 | 71:47 | 97.735 | 96.7132
42 | Murdeshwar | 4 | 4 | 7:12 | 123:40 | 55:08 | 59:46 | 114:54 | 229:45 | 122:06 | 30:31 | 96.0104 | 95.7604 | 353:25 | 88:21 | 97.3701 | 95.9545
43 | Bhatkal | 3 | 3 | 50:09 | 81:27 | 27:50 | 24:06 | 51:56 | 149:12 | 102:05 | 34:02 | 97.5957 | 95.2739 | 230:39 | 76:53 | 97.7228 | 96.4797
44 | Khanapur | 2 | 2 | 12:25 | 33:55 | 17:40 | 10:50 | 28:30 | 95:40 | 40:55 | 20:28 | 98.0208 | 97.1586 | 129:35 | 64:48 | 97.8098 | 97.0333
45 | Bailhongal | 3 | 3 | 0:15 | 0:45 | 92:20 | 12:10 | 104:30 | 197:20 | 104:45 | 34:55 | 95.162 | 95.1505 | 198:05 | 66:02 | 96.9882 | 96.9768
46 | Soundatti | 3 | 3 | 0:57 | 15:57 | 22:07 | 5:46 | 27:53 | 129:33 | 28:50 | 9:37 | 98.7091 | 98.6651 | 145:30 | 48:30 | 98.0227 | 97.7793
47 | Ramdurg | 2 | 2 | 18:32 | 24:02 | 23:27 | 24:45 | 48:12 | 122:52 | 66:44 | 33:22 | 96.6528 | 95.3657 | 146:54 | 73:27 | 97.1871 | 96.6369
48 | Gokak | 11 | 11 | 36:41 | 86:02 | 244:11 | 24:03 | 268:14 | 540:42 | 304:55 | 27:43 | 96.6132 | 96.15 | 626:44 | 56:59 | 97.7493 | 97.3912
49 | Mudalagi | 2 | 2 | 15:50 | 34:10 | 29:55 | 1:55 | 31:50 | 100:55 | 47:40 | 23:50 | 97.7894 | 96.6898 | 135:05 | 67:33 | 97.6896 | 96.9074
50 | Konnur | 1 | 1 | 2:00 | 3:45 | 16:30 | 1:25 | 17:55 | 51:45 | 19:55 | 19:55 | 97.5116 | 97.2338 | 55:30 | 55:30 | 97.6305 | 97.4588
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 39:32 | 14:34 | 54:06 | 102:12 | 54:06 | 54:06 | 92.4861 | 92.4861 | 102:12 | 102:12 | 95.3205 | 95.3205
52 | Kudachi | 1 | 1 | 7:15 | 7:15 | 20:50 | 10:55 | 31:45 | 72:45 | 39:00 | 39:00 | 95.5903 | 94.5833 | 80:00 | 80:00 | 96.669 | 96.337
53 | Athani | 6 | 6 | 19:12 | 118:04 | 75:05 | 80:29 | 155:34 | 420:54 | 174:46 | 29:08 | 96.3989 | 95.9545 | 538:58 | 89:50 | 96.788 | 95.887
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 14:35 | 9:50 | 24:25 | 76:40 | 24:25 | 12:12 | 98.3044 | 98.3044 | 76:40 | 38:20 | 98.2448 | 98.2448
55 | Nippani | 5 | 5 | 0:00 | 60:50 | 51:05 | 17:35 | 68:40 | 269:15 | 68:40 | 13:44 | 98.0926 | 98.0926 | 330:05 | 66:01 | 97.5343 | 96.9773
56 | Sadalaga | 1 | 1 | 0:15 | 6:13 | 22:55 | 7:45 | 30:40 | 75:10 | 30:55 | 30:55 | 95.7407 | 95.706 | 81:23 | 81:23 | 96.5583 | 96.2737
57 | Muddebihal | 2 | 2 | 1:20 | 8:43 | 40:00 | 56:45 | 96:45 | 193:30 | 98:05 | 49:02 | 93.2812 | 93.1887 | 202:13 | 101:06 | 95.5701 | 95.3705
58 | Talikoti | 1 | 1 | 4:00 | 6:10 | 17:00 | 19:00 | 36:00 | 111:00 | 40:00 | 40:00 | 95 | 94.4444 | 117:10 | 117:10 | 94.9176 | 94.6352
59 | B.Bagewadi | 1 | 1 | 5:17 | 15:31 | 5:50 | 6:18 | 12:08 | 39:33 | 17:25 | 17:25 | 98.3148 | 97.581 | 55:04 | 55:04 | 98.1891 | 97.4786
60 | Indi | 3 | 3 | 6:31 | 8:14 | 15:07 | 15:53 | 31:00 | 83:24 | 37:31 | 12:30 | 98.5648 | 98.2631 | 91:38 | 30:33 | 98.7271 | 98.6014
61 | Sindagi | 2 | 2 | 4:40 | 26:30 | 19:55 | 14:45 | 34:40 | 100:55 | 39:20 | 19:40 | 97.5926 | 97.2685 | 127:25 | 63:42 | 97.6896 | 97.083
62 | Guledgudda | 1 | 1 | 7:25 | 19:40 | 22:04 | 7:33 | 29:37 | 53:14 | 37:02 | 37:02 | 95.8866 | 94.8565 | 72:54 | 72:54 | 97.5626 | 96.6621
63 | Ilkal | 8 | 8 | 39:39 | 86:46 | 119:03 | 143:45 | 262:48 | 773:09 | 302:27 | 37:48 | 95.4375 | 94.7491 | 859:55 | 107:29 | 95.5749 | 95.0783
64 | Kerur | 2 | 2 | 4:42 | 7:32 | 18:36 | 20:53 | 39:29 | 96:53 | 44:11 | 22:06 | 97.2581 | 96.9317 | 104:25 | 52:12 | 97.782 | 97.6095
65 | Hungund | 4 | 4 | 12:52 | 27:22 | 58:31 | 46:21 | 104:52 | 322:33 | 117:44 | 29:26 | 96.3588 | 95.912 | 349:55 | 87:29 | 96.3078 | 95.9945
66 | Gaddankeri | 4 | 4 | 12:14 | 74:00 | 37:12 | 33:32 | 70:44 | 133:25 | 82:58 | 20:44 | 97.544 | 97.1192 | 207:25 | 51:51 | 98.4728 | 97.6257
67 | Rampur | 1 | 1 | 4:09 | 21:03 | 19:27 | 6:03 | 25:30 | 39:36 | 29:39 | 29:39 | 96.4583 | 95.8819 | 60:39 | 60:39 | 98.1868 | 97.223
68 | Kaladagi | 2 | 2 | 0:15 | 0:15 | 53:36 | 39:45 | 93:21 | 195:36 | 93:36 | 46:48 | 93.5174 | 93.5 | 195:51 | 97:56 | 95.522 | 95.5163
69 | Achanur | 1 | 1 | 0:00 | 6:54 | 37:21 | 22:09 | 59:30 | 137:39 | 59:30 | 59:30 | 91.7361 | 91.7361 | 144:33 | 144:33 | 93.6973 | 93.3814
70 | Shirur | 1 | 1 | 15:13 | 30:16 | 21:15 | 55:24 | 76:39 | 106:21 | 91:52 | 91:52 | 89.3542 | 87.2407 | 136:37 | 136:37 | 95.1305 | 93.7447
71 | Badami | 1 | 1 | 11:39 | 23:18 | 12:30 | 14:12 | 26:42 | 74:33 | 38:21 | 38:21 | 96.2917 | 94.6736 | 97:51 | 97:51 | 96.5865 | 95.5197
72 | Kulageri | 1 | 1 | 0:55 | 6:38 | 5:20 | 8:45 | 14:05 | 25:45 | 15:00 | 15:00 | 98.044 | 97.9167 | 32:23 | 32:23 | 98.821 | 98.5172
73 | Jamkhandi | 5 | 5 | 22:55 | 53:20 | 85:40 | 87:15 | 172:55 | 292:50 | 195:50 | 39:10 | 95.1968 | 94.5602 | 346:10 | 69:14 | 97.3184 | 96.83
74 | Mahalingapur | 3 | 3 | 4:24 | 20:12 | 95:48 | 95:42 | 191:30 | 301:12 | 195:54 | 65:18 | 91.1343 | 90.9306 | 321:24 | 107:08 | 95.4029 | 95.0946
75 | Rabakavi | 2 | 2 | 5:50 | 9:55 | 20:25 | 21:49 | 42:14 | 81:44 | 48:04 | 24:02 | 97.0671 | 96.662 | 91:39 | 45:50 | 98.1288 | 97.9018
76 | Banahatti | 2 | 2 | 8:30 | 21:25 | 38:10 | 24:55 | 63:05 | 183:55 | 71:35 | 35:48 | 95.6192 | 95.0289 | 205:20 | 102:40 | 95.7895 | 95.2991
77 | Terdal | 1 | 1 | 1:00 | 20:45 | 22:10 | 19:35 | 41:45 | 135:15 | 42:45 | 42:45 | 94.2014 | 94.0625 | 156:00 | 156:00 | 93.8072 | 92.8571
78 | Mudhol | 4 | 4 | 12:01 | 13:27 | 49:34 | 21:30 | 71:04 | 240:32 | 83:05 | 20:46 | 97.5324 | 97.1152 | 253:59 | 63:30 | 97.2466 | 97.0927
79 | Bilagi | 1 | 1 | 4:30 | 5:10 | 14:45 | 3:35 | 18:20 | 43:15 | 22:50 | 22:50 | 97.4537 | 96.8287 | 48:25 | 48:25 | 98.0197 | 97.7831
80 | Lokapur | 2 | 2 | 0:10 | 7:37 | 89:05 | 18:00 | 107:05 | 250:00 | 107:15 | 53:38 | 92.5637 | 92.5521 | 257:37 | 128:48 | 94.2766 | 94.1022
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of July-2020
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2020 |  |  |  | Reliability for cumulative period from Apr-20 to July-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 20:03 | 74:01 | 83:52 | 234:42 | 318:34 | 1829:45 | 338:37 | 4:17 | 99.458 | 99.4239 | 1903:46 | 24:06 | 99.209 | 99.177
2 | Dharwad(R) | 19 | 19 | 0:00 | 21:46 | 117:37 | 86:02 | 203:39 | 1646:35 | 203:39 | 10:43 | 98.5594 | 98.5594 | 1668:21 | 87:48 | 97.0402 | 97.0011
3 | Kundagol | 1 | 1 | 3:05 | 41:55 | 6:25 | 5:05 | 11:30 | 58:00 | 14:35 | 14:35 | 98.4543 | 98.0399 | 99:55 | 99:55 | 98.0191 | 96.5875
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 7:14 | 8:54 | 16:08 | 82:44 | 16:08 | 16:08 | 97.8315 | 97.8315 | 82:44 | 82:44 | 97.1744 | 97.1744
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 7:05 | 7:25 | 14:30 | 100:50 | 14:30 | 14:30 | 98.0511 | 98.0511 | 100:50 | 100:50 | 96.5562 | 96.5562
6 | Kalghatagi | 2 | 2 | 0:00 | 2:20 | 8:25 | 18:00 | 26:25 | 265:35 | 26:25 | 13:12 | 98.2247 | 98.2247 | 267:55 | 133:58 | 95.4648 | 95.4249
7 | Alnavar | 1 | 1 | 1:30 | 16:45 | 12:55 | 0:55 | 13:50 | 72:20 | 15:20 | 15:20 | 98.1407 | 97.9391 | 89:05 | 89:05 | 97.5296 | 96.9575
8 | Naragund | 2 | 2 | 0:20 | 14:50 | 37:40 | 25:10 | 62:50 | 299:10 | 63:10 | 31:35 | 95.7773 | 95.7549 | 314:00 | 157:00 | 94.8913 | 94.638
9 | Shirahatti | 4 | 4 | 0:00 | 18:50 | 31:55 | 100:35 | 132:30 | 392:48 | 132:30 | 33:08 | 95.5477 | 95.5477 | 411:38 | 102:54 | 96.6462 | 96.4854
10 | Laxmeshwar | 5 | 5 | 0:00 | 0:00 | 56:38 | 44:02 | 100:40 | 416:33 | 100:40 | 20:08 | 97.2939 | 97.2939 | 416:33 | 83:19 | 97.1547 | 97.1547
11 | Naregal | 1 | 1 | 0:00 | 12:50 | 9:10 | 4:10 | 13:20 | 104:20 | 13:20 | 13:20 | 98.2079 | 98.2079 | 117:10 | 117:10 | 96.4367 | 95.9984
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 32:05 | 12:10 | 44:15 | 177:30 | 44:15 | 22:08 | 97.0262 | 97.0262 | 177:30 | 88:45 | 96.9689 | 96.9689
13 | Ron | 3 | 3 | 0:00 | 20:15 | 22:20 | 43:05 | 65:25 | 333:55 | 65:25 | 21:48 | 97.0691 | 97.0691 | 354:10 | 118:03 | 96.1986 | 95.968
14 | Mundaragi | 3 | 3 | 1:25 | 48:00 | 187:45 | 57:45 | 245:30 | 470:50 | 246:55 | 82:18 | 89.0009 | 88.9374 | 518:50 | 172:57 | 94.6399 | 94.0934
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 20:51 | 33:50 | 54:41 | 194:53 | 54:41 | 54:41 | 92.6501 | 92.6501 | 194:53 | 194:53 | 93.3441 | 93.3441
16 | G.C.T.M | 1 | 1 | 9:05 | 61:55 | 7:35 | 1:05 | 8:40 | 175:55 | 17:45 | 17:45 | 98.8351 | 97.6142 | 237:50 | 237:50 | 93.9919 | 91.8773
17 | F.C.S.M | 2 | 2 | 9:10 | 105:35 | 5:50 | 2:30 | 8:20 | 148:10 | 17:30 | 8:45 | 99.44 | 98.8239 | 253:45 | 126:52 | 97.4698 | 95.6668
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 7:27 | 4:38 | 12:05 | 93:26 | 12:05 | 12:05 | 98.3759 | 98.3759 | 93:26 | 93:26 | 96.809 | 96.809
19 | Hole-Alur | 1 | 1 | 2:10 | 40:35 | 10:35 | 2:50 | 13:25 | 83:55 | 15:35 | 15:35 | 98.1967 | 97.9055 | 124:30 | 124:30 | 97.134 | 95.748
20 | Savanur | 2 | 2 | 15:10 | 39:50 | 35:45 | 42:00 | 77:45 | 258:55 | 92:55 | 46:28 | 94.7749 | 93.7556 | 298:45 | 149:22 | 95.5786 | 94.8984
21 | Shiggaon | 2 | 2 | 24:55 | 77:15 | 17:15 | 17:00 | 34:15 | 218:15 | 59:10 | 29:35 | 97.6983 | 96.0237 | 295:30 | 147:45 | 96.2731 | 94.9539
22 | Bankapur | 1 | 1 | 18:50 | 104:12 | 19:55 | 12:05 | 32:00 | 138:51 | 50:50 | 50:50 | 95.6989 | 93.1676 | 243:03 | 243:03 | 95.2579 | 91.6991
23 | Hangal | 2 | 2 | 1:15 | 15:40 | 23:20 | 21:25 | 44:45 | 205:05 | 46:00 | 23:00 | 96.9926 | 96.9086 | 220:45 | 110:23 | 96.4979 | 96.2304
24 | Ranebennur | 16 | 16 | 14:35 | 48:20 | 202:29 | 71:13 | 273:42 | 964:52 | 288:17 | 18:01 | 97.7008 | 97.5783 | 1013:12 | 63:20 | 97.9404 | 97.8373
25 | Halageri | 2 | 2 | 64:20 | 185:00 | 97:00 | 6:20 | 103:20 | 200:55 | 167:40 | 83:50 | 93.0556 | 88.7321 | 385:55 | 192:58 | 96.569 | 93.4099
26 | Tuminakatti | 2 | 2 | 1:00 | 3:55 | 7:05 | 2:35 | 9:40 | 67:05 | 10:40 | 5:20 | 99.3504 | 99.2832 | 71:00 | 35:30 | 98.8545 | 98.7876
27 | Kahanderayanahalli | 1 | 1 | 1:15 | 3:30 | 9:00 | 8:15 | 17:15 | 149:05 | 18:30 | 18:30 | 97.6815 | 97.5134 | 152:35 | 152:35 | 94.9084 | 94.7888
28 | Rattihalli | 1 | 1 | 0:40 | 5:05 | 11:25 | 13:30 | 24:55 | 84:05 | 25:35 | 25:35 | 96.651 | 96.5614 | 89:10 | 89:10 | 97.1283 | 96.9547
29 | Hirekerur | 2 | 2 | 8:45 | 43:02 | 24:20 | 14:05 | 38:25 | 199:50 | 47:10 | 23:35 | 97.4182 | 96.8302 | 242:52 | 121:26 | 96.5875 | 95.8527
30 | Byadagi | 7 | 7 | 18:35 | 113:25 | 130:30 | 32:35 | 163:05 | 835:58 | 181:40 | 25:57 | 96.8686 | 96.5118 | 949:23 | 135:38 | 95.9213 | 95.368
31 | Sirsi | 5 | 5 | 2:35 | 31:45 | 10:58 | 29:35 | 40:33 | 157:33 | 43:08 | 8:38 | 98.9099 | 98.8405 | 189:18 | 37:52 | 98.9238 | 98.707
32 | Yellapur | 3 | 3 | 19:00 | 133:05 | 15:10 | 17:35 | 32:45 | 110:30 | 51:45 | 17:15 | 98.5327 | 97.6815 | 243:35 | 81:12 | 98.742 | 97.227
33 | Mundagod | 3 | 3 | 28:30 | 477:06 | 32:05 | 39:35 | 71:40 | 511:15 | 100:10 | 33:23 | 96.7891 | 95.5122 | 988:21 | 329:27 | 94.1798 | 88.7483
34 | Siddapur | 2 | 2 | 19:00 | 170:10 | 23:40 | 8:20 | 32:00 | 132:50 | 51:00 | 25:30 | 97.8495 | 96.5726 | 303:00 | 151:30 | 97.7317 | 94.8258
35 | Dandeli | 8 | 8 | 41:52 | 142:16 | 53:34 | 58:21 | 111:55 | 635:22 | 153:47 | 19:13 | 98.1197 | 97.4163 | 777:38 | 97:12 | 97.2875 | 96.6802
36 | Haliyal | 3 | 3 | 1:00 | 13:49 | 12:44 | 8:20 | 21:04 | 184:43 | 22:04 | 7:21 | 99.0562 | 99.0114 | 198:32 | 66:11 | 97.8971 | 97.7398
37 | Ankola | 3 | 3 | 74:52 | 227:07 | 11:54 | 10:56 | 22:50 | 113:56 | 97:42 | 32:34 | 98.977 | 95.6228 | 341:03 | 113:41 | 98.7029 | 96.1174
38 | Kumta | 3 | 3 | 0:15 | 22:15 | 17:29 | 17:05 | 34:34 | 176:38 | 34:49 | 11:36 | 98.4513 | 98.4401 | 198:53 | 66:18 | 97.9891 | 97.7358
39 | Gokarna | 1 | 1 | 12:17 | 67:56 | 9:45 | 3:40 | 13:25 | 42:48 | 25:42 | 25:42 | 98.1967 | 96.5457 | 110:44 | 110:44 | 98.5383 | 96.2181
40 | Kasarkod | 1 | 1 | 7:22 | 45:43 | 8:55 | 8:35 | 17:30 | 34:35 | 24:52 | 24:52 | 97.6478 | 96.6577 | 80:18 | 80:18 | 98.8189 | 97.2575
41 | Honnavar | 3 | 3 | 26:03 | 93:00 | 21:20 | 19:37 | 40:57 | 189:21 | 67:00 | 22:20 | 98.1653 | 96.9982 | 282:21 | 94:07 | 97.8444 | 96.7856
42 | Murdeshwar | 4 | 4 | 42:16 | 165:56 | 32:32 | 26:34 | 59:06 | 288:51 | 101:22 | 25:20 | 98.0141 | 96.5939 | 454:47 | 113:42 | 97.5337 | 96.1169
43 | Bhatkal | 3 | 3 | 47:51 | 129:18 | 22:08 | 7:51 | 29:59 | 179:11 | 77:50 | 25:57 | 98.6567 | 96.5128 | 308:29 | 102:50 | 97.9601 | 96.4881
44 | Khanapur | 2 | 2 | 2:30 | 36:25 | 11:30 | 4:55 | 16:25 | 112:05 | 18:55 | 9:27 | 98.8967 | 98.7287 | 148:30 | 74:15 | 98.086 | 97.4641
45 | Bailhongal | 3 | 3 | 0:03 | 0:48 | 25:00 | 10:20 | 35:20 | 232:40 | 35:23 | 11:48 | 98.417 | 98.4147 | 233:28 | 77:49 | 97.3512 | 97.3421
46 | Soundatti | 3 | 3 | 7:20 | 23:17 | 15:35 | 6:05 | 21:40 | 151:13 | 29:00 | 9:40 | 99.0293 | 98.7007 | 174:30 | 58:10 | 98.2785 | 98.0134
47 | Ramdurg | 2 | 2 | 0:00 | 24:02 | 12:00 | 5:55 | 17:55 | 140:47 | 17:55 | 8:58 | 98.7959 | 98.7959 | 164:49 | 82:24 | 97.5959 | 97.1855
48 | Gokak | 11 | 11 | 62:59 | 149:01 | 154:44 | 23:23 | 178:07 | 718:49 | 241:06 | 21:55 | 97.8236 | 97.054 | 867:50 | 78:54 | 97.7682 | 97.3055
49 | Mudalagi | 2 | 2 | 0:00 | 34:10 | 21:30 | 10:55 | 32:25 | 133:20 | 32:25 | 16:12 | 97.8215 | 97.8215 | 167:30 | 83:45 | 97.7231 | 97.1397
50 | Konnur | 1 | 1 | 0:00 | 3:45 | 28:00 | 5:45 | 33:45 | 85:30 | 33:45 | 33:45 | 95.4637 | 95.4637 | 89:15 | 89:15 | 97.0799 | 96.9518
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 27:45 | 23:17 | 51:02 | 153:14 | 51:02 | 51:02 | 93.1407 | 93.1407 | 153:14 | 153:14 | 94.7666 | 94.7666
52 | Kudachi | 1 | 1 | 0:00 | 7:15 | 36:45 | 10:35 | 47:20 | 120:05 | 47:20 | 47:20 | 93.638 | 93.638 | 127:20 | 127:20 | 95.8988 | 95.6512
53 | Athani | 6 | 6 | 42:52 | 160:56 | 73:50 | 64:44 | 138:34 | 559:28 | 181:26 | 30:14 | 96.8959 | 95.9356 | 720:24 | 120:04 | 96.8154 | 95.8993
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 7:40 | 13:25 | 21:05 | 97:45 | 21:05 | 10:33 | 98.5831 | 98.5831 | 97:45 | 48:52 | 98.3308 | 98.3308
55 | Nippani | 5 | 5 | 0:00 | 60:50 | 47:05 | 20:50 | 67:55 | 337:10 | 67:55 | 13:35 | 98.1743 | 98.1743 | 398:00 | 79:36 | 97.6969 | 97.2814
56 | Sadalaga | 1 | 1 | 0:52 | 7:05 | 22:00 | 4:20 | 26:20 | 101:30 | 27:12 | 27:12 | 96.4606 | 96.3441 | 108:35 | 108:35 | 96.5335 | 96.2916
57 | Muddebihal | 2 | 2 | 3:35 | 12:18 | 72:05 | 48:25 | 120:30 | 314:00 | 124:05 | 62:02 | 91.9019 | 91.6611 | 326:18 | 163:09 | 94.638 | 94.4279
58 | Talikoti | 1 | 1 | 13:00 | 19:10 | 15:00 | 2:00 | 17:00 | 128:00 | 30:00 | 30:00 | 97.7151 | 95.9677 | 147:10 | 147:10 | 95.6284 | 94.9738
59 | B.Bagewadi | 1 | 1 | 2:17 | 17:48 | 3:19 | 2:45 | 6:04 | 45:37 | 8:21 | 8:21 | 99.1846 | 98.8777 | 63:25 | 63:25 | 98.4421 | 97.8341
60 | Indi | 3 | 3 | 0:00 | 8:14 | 9:06 | 12:15 | 21:21 | 104:45 | 21:21 | 7:07 | 99.0435 | 99.0435 | 112:59 | 37:40 | 98.8075 | 98.7138
61 | Sindagi | 2 | 2 | 55:40 | 82:10 | 18:10 | 14:15 | 32:25 | 133:20 | 88:05 | 44:02 | 97.8215 | 94.0804 | 215:30 | 107:45 | 97.7231 | 96.32
62 | Guledgudda | 1 | 1 | 0:00 | 19:40 | 13:25 | 8:27 | 21:52 | 75:06 | 21:52 | 21:52 | 97.0609 | 97.0609 | 94:46 | 94:46 | 97.4351 | 96.7634
63 | Ilkal | 8 | 8 | 31:05 | 117:51 | 119:10 | 201:59 | 321:09 | 1094:18 | 352:14 | 44:02 | 94.6043 | 94.0821 | 1212:09 | 151:31 | 95.3283 | 94.8252
64 | Kerur | 2 | 2 | 6:17 | 13:49 | 12:37 | 12:45 | 25:22 | 122:15 | 31:39 | 15:50 | 98.2953 | 97.873 | 136:04 | 68:02 | 97.9124 | 97.6765
65 | Hungund | 4 | 4 | 20:30 | 47:52 | 62:41 | 23:44 | 86:25 | 408:58 | 106:55 | 26:44 | 97.0962 | 96.4074 | 456:50 | 114:12 | 96.5081 | 96.0994
66 | Gaddankeri | 4 | 4 | 0:21 | 74:21 | 49:41 | 17:27 | 67:08 | 200:33 | 67:29 | 16:52 | 97.7442 | 97.7324 | 274:54 | 68:44 | 98.2877 | 97.6528
67 | Rampur | 1 | 1 | 5:30 | 26:33 | 12:06 | 2:15 | 14:21 | 53:57 | 19:51 | 19:51 | 98.0712 | 97.332 | 80:30 | 80:30 | 98.1574 | 97.2507
68 | Kaladagi | 2 | 2 | 0:00 | 0:15 | 14:18 | 22:18 | 36:36 | 232:12 | 36:36 | 18:18 | 97.5403 | 97.5403 | 232:27 | 116:14 | 96.0348 | 96.0306
69 | Achanur | 1 | 1 | 0:00 | 6:54 | 46:00 | 21:48 | 67:48 | 205:27 | 67:48 | 67:48 | 90.8871 | 90.8871 | 212:21 | 212:21 | 92.9833 | 92.7476
70 | Shirur | 1 | 1 | 1:24 | 31:40 | 17:06 | 13:57 | 31:03 | 137:24 | 32:27 | 32:27 | 95.8266 | 95.6384 | 169:04 | 169:04 | 95.3074 | 94.2259
71 | Badami | 1 | 1 | 1:10 | 24:28 | 12:57 | 10:00 | 22:57 | 97:30 | 24:07 | 24:07 | 96.9153 | 96.7585 | 121:58 | 121:58 | 96.6701 | 95.8345
72 | Kulageri | 1 | 1 | 0:00 | 6:38 | 5:27 | 5:10 | 10:37 | 36:22 | 10:37 | 10:37 | 98.573 | 98.573 | 43:00 | 43:00 | 98.758 | 98.5314
73 | Jamkhandi | 6 | 6 | 15:00 | 68:20 | 72:25 | 21:50 | 94:15 | 387:05 | 109:15 | 18:13 | 97.8887 | 97.5526 | 455:25 | 75:54 | 97.7967 | 97.4077
74 | Mahalingapur | 3 | 3 | 22:03 | 42:15 | 71:40 | 13:04 | 84:44 | 385:56 | 106:47 | 35:36 | 96.2037 | 95.2158 | 428:11 | 142:44 | 95.6064 | 95.1254
75 | Rabakavi | 2 | 2 | 0:00 | 9:55 | 15:05 | 5:35 | 20:40 | 102:24 | 20:40 | 10:20 | 98.6111 | 98.6111 | 112:19 | 56:10 | 98.2514 | 98.082
76 | Banahatti | 2 | 2 | 18:30 | 39:55 | 62:35 | 2:45 | 65:20 | 249:15 | 83:50 | 41:55 | 95.6093 | 94.366 | 289:10 | 144:35 | 95.7437 | 95.062
77 | Teradal | 2 | 2 | 0:00 | 20:45 | 28:55 | 15:20 | 44:15 | 179:30 | 44:15 | 22:08 | 97.0262 | 97.0262 | 200:15 | 100:08 | 96.9348 | 96.5804
78 | Mudhol | 4 | 4 | 25:04 | 38:31 | 46:24 | 18:15 | 64:39 | 305:11 | 89:43 | 22:26 | 97.8276 | 96.9853 | 343:42 | 85:56 | 97.3943 | 97.0654
79 | Bilagi | 1 | 1 | 2:20 | 7:30 | 20:55 | 1:30 | 22:25 | 65:40 | 24:45 | 24:45 | 96.987 | 96.6734 | 73:10 | 73:10 | 97.7573 | 97.5011
80 | Lokapur | 2 | 2 | 0:30 | 8:07 | 45:30 | 16:10 | 61:40 | 311:40 | 62:10 | 31:05 | 95.8557 | 95.8221 | 319:47 | 159:54 | 94.6778 | 94.5392
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of August-2020
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of August-2020 |  |  |  | Reliability for cumulative period from Apr-20 to August-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 20:03 | 94:04 | 629:15 | 268:27 | 897:42 | 2727:27 | 917:45 | 11:37 | 98.4727 | 98.4386 | 2821:31 | 35:43 | 99.0598 | 99.0274
2 | Dharwad(R) | 19 | 19 | 20:25 | 42:11 | 402:43 | 304:17 | 707:00 | 2353:35 | 727:25 | 38:17 | 94.9986 | 94.8542 | 2395:46 | 126:06 | 96.6266 | 96.5661
3 | Kundagol | 1 | 1 | 9:00 | 50:55 | 3:00 | 19:00 | 22:00 | 80:00 | 31:00 | 31:00 | 97.043 | 95.8333 | 130:55 | 130:55 | 97.8214 | 96.4347
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 13:00 | 18:00 | 31:00 | 113:44 | 31:00 | 31:00 | 95.8333 | 95.8333 | 113:44 | 113:44 | 96.9027 | 96.9027
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 0:00 | 31:00 | 31:00 | 131:50 | 31:00 | 31:00 | 95.8333 | 95.8333 | 131:50 | 131:50 | 96.4098 | 96.4098
6 | Kalghatagi | 2 | 2 | 0:00 | 2:20 | 13:10 | 40:45 | 53:55 | 319:30 | 53:55 | 26:58 | 96.3766 | 96.3766 | 321:50 | 160:55 | 95.6495 | 95.6177
7 | Alnavar | 1 | 1 | 1:45 | 18:30 | 20:35 | 6:45 | 27:20 | 99:40 | 29:05 | 29:05 | 96.3262 | 96.0909 | 118:10 | 118:10 | 97.2858 | 96.782
8 | Naragund | 2 | 2 | 3:10 | 18:00 | 25:05 | 35:45 | 60:50 | 360:00 | 64:00 | 32:00 | 95.9117 | 95.6989 | 378:00 | 189:00 | 95.098 | 94.8529
9 | Shirahatti | 4 | 4 | 0:00 | 18:50 | 24:25 | 91:35 | 116:00 | 508:48 | 116:00 | 29:00 | 96.1022 | 96.1022 | 527:38 | 131:54 | 96.5359 | 96.4077
10 | Laxmeshwar | 5 | 5 | 0:00 | 0:00 | 177:31 | 41:34 | 219:05 | 635:38 | 219:05 | 43:49 | 94.1107 | 94.1107 | 635:38 | 127:08 | 96.5379 | 96.5379
11 | Naregal | 1 | 1 | 0:00 | 12:50 | 9:05 | 2:10 | 11:15 | 115:35 | 11:15 | 11:15 | 98.4879 | 98.4879 | 128:25 | 128:25 | 96.8523 | 96.5028
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 27:45 | 16:50 | 44:35 | 222:05 | 44:35 | 22:18 | 97.0038 | 97.0038 | 222:05 | 111:02 | 96.976 | 96.976
13 | Ron | 3 | 3 | 0:00 | 20:15 | 24:40 | 34:35 | 59:15 | 393:10 | 59:15 | 19:45 | 97.3454 | 97.3454 | 413:25 | 137:48 | 96.4309 | 96.2471
14 | Mundaragi | 3 | 3 | 4:45 | 52:45 | 32:30 | 18:40 | 51:10 | 522:00 | 55:55 | 18:38 | 97.7076 | 97.4948 | 574:45 | 191:35 | 95.2614 | 94.7826
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 30:31 | 23:37 | 54:08 | 249:01 | 54:08 | 54:08 | 92.724 | 92.724 | 249:01 | 249:01 | 93.2185 | 93.2185
16 | G.C.T.M | 1 | 1 | 16:00 | 77:55 | 9:20 | 1:10 | 10:30 | 186:25 | 26:30 | 26:30 | 98.5887 | 96.4382 | 264:20 | 264:20 | 94.9233 | 92.8014
17 | F.C.S.M | 2 | 2 | 22:30 | 128:05 | 8:50 | 1:25 | 10:15 | 158:25 | 32:45 | 16:23 | 99.3112 | 97.7991 | 286:30 | 143:15 | 97.8429 | 96.0989
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 10:18 | 2:00 | 12:18 | 105:44 | 12:18 | 12:18 | 98.3468 | 98.3468 | 105:44 | 105:44 | 97.1206 | 97.1206
19 | Hole-Alur | 1 | 1 | 3:10 | 43:45 | 20:20 | 1:05 | 21:25 | 105:20 | 24:35 | 24:35 | 97.1214 | 96.6958 | 149:05 | 149:05 | 97.1314 | 95.94
20 | Savanur | 2 | 2 | 6:20 | 46:10 | 75:40 | 3:20 | 79:00 | 337:55 | 85:20 | 42:40 | 94.6909 | 94.2652 | 384:05 | 192:03 | 95.3987 | 94.7701
21 | Shiggaon | 2 | 2 | 13:50 | 91:05 | 14:40 | 27:40 | 42:20 | 260:35 | 56:10 | 28:05 | 97.155 | 96.2254 | 351:40 | 175:50 | 96.4518 | 95.2115
22 | Bankapur | 1 | 1 | 10:05 | 114:17 | 28:35 | 12:55 | 41:30 | 180:21 | 51:35 | 51:35 | 94.422 | 93.0668 | 294:38 | 294:38 | 95.0885 | 91.9762
23 | Hangal | 2 | 2 | 1:30 | 17:10 | 44:00 | 14:25 | 58:25 | 263:30 | 59:55 | 29:58 | 96.0741 | 95.9733 | 280:40 | 140:20 | 96.412 | 96.1783
24 | Ranebennur | 16 | 16 | 11:00 | 59:20 | 127:06 | 58:45 | 185:51 | 1150:43 | 196:51 | 12:18 | 98.4388 | 98.3464 | 1210:03 | 75:38 | 98.0414 | 97.9404
25 | Halageri | 2 | 2 | 16:40 | 201:40 | 20:40 | 2:45 | 23:25 | 224:20 | 40:05 | 20:03 | 98.4263 | 97.3062 | 426:00 | 213:00 | 96.9454 | 94.1993
26 | Tuminakatti | 2 | 2 | 0:55 | 4:50 | 5:05 | 0:00 | 5:05 | 72:10 | 6:00 | 3:00 | 99.6584 | 99.5968 | 77:00 | 38:30 | 99.0173 | 98.9515
27 | Kahanderayanahalli | 1 | 1 | 1:15 | 4:45 | 8:05 | 81:35 | 89:40 | 238:45 | 90:55 | 90:55 | 87.948 | 87.78 | 243:30 | 243:30 | 93.4981 | 93.3687
28 | Rattihalli | 1 | 1 | 0:50 | 5:55 | 18:45 | 7:05 | 25:50 | 109:55 | 26:40 | 26:40 | 96.5278 | 96.4158 | 115:50 | 115:50 | 97.0066 | 96.8455
29 | Hirekerur | 2 | 2 | 12:10 | 55:12 | 21:15 | 6:40 | 27:55 | 227:45 | 40:05 | 20:02 | 98.1239 | 97.3062 | 282:57 | 141:28 | 96.8988 | 96.1472
30 | Byadagi | 7 | 7 | 4:45 | 118:10 | 406:25 | 61:05 | 467:30 | 1303:28 | 472:15 | 67:28 | 91.0234 | 90.9322 | 1421:38 | 203:05 | 94.9289 | 94.4692
31 | Sirsi | 5 | 5 | 2:55 | 34:40 | 33:51 | 48:15 | 82:06 | 239:39 | 85:01 | 17:00 | 97.793 | 97.7146 | 274:19 | 54:52 | 98.6947 | 98.5059
32 | Yellapur | 3 | 3 | 49:01 | 182:06 | 17:50 | 36:50 | 54:40 | 165:10 | 103:41 | 34:34 | 97.5508 | 95.3547 | 347:16 | 115:45 | 98.5007 | 96.8476
33 | Mundagod | 3 | 3 | 202:00 | 679:06 | 96:55 | 42:55 | 139:50 | 651:05 | 341:50 | 113:57 | 93.7351 | 84.6849 | 1330:11 | 443:24 | 94.0897 | 87.925
34 | Siddapur | 2 | 2 | 134:40 | 304:50 | 12:00 | 77:25 | 89:25 | 222:15 | 224:05 | 112:02 | 93.9908 | 84.9406 | 527:05 | 263:33 | 96.9737 | 92.8229
35 | Dandeli | 8 | 8 | 9:56 | 152:12 | 45:55 | 137:52 | 183:47 | 819:09 | 193:43 | 24:13 | 96.9122 | 96.7454 | 971:21 | 121:25 | 97.2115 | 96.6934
36 | Haliyal | 3 | 3 | 0:53 | 14:42 | 48:09 | 25:03 | 73:12 | 257:55 | 74:05 | 24:42 | 96.7204 | 96.6809 | 272:37 | 90:52 | 97.6587 | 97.5253
37 | Ankola | 3 | 3 | 81:58 | 309:05 | 11:22 | 220:02 | 231:24 | 345:20 | 313:22 | 104:27 | 89.6326 | 85.9603 | 654:25 | 218:08 | 96.8652 | 94.0594
38 | Kumta | 3 | 3 | 13:33 | 35:48 | 67:12 | 50:32 | 117:44 | 294:22 | 131:17 | 43:46 | 94.7252 | 94.1181 | 330:10 | 110:03 | 97.3278 | 97.0028
39 | Gokarna | 1 | 1 | 11:30 | 79:26 | 3:45 | 0:35 | 4:20 | 47:08 | 15:50 | 15:50 | 99.4176 | 97.8719 | 126:34 | 126:34 | 98.7164 | 96.5532
40 | Kasarkod | 1 | 1 | 47:33 | 93:16 | 11:30 | 15:10 | 26:40 | 61:15 | 74:13 | 74:13 | 96.4158 | 90.0246 | 154:31 | 154:31 | 98.332 | 95.792
41 | Honnavar | 3 | 3 | 7:06 | 100:06 | 31:32 | 18:30 | 50:02 | 239:23 | 57:08 | 19:03 | 97.7584 | 97.4403 | 339:29 | 113:10 | 97.8269 | 96.9183
42 | Murdeshwar | 4 | 4 | 9:44 | 175:40 | 48:23 | 54:33 | 102:56 | 391:47 | 112:40 | 28:10 | 96.5412 | 96.2142 | 567:27 | 141:52 | 97.3326 | 96.1366
43 | Bhatkal | 3 | 3 | 34:57 | 164:15 | 17:52 | 13:13 | 31:05 | 210:16 | 66:02 | 22:01 | 98.6074 | 97.0415 | 374:31 | 124:50 | 98.0913 | 96.6002
44 | Khanapur | 2 | 2 | 6:15 | 42:40 | 22:15 | 40:50 | 63:05 | 175:10 | 69:20 | 34:40 | 95.7605 | 95.3405 | 217:50 | 108:55 | 97.6148 | 97.0339
45 | Bailhongal | 3 | 3 | 3:00 | 3:48 | 17:00 | 13:48 | 30:48 | 263:28 | 33:48 | 11:16 | 98.6201 | 98.4857 | 267:16 | 89:05 | 97.6083 | 97.5738
46 | Soundatti | 3 | 3 | 15:04 | 38:21 | 37:24 | 7:34 | 44:58 | 196:11 | 60:02 | 20:01 | 97.9854 | 97.3103 | 234:32 | 78:11 | 98.2191 | 97.871
47 | Ramdurg | 2 | 2 | 8:30 | 32:32 | 23:04 | 4:45 | 27:49 | 168:36 | 36:19 | 18:10 | 98.1306 | 97.5594 | 201:08 | 100:34 | 97.7042 | 97.2613
48 | Gokak | 10 | 10 | 43:12 | 192:13 | 11:24 | 27:49 | 39:13 | 758:02 | 82:25 | 8:14 | 99.4729 | 98.8922 | 950:15 | 95:02 | 97.9356 | 97.4122
49 | Mudalagi | 2 | 2 | 0:00 | 34:10 | 19:20 | 3:20 | 22:40 | 156:00 | 22:40 | 11:20 | 98.4767 | 98.4767 | 190:10 | 95:05 | 97.8758 | 97.4106
50 | Konnur | 1 | 1 | 0:00 | 3:45 | 15:55 | 1:50 | 17:45 | 103:15 | 17:45 | 17:45 | 97.6142 | 97.6142 | 107:00 | 107:00 | 97.1882 | 97.0861
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 25:10 | 10:22 | 35:32 | 188:46 | 35:32 | 35:32 | 95.224 | 95.224 | 188:46 | 188:46 | 94.8593 | 94.8593
52 | Kudachi | 1 | 1 | 0:00 | 7:15 | 20:30 | 41:15 | 61:45 | 181:50 | 61:45 | 61:45 | 91.7003 | 91.7003 | 189:05 | 189:05 | 95.0481 | 94.8507
53 | Athani | 6 | 6 | 27:12 | 188:08 | 47:27 | 38:04 | 85:31 | 644:59 | 112:43 | 18:47 | 98.0843 | 97.475 | 833:07 | 138:51 | 97.0725 | 96.2186
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 5:45 | 8:45 | 14:30 | 112:15 | 14:30 | 7:15 | 99.0255 | 99.0255 | 112:15 | 56:08 | 98.4715 | 98.4715
55 | Nippani | 5 | 5 | 0:00 | 60:50 | 37:30 | 17:20 | 54:50 | 392:00 | 54:50 | 10:58 | 98.526 | 98.526 | 452:50 | 90:34 | 97.8649 | 97.5336
56 | Sadalaga | 1 | 1 | 0:00 | 7:05 | 24:00 | 8:20 | 32:20 | 133:50 | 32:20 | 32:20 | 95.6541 | 95.6541 | 140:55 | 140:55 | 96.3553 | 96.1624
57 | Muddebihal | 2 | 2 | 5:20 | 17:38 | 45:10 | 19:20 | 64:30 | 378:30 | 69:50 | 34:55 | 95.6653 | 95.3069 | 396:08 | 198:04 | 94.8461 | 94.606
58 | Talikoti | 1 | 1 | 1:35 | 20:45 | 6:20 | 7:00 | 13:20 | 141:20 | 14:55 | 14:55 | 98.2079 | 97.9951 | 162:05 | 162:05 | 96.1511 | 95.586
59 | B.Bagewadi | 1 | 1 | 2:41 | 20:29 | 3:35 | 2:50 | 6:25 | 52:02 | 9:06 | 9:06 | 99.1375 | 98.7769 | 72:31 | 72:31 | 98.583 | 98.0251
60 | Indi | 3 | 3 | 1:03 | 9:17 | 12:15 | 18:26 | 30:41 | 135:26 | 31:44 | 10:35 | 98.6253 | 98.5783 | 144:43 | 48:14 | 98.7706 | 98.6863
61 | Sindagi | 2 | 2 | 23:10 | 105:20 | 31:55 | 5:10 | 37:05 | 170:25 | 60:15 | 30:08 | 97.5078 | 95.9509 | 275:45 | 137:52 | 97.6795 | 96.2452
62 | Guledgudda | 1 | 1 | 0:00 | 19:40 | 13:25 | 8:27 | 21:52 | 96:58 | 21:52 | 21:52 | 97.0609 | 97.0609 | 116:38 | 116:38 | 97.3593 | 96.8237
63 | Ilkal | 8 | 8 | 27:48 | 145:39 | 111:22 | 156:31 | 267:53 | 1362:11 | 295:41 | 36:58 | 95.4993 | 95.0322 | 1507:50 | 188:29 | 95.3629 | 94.8671
64 | Kerur | 2 | 2 | 1:47 | 15:36 | 9:45 | 5:22 | 15:07 | 137:22 | 16:54 | 8:27 | 98.9841 | 98.8642 | 152:58 | 76:29 | 98.1295 | 97.9171
65 | Hungund | 4 | 4 | 13:48 | 61:40 | 56:48 | 11:10 | 67:58 | 476:56 | 81:46 | 20:26 | 97.7162 | 97.2525 | 538:36 | 134:39 | 96.7529 | 96.3331
66 | Gaddankeri | 3 | 3 | 2:40 | 77:01 | 40:21 | 34:47 | 75:08 | 275:41 | 77:48 | 25:56 | 96.6338 | 96.5143 | 352:42 | 117:34 | 97.4974 | 96.7983
67 | Rampur | 1 | 1 | 3:31 | 30:04 | 15:21 | 1:57 | 17:18 | 71:15 | 20:49 | 20:49 | 97.6747 | 97.2021 | 101:19 | 101:19 | 98.0596 | 97.2408
68 | Kaladagi | 2 | 2 | 7:27 | 7:42 | 26:27 | 24:27 | 50:54 | 283:06 | 58:21 | 29:11 | 96.5793 | 96.0786 | 290:48 | 145:24 | 96.1452 | 96.0403
69 | Achanur | 1 | 1 | 0:30 | 7:24 | 30:03 | 22:18 | 52:21 | 257:48 | 52:51 | 52:51 | 92.9637 | 92.8965 | 265:12 | 265:12 | 92.9793 | 92.7778
70 | Shirur | 1 | 1 | 3:07 | 34:47 | 9:12 | 3:18 | 12:30 | 149:54 | 15:37 | 15:37 | 98.3199 | 97.901 | 184:41 | 184:41 | 95.9178 | 94.9705
71 | Badami | 1 | 1 | 0:59 | 25:27 | 7:11 | 4:11 | 11:22 | 108:52 | 12:21 | 12:21 | 98.4722 | 98.3401 | 134:19 | 134:19 | 97.0352 | 96.3421
72 | Kulageri | 1 | 1 | 1:25 | 8:03 | 17:20 | 8:40 | 26:00 | 62:22 | 27:25 | 27:25 | 96.5054 | 96.315 | 70:25 | 70:25 | 98.3016 | 98.0823
73 | Jamkhandi | 6 | 6 | 2:00 | 70:20 | 92:15 | 27:05 | 119:20 | 506:25 | 121:20 | 20:13 | 97.3268 | 97.282 | 576:45 | 96:08 | 97.7014 | 97.3822
74 | Mahalingapur | 3 | 3 | 13:26 | 55:41 | 45:07 | 12:07 | 57:14 | 443:10 | 70:40 | 23:33 | 97.4358 | 96.8339 | 498:51 | 166:17 | 95.9771 | 95.4716
75 | Rabakavi | 2 | 2 | 0:45 | 10:40 | 15:55 | 7:45 | 23:40 | 126:04 | 24:25 | 12:12 | 98.4095 | 98.3591 | 136:44 | 68:22 | 98.2834 | 98.1382
76 | Banahatti | 2 | 2 | 0:00 | 39:55 | 29:35 | 2:20 | 31:55 | 281:10 | 31:55 | 15:58 | 97.8551 | 97.8551 | 321:05 | 160:32 | 96.1715 | 95.628
77 | Teradal | 2 | 2 | 2:25 | 23:10 | 116:30 | 10:20 | 126:50 | 306:20 | 129:15 | 64:38 | 91.4763 | 91.3138 | 329:30 | 164:45 | 95.8288 | 95.5133
78 | Mudhol | 4 | 4 | 6:12 | 44:43 | 72:27 | 9:24 | 81:51 | 387:02 | 88:03 | 22:01 | 97.2497 | 97.0413 | 431:45 | 107:56 | 97.365 | 97.0605
79 | Bilagi | 1 | 1 | 2:10 | 9:40 | 14:35 | 1:30 | 16:05 | 81:45 | 18:15 | 18:15 | 97.8383 | 97.547 | 91:25 | 91:25 | 97.7737 | 97.5104
80 | Lokapur | 2 | 2 | 1:30 | 9:37 | 60:10 | 11:55 | 72:05 | 383:45 | 73:35 | 36:48 | 95.1557 | 95.0549 | 393:22 | 196:41 | 94.7746 | 94.6437
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of September-2020
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of September-2020 |  |  |  | Reliability for cumulative period from Apr-20 to September-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 20:03 | 114:07 | 357:39 | 269:25 | 627:04 | 3354:31 | 647:07 | 8:11 | 98.8976 | 98.8623 | 3468:38 | 43:54 | 99.0332 | 99.0003
2 | Dharwad(R) | 19 | 19 | 19:55 | 62:06 | 332:28 | 197:54 | 530:22 | 2883:57 | 550:17 | 28:58 | 96.1231 | 95.9775 | 2946:03 | 155:03 | 96.544 | 96.4696
3 | Kundagol | 1 | 1 | 16:45 | 67:40 | 6:45 | 10:05 | 16:50 | 96:50 | 33:35 | 33:35 | 97.662 | 95.3356 | 164:30 | 164:30 | 97.7952 | 96.2546
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 13:38 | 10:58 | 24:36 | 138:20 | 24:36 | 24:36 | 96.5833 | 96.5833 | 138:20 | 138:20 | 96.8503 | 96.8503
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 3:35 | 1:55 | 5:30 | 137:20 | 5:30 | 5:30 | 99.2361 | 99.2361 | 137:20 | 137:20 | 96.8731 | 96.8731
6 | Kalghatagi | 2 | 2 | 0:00 | 2:20 | 8:55 | 30:55 | 39:50 | 359:20 | 39:50 | 19:55 | 97.2338 | 97.2338 | 361:40 | 180:50 | 95.9092 | 95.8827
7 | Alnavar | 1 | 1 | 2:00 | 20:30 | 14:50 | 2:00 | 16:50 | 116:30 | 18:50 | 18:50 | 97.662 | 97.3843 | 137:00 | 137:00 | 97.3474 | 96.8807
8 | Naragund | 2 | 2 | 5:20 | 23:20 | 16:00 | 17:40 | 33:40 | 393:40 | 39:00 | 19:30 | 97.662 | 97.2917 | 417:00 | 208:30 | 95.5184 | 95.2527
9 | Shirahatti | 4 | 4 | 0:00 | 18:50 | 18:05 | 80:55 | 99:00 | 607:48 | 99:00 | 24:45 | 96.5625 | 96.5625 | 626:38 | 156:40 | 96.5403 | 96.4331
10 | Laxmeshwar | 5 | 5 | 0:00 | 0:00 | 38:58 | 18:31 | 57:29 | 693:07 | 57:29 | 11:30 | 98.4032 | 98.4032 | 693:07 | 138:37 | 96.8437 | 96.8437
11 | Naregal | 1 | 1 | 2:00 | 14:50 | 8:35 | 1:55 | 10:30 | 126:05 | 12:30 | 12:30 | 98.5417 | 98.2639 | 140:55 | 140:55 | 97.1293 | 96.7915
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 23:50 | 16:45 | 40:35 | 262:40 | 40:35 | 20:18 | 97.1817 | 97.1817 | 262:40 | 131:20 | 97.0097 | 97.0097
13 | Ron | 3 | 3 | 8:00 | 28:15 | 56:10 | 18:00 | 74:10 | 467:20 | 82:10 | 27:23 | 96.5664 | 96.196 | 495:35 | 165:12 | 96.4531 | 96.2387
14 | Mundaragi | 3 | 3 | 11:55 | 64:40 | 8:45 | 36:00 | 44:45 | 566:45 | 56:40 | 18:53 | 97.9282 | 97.3765 | 631:25 | 210:28 | 95.6986 | 95.2078
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 23:05 | 14:15 | 37:20 | 286:21 | 37:20 | 37:20 | 94.8148 | 94.8148 | 286:21 | 286:21 | 93.4802 | 93.4802
16 | G.C.T.M | 1 | 1 | 16:35 | 94:30 | 3:55 | 3:05 | 7:00 | 193:25 | 23:35 | 23:35 | 99.0278 | 96.7245 | 287:55 | 287:55 | 95.5962 | 93.4445
17 | F.C.S.M | 2 | 2 | 44:05 | 172:10 | 100:10 | 1:50 | 102:00 | 260:25 | 146:05 | 73:03 | 92.9167 | 89.8553 | 432:35 | 216:18 | 97.0353 | 95.0753
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 3:58 | 8:44 | 12:42 | 118:26 | 12:42 | 12:42 | 98.2361 | 98.2361 | 118:26 | 118:26 | 97.3034 | 97.3034
19 | Hole-Alur | 1 | 1 | 4:30 | 48:15 | 15:05 | 0:55 | 16:00 | 121:20 | 20:30 | 20:30 | 97.7778 | 97.1528 | 169:35 | 169:35 | 97.2374 | 96.1388
20 | Savanur | 2 | 2 | 11:05 | 57:15 | 74:00 | 12:00 | 86:00 | 423:55 | 97:05 | 48:33 | 94.0278 | 93.2581 | 481:10 | 240:35 | 95.174 | 94.5222
21 | Shiggaon | 2 | 2 | 17:20 | 108:25 | 96:45 | 20:10 | 116:55 | 377:30 | 134:15 | 67:08 | 91.8808 | 90.6771 | 485:55 | 242:58 | 95.7024 | 94.4682
22 | Bankapur | 1 | 1 | 11:15 | 125:32 | 14:25 | 5:30 | 19:55 | 200:16 | 31:10 | 31:10 | 97.2338 | 95.6713 | 325:48 | 325:48 | 95.4402 | 92.582
23 | Hangal | 2 | 2 | 6:45 | 23:55 | 28:55 | 14:10 | 43:05 | 306:35 | 49:50 | 24:55 | 97.0081 | 96.5394 | 330:30 | 165:15 | 96.5098 | 96.2375
24 | Ranebennur | 16 | 16 | 21:09 | 80:29 | 955:49 | 51:10 | 1006:59 | 2157:42 | 1028:08 | 64:16 | 91.2588 | 91.0752 | 2238:11 | 139:53 | 96.9295 | 96.815
25 | Halageri | 2 | 2 | 42:05 | 243:45 | 30:40 | 1:35 | 32:15 | 256:35 | 74:20 | 37:10 | 97.7604 | 94.838 | 500:20 | 250:10 | 97.079 | 94.304
26 | Tuminakatti | 2 | 2 | 1:35 | 6:25 | 17:40 | 2:25 | 20:05 | 92:15 | 21:40 | 10:50 | 98.6053 | 98.4954 | 98:40 | 49:20 | 98.9498 | 98.8767
27 | Kahanderayanahalli | 1 | 1 | 0:35 | 5:20 | 2:35 | 11:10 | 13:45 | 252:30 | 14:20 | 14:20 | 98.0903 | 98.0093 | 257:50 | 257:50 | 94.2509 | 94.1295
28 | Rattihalli | 1 | 1 | 2:30 | 8:25 | 4:55 | 9:35 | 14:30 | 124:25 | 17:00 | 17:00 | 97.9861 | 97.6389 | 132:50 | 132:50 | 97.1672 | 96.9756
29 | Hirekerur | 2 | 2 | 20:55 | 76:07 | 37:20 | 65:35 | 102:55 | 330:40 | 123:50 | 61:55 | 92.853 | 91.4005 | 406:47 | 203:24 | 96.2356 | 95.369
30 | Byadagi | 7 | 7 | 11:15 | 129:25 | 94:25 | 78:10 | 172:35 | 1476:03 | 183:50 | 26:16 | 96.5757 | 96.3525 | 1605:28 | 229:21 | 95.1989 | 94.778
31 | Sirsi | 5 | 5 | 0:00 | 34:40 | 76:15 | 12:15 | 88:30 | 328:09 | 88:30 | 17:42 | 97.5417 | 97.5417 | 362:49 | 72:34 | 98.5057 | 98.3478
32 | Yellapur | 3 | 3 | 10:25 | 192:31 | 9:55 | 6:55 | 16:50 | 182:00 | 27:15 | 9:05 | 99.2207 | 98.7384 | 374:31 | 124:50 | 98.6187 | 97.1576
33 | Mundagod | 3 | 3 | 3:15 | 682:21 | 55:10 | 31:05 | 86:15 | 737:20 | 89:30 | 29:50 | 96.0069 | 95.8565 | 1419:41 | 473:14 | 94.404 | 89.2252
34 | Siddapur | 2 | 2 | 0:00 | 304:50 | 2:40 | 21:55 | 24:35 | 246:50 | 24:35 | 12:18 | 98.2928 | 98.2928 | 551:40 | 275:50 | 97.19 | 93.7196
35 | Dandeli | 8 | 8 | 3:00 | 155:12 | 71:46 | 80:00 | 151:46 | 970:55 | 154:46 | 19:21 | 97.3652 | 97.3131 | 1126:07 | 140:46 | 97.2367 | 96.795
36 | Haliyal | 3 | 3 | 11:20 | 26:02 | 33:38 | 15:31 | 49:09 | 307:04 | 60:29 | 20:10 | 97.7245 | 97.1998 | 333:06 | 111:02 | 97.6695 | 97.4719
37 | Ankola | 3 | 3 | 51:53 | 360:58 | 9:29 | 0:00 | 9:29 | 354:49 | 61:22 | 20:27 | 99.561 | 97.159 | 715:47 | 238:36 | 97.3071 | 94.5675
38 | Kumta | 3 | 3 | 2:03 | 37:51 | 30:06 | 17:53 | 47:59 | 342:21 | 50:02 | 16:41 | 97.7785 | 97.6836 | 380:12 | 126:44 | 97.4017 | 97.1145
39 | Gokarna | 1 | 1 | 2:51 | 82:17 | 1:00 | 0:40 | 1:40 | 48:48 | 4:31 | 4:31 | 99.7685 | 99.3727 | 131:05 | 131:05 | 98.8889 | 97.0154
40 | Kasarkod | 1 | 1 | 36:41 | 129:57 | 9:50 | 12:55 | 22:45 | 84:00 | 59:26 | 59:26 | 96.8403 | 91.7454 | 213:57 | 213:57 | 98.0874 | 95.1286
41 | Honnavar | 3 | 3 | 2:09 | 102:15 | 31:13 | 11:22 | 42:35 | 281:58 | 44:44 | 14:55 | 98.0285 | 97.929 | 384:13 | 128:04 | 97.86 | 97.084
42 | Murdeshwar | 4 | 4 | 3:04 | 178:44 | 49:35 | 21:11 | 70:46 | 462:33 | 73:50 | 18:28 | 97.5428 | 97.4363 | 641:17 | 160:19 | 97.3671 | 96.3497
43 | Bhatkal | 3 | 3 | 17:51 | 182:06 | 27:07 | 5:43 | 32:50 | 243:06 | 50:41 | 16:54 | 98.4799 | 97.6535 | 425:12 | 141:44 | 98.155 | 96.7729
44 | Khanapur | 2 | 2 | 35:05 | 77:45 | 6:35 | 4:30 | 11:05 | 186:15 | 46:10 | 23:05 | 99.2303 | 96.794 | 264:00 | 132:00 | 97.8797 | 96.9945
45 | Bailhongal | 3 | 3 | 4:35 | 8:23 | 19:30 | 26:15 | 45:45 | 309:13 | 50:20 | 16:47 | 97.8819 | 97.6698 | 317:36 | 105:52 | 97.6532 | 97.5896
46 | Soundatti | 3 | 3 | 16:35 | 54:56 | 26:35 | 14:20 | 40:55 | 237:06 | 57:30 | 19:10 | 98.1057 | 97.338 | 292:02 | 97:21 | 98.2005 | 97.7836
47 | Ramdurg | 2 | 2 | 14:20 | 46:52 | 25:00 | 14:30 | 39:30 | 208:06 | 53:50 | 26:55 | 97.2569 | 96.2616 | 254:58 | 127:29 | 97.6309 | 97.0974
48 | Gokak | 10 | 10 | 65:34 | 257:47 | 165:52 | 33:56 | 199:48 | 957:50 | 265:22 | 26:32 | 97.225 | 96.3144 | 1215:37 | 121:34 | 97.8191 | 97.2322
49 | Mudalagi | 2 | 2 | 16:20 | 50:30 | 34:55 | 21:15 | 56:10 | 212:10 | 72:30 | 36:15 | 96.0995 | 94.9653 | 262:40 | 131:20 | 97.5846 | 97.0097
50 | Konnur | 1 | 1 | 0:00 | 3:45 | 18:55 | 2:25 | 21:20 | 124:35 | 21:20 | 21:20 | 97.037 | 97.037 | 128:20 | 128:20 | 97.1634 | 97.078
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 27:05 | 5:10 | 32:15 | 221:01 | 32:15 | 32:15 | 95.5208 | 95.5208 | 221:01 | 221:01 | 94.9677 | 94.9677
52 | Kudachi | 1 | 1 | 0:00 | 7:15 | 23:55 | 7:00 | 30:55 | 212:45 | 30:55 | 30:55 | 95.706 | 95.706 | 220:00 | 220:00 | 95.156 | 94.9909
53 | Athani | 6 | 6 | 12:44 | 200:52 | 39:32 | 52:00 | 91:32 | 736:31 | 104:16 | 17:23 | 97.8812 | 97.5864 | 937:23 | 156:14 | 97.2051 | 96.4428
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 7:40 | 6:50 | 14:30 | 126:45 | 14:30 | 7:15 | 98.9931 | 98.9931 | 126:45 | 63:23 | 98.557 | 98.557
55 | Nippani | 5 | 5 | 0:00 | 60:50 | 52:40 | 22:05 | 74:45 | 466:45 | 74:45 | 14:57 | 97.9236 | 97.9236 | 527:35 | 105:31 | 97.8745 | 97.5975
56 | Sadalaga | 1 | 1 | 0:00 | 7:05 | 12:50 | 3:05 | 15:55 | 149:45 | 15:55 | 15:55 | 97.7894 | 97.7894 | 156:50 | 156:50 | 96.5904 | 96.4291
57 | Muddebihal | 2 | 2 | 1:20 | 18:58 | 45:00 | 33:25 | 78:25 | 456:55 | 79:45 | 39:52 | 94.5544 | 94.4618 | 475:53 | 237:56 | 94.7983 | 94.5824
58 | Talikoti | 1 | 1 | 11:45 | 32:30 | 16:00 | 5:00 | 21:00 | 162:20 | 32:45 | 32:45 | 97.0833 | 95.4514 | 194:50 | 194:50 | 96.3039 | 95.5639
59 | B.Bagewadi | 1 | 1 | 1:05 | 21:34 | 3:06 | 28:08 | 31:14 | 83:16 | 32:19 | 32:19 | 95.662 | 95.5116 | 104:50 | 104:50 | 98.1041 | 97.6131
60 | Indi | 3 | 3 | 5:06 | 14:23 | 13:59 | 14:12 | 28:11 | 163:37 | 33:17 | 11:06 | 98.6952 | 98.4591 | 178:00 | 59:20 | 98.7582 | 98.6491
61 | Sindagi | 2 | 2 | 19:20 | 124:40 | 13:25 | 14:05 | 27:30 | 197:55 | 46:50 | 23:25 | 98.0903 | 96.7477 | 322:35 | 161:18 | 97.7469 | 96.3276
62 | Guledgudda | 1 | 1 | 1:45 | 21:25 | 11:18 | 4:20 | 15:38 | 112:36 | 17:23 | 17:23 | 97.8287 | 97.5856 | 134:01 | 134:01 | 97.4362 | 96.9486
63 | Ilkal | 8 | 8 | 66:35 | 212:14 | 326:47 | 151:17 | 478:04 | 1840:15 | 544:39 | 68:05 | 91.7002 | 90.5443 | 2052:29 | 256:34 | 94.7625 | 94.1585
64 | Kerur | 2 | 2 | 4:04 | 19:40 | 16:34 | 9:39 | 26:13 | 163:35 | 30:17 | 15:08 | 98.1794 | 97.897 | 183:15 | 91:38 | 98.1377 | 97.9138
65 | Hungund | 4 | 4 | 41:54 | 103:34 | 65:36 | 29:18 | 94:54 | 571:50 | 136:48 | 34:12 | 96.7049 | 95.25 | 675:24 | 168:51 | 96.745 | 96.1555
66 | Gaddankeri | 3 | 3 | 22:58 | 99:59 | 54:13 | 51:22 | 105:35 | 381:16 | 128:33 | 42:51 | 95.1119 | 94.0486 | 481:15 | 160:25 | 97.1064 | 96.3475
67 | Rampur | 1 | 1 | 10:12 | 40:16 | 9:21 | 7:06 | 16:27 | 87:42 | 26:39 | 26:39 | 97.7153 | 96.2986 | 127:58 | 127:58 | 98.0032 | 97.0864
68 | Kaladagi | 2 | 2 | 7:45 | 15:27 | 16:57 | 26:54 | 43:51 | 326:57 | 51:36 | 25:48 | 96.9549 | 96.4167 | 342:24 | 171:12 | 96.2779 | 96.102
69 | Achanur | 1 | 1 | 4:12 | 11:36 | 32:33 | 8:15 | 40:48 | 298:36 | 45:00 | 45:00 | 94.3333 | 93.75 | 310:12 | 310:12 | 93.2013 | 92.9372
70 | Shirur | 1 | 1 | 1:30 | 36:17 | 7:20 | 17:35 | 24:55 | 174:49 | 26:25 | 26:25 | 96.5394 | 96.331 | 211:06 | 211:06 | 96.0197 | 95.1935
71 | Badami | 1 | 1 | 2:07 | 27:34 | 11:57 | 7:45 | 19:42 | 128:34 | 21:49 | 21:49 | 97.2639 | 96.9699 | 156:08 | 156:08 | 97.0727 | 96.4451
72 | Kulageri | 1 | 1 | 2:33 | 10:36 | 11:15 | 3:45 | 15:00 | 77:22 | 17:33 | 17:33 | 97.9167 | 97.5625 | 87:58 | 87:58 | 98.2385 | 97.9971
73 | Jamkhandi | 6 | 6 | 14:00 | 84:20 | 94:10 | 31:45 | 125:55 | 632:20 | 139:55 | 23:19 | 97.0853 | 96.7612 | 716:40 | 119:27 | 97.6004 | 97.2804
74 | Mahalingapur | 3 | 3 | 4:28 | 60:09 | 48:34 | 13:16 | 61:50 | 505:00 | 66:18 | 22:06 | 97.1373 | 96.9306 | 565:09 | 188:23 | 96.1673 | 95.7108
75 | Rabakavi | 2 | 2 | 2:10 | 12:50 | 10:45 | 13:30 | 24:15 | 150:19 | 26:25 | 13:12 | 98.316 | 98.1655 | 163:09 | 81:35 | 98.2887 | 98.1426
76 | Banahatti | 2 | 2 | 1:50 | 41:45 | 23:35 | 4:30 | 28:05 | 309:15 | 29:55 | 14:57 | 98.0498 | 97.9225 | 351:00 | 175:30 | 96.4794 | 96.0041
77 | Teradal | 2 | 2 | 5:40 | 28:50 | 26:00 | 6:05 | 32:05 | 338:25 | 37:45 | 18:52 | 97.772 | 97.3785 | 367:15 | 183:38 | 96.1474 | 95.8191
78 | Mudhol | 4 | 4 | 7:52 | 52:35 | 74:40 | 12:07 | 86:47 | 473:49 | 94:39 | 23:40 | 96.9867 | 96.7135 | 526:24 | 131:36 | 97.303 | 97.0036
79 | Bilagi | 1 | 1 | 1:10 | 10:50 | 19:35 | 1:25 | 21:00 | 102:45 | 22:10 | 22:10 | 97.0833 | 96.9213 | 113:35 | 113:35 | 97.6605 | 97.4139
80 | Lokapur | 2 | 2 | 1:00 | 10:37 | 49:35 | 64:15 | 113:50 | 497:35 | 114:50 | 57:25 | 92.0949 | 92.0255 | 508:12 | 254:06 | 94.3353 | 94.2145
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of October-2020
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of October-2020 |  |  |  | Reliability for cumulative period from April-20 to October-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 20:03 | 134:10 | 382:37 | 215:59 | 598:36 | 3953:07 | 618:39 | 7:50 | 98.9816 | 98.9474 | 4087:17 | 51:44 | 99.0257 | 98.9926
2 | Dharwad(R) | 19 | 19 | 34:25 | 96:31 | 193:08 | 120:05 | 313:13 | 3197:10 | 347:38 | 18:18 | 97.7843 | 97.5408 | 3293:41 | 173:21 | 96.7237 | 96.6248
3 | Kundagol | 1 | 1 | 51:20 | 119:00 | 4:15 | 4:25 | 8:40 | 105:30 | 60:00 | 60:00 | 98.8351 | 91.9355 | 224:30 | 224:30 | 97.9459 | 95.6289
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 9:01 | 11:24 | 20:25 | 158:45 | 20:25 | 20:25 | 97.2558 | 97.2558 | 158:45 | 158:45 | 96.9091 | 96.9091
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 5:55 | 8:33 | 14:28 | 151:48 | 14:28 | 14:28 | 98.0556 | 98.0556 | 151:48 | 151:48 | 97.0444 | 97.0444
6 | Kalghatagi | 2 | 2 | 0:00 | 2:20 | 15:00 | 6:10 | 21:10 | 380:30 | 21:10 | 10:35 | 98.5775 | 98.5775 | 382:50 | 191:25 | 96.2958 | 96.273
7 | Alnavar | 1 | 1 | 3:20 | 23:50 | 12:35 | 1:05 | 13:40 | 130:10 | 17:00 | 17:00 | 98.1631 | 97.7151 | 154:00 | 154:00 | 97.4656 | 97.0016
8 | Naragund | 2 | 2 | 2:10 | 25:30 | 35:30 | 34:20 | 69:50 | 463:30 | 72:00 | 36:00 | 95.3069 | 95.1613 | 489:00 | 244:30 | 95.4877 | 95.2395
9 | Shirahatti | 4 | 4 | 0:00 | 18:50 | 24:25 | 91:35 | 116:00 | 723:48 | 116:00 | 29:00 | 96.1022 | 96.1022 | 742:38 | 185:39 | 96.4768 | 96.3852
10 | Laxmeshwar | 5 | 5 | 0:00 | 0:00 | 75:15 | 43:11 | 118:26 | 811:33 | 118:26 | 23:41 | 96.8163 | 96.8163 | 811:33 | 162:19 | 96.8398 | 96.8398
11 | Naregal | 1 | 1 | 1:45 | 16:35 | 8:55 | 3:35 | 12:30 | 138:35 | 14:15 | 14:15 | 98.3199 | 98.0847 | 155:10 | 155:10 | 97.3017 | 96.9788
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 21:30 | 11:50 | 33:20 | 296:00 | 33:20 | 16:40 | 97.7599 | 97.7599 | 296:00 | 148:00 | 97.1184 | 97.1184
13 | Ron | 3 | 3 | 8:15 | 36:30 | 23:10 | 34:50 | 58:00 | 525:20 | 66:15 | 22:05 | 97.4014 | 97.0318 | 561:50 | 187:17 | 96.5905 | 96.3536
14 | Mundaragi | 3 | 3 | 4:45 | 69:25 | 33:05 | 23:15 | 56:20 | 623:05 | 61:05 | 20:22 | 97.4761 | 97.2633 | 692:30 | 230:50 | 95.9561 | 95.5056
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 13:00 | 33:23 | 46:23 | 332:44 | 46:23 | 46:23 | 93.7657 | 93.7657 | 332:44 | 332:44 | 93.5215 | 93.5215
16 | G.C.T.M | 1 | 1 | 0:00 | 94:30 | 1:35 | 10:30 | 12:05 | 205:30 | 12:05 | 12:05 | 98.3759 | 98.3759 | 300:00 | 300:00 | 95.9988 | 94.1589
17 | F.C.S.M | 2 | 2 | 0:00 | 172:10 | 16:02 | 6:12 | 22:14 | 282:39 | 22:14 | 11:07 | 98.5058 | 98.5058 | 454:49 | 227:24 | 97.2483 | 95.5723
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 8:25 | 3:57 | 12:22 | 130:48 | 12:22 | 12:22 | 98.3378 | 98.3378 | 130:48 | 130:48 | 97.4533 | 97.4533
19 | Hole-Alur | 1 | 1 | 13:55 | 62:10 | 11:35 | 2:30 | 14:05 | 135:25 | 28:00 | 28:00 | 98.1071 | 96.2366 | 197:35 | 197:35 | 97.3634 | 96.153
20 | Savanur | 2 | 2 | 4:05 | 61:20 | 50:25 | 10:55 | 61:20 | 485:15 | 65:25 | 32:42 | 95.8781 | 95.6037 | 546:35 | 273:18 | 95.276 | 94.6789
21 | Shiggaon | 2 | 2 | 17:05 | 125:30 | 133:40 | 14:00 | 147:40 | 525:10 | 164:45 | 82:22 | 90.0762 | 88.9281 | 650:40 | 325:20 | 94.8874 | 93.6656
22 | Bankapur | 1 | 1 | 21:45 | 147:17 | 12:55 | 4:30 | 17:25 | 217:41 | 39:10 | 39:10 | 97.6591 | 94.7357 | 364:58 | 364:58 | 95.7616 | 92.894
23 | Hangal | 2 | 2 | 18:40 | 42:35 | 40:40 | 11:10 | 51:50 | 358:25 | 70:30 | 35:15 | 96.5166 | 95.2621 | 401:00 | 200:30 | 96.5107 | 96.0962
24 | Ranebennur | 16 | 16 | 7:15 | 87:44 | 162:25 | 56:20 | 218:45 | 2376:27 | 226:00 | 14:08 | 98.1624 | 98.1015 | 2464:11 | 154:01 | 97.1081 | 97.0013
25 | Halageri | 2 | 2 | 27:40 | 271:25 | 44:05 | 10:55 | 55:00 | 311:35 | 82:40 | 41:20 | 96.3038 | 94.4444 | 583:00 | 291:30 | 96.9667 | 94.3244
26 | Tuminakatti | 2 | 2 | 0:35 | 7:00 | 9:30 | 2:35 | 12:05 | 104:20 | 12:40 | 6:20 | 99.1879 | 99.1487 | 111:20 | 55:40 | 98.9843 | 98.9161
27 | Kahanderayanahalli | 1 | 1 | 0:14 | 5:34 | 10:30 | 6:30 | 17:00 | 269:30 | 17:14 | 17:14 | 97.7151 | 97.6837 | 275:04 | 275:04 | 94.7527 | 94.6443
28 | Rattihalli | 1 | 1 | 0:20 | 8:45 | 11:10 | 7:05 | 18:15 | 142:40 | 18:35 | 18:35 | 97.547 | 97.5022 | 151:25 | 151:25 | 97.2222 | 97.0519
29 | Hirekerur | 2 | 2 | 6:50 | 82:57 | 16:00 | 4:30 | 20:30 | 351:10 | 27:20 | 13:40 | 98.6223 | 98.1631 | 434:07 | 217:04 | 96.5813 | 95.7738
30 | Byadagi | 7 | 7 | 23:00 | 152:25 | 53:25 | 57:10 | 110:35 | 1586:38 | 133:35 | 19:05 | 97.8767 | 97.435 | 1739:03 | 248:26 | 95.5868 | 95.1629
31 | Sirsi | 5 | 5 | 2:05 | 36:45 | 14:30 | 13:46 | 28:16 | 356:25 | 30:21 | 6:04 | 99.2401 | 99.1841 | 393:10 | 78:38 | 98.6121 | 98.469
32 | Yellapur | 3 | 3 | 22:55 | 215:26 | 21:15 | 5:10 | 26:25 | 208:25 | 49:20 | 16:27 | 98.8165 | 97.7897 | 423:51 | 141:17 | 98.6473 | 97.2492
33 | Mundagod | 3 | 3 | 2:00 | 684:21 | 44:20 | 31:45 | 76:05 | 813:25 | 78:05 | 26:02 | 96.5912 | 96.5016 | 1497:46 | 499:15 | 94.7208 | 90.2793
34 | Siddapur | 2 | 2 | 30:40 | 335:30 | 18:55 | 11:00 | 29:55 | 276:45 | 60:35 | 30:18 | 97.9895 | 95.9285 | 612:15 | 306:08 | 97.3058 | 94.0396
35 | Dandeli | 8 | 8 | 3:00 | 158:12 | 69:21 | 87:42 | 157:03 | 1127:58 | 160:03 | 20:00 | 97.3614 | 97.311 | 1286:10 | 160:46 | 97.2548 | 96.8697
36 | Haliyal | 3 | 3 | 11:20 | 37:22 | 16:20 | 12:38 | 28:58 | 336:02 | 40:18 | 13:26 | 98.7022 | 98.1944 | 373:24 | 124:28 | 97.8191 | 97.5766
37 | Ankola | 3 | 3 | 34:11 | 395:09 | 7:14 | 0:00 | 7:14 | 362:03 | 41:25 | 13:48 | 99.6759 | 98.1444 | 757:12 | 252:24 | 97.6502 | 95.0857
38 | Kumta | 3 | 3 | 6:15 | 44:06 | 24:07 | 19:50 | 43:57 | 386:18 | 50:12 | 16:44 | 98.0309 | 97.7509 | 430:24 | 143:28 | 97.4929 | 97.2066
39 | Gokarna | 1 | 1 | 4:02 | 86:19 | 1:35 | 0:50 | 2:25 | 51:13 | 6:27 | 6:27 | 99.6752 | 99.1331 | 137:32 | 137:32 | 99.0028 | 97.3222
40 | Kasarkod | 1 | 1 | 16:40 | 146:37 | 12:05 | 6:20 | 18:25 | 102:25 | 35:05 | 35:05 | 97.5246 | 95.2845 | 249:02 | 249:02 | 98.0059 | 95.1512
41 | Honnavar | 3 | 3 | 30:51 | 133:06 | 25:23 | 8:08 | 33:31 | 315:29 | 64:22 | 21:27 | 98.4984 | 97.1162 | 448:35 | 149:32 | 97.9525 | 97.0886
42 | Murdeshwar | 4 | 4 | 12:40 | 191:24 | 18:48 | 7:57 | 26:45 | 489:18 | 39:25 | 9:51 | 99.1011 | 98.6755 | 680:42 | 170:10 | 97.6183 | 96.6866
43 | Bhatkal | 3 | 3 | 9:12 | 191:18 | 19:29 | 9:38 | 29:07 | 272:13 | 38:19 | 12:46 | 98.6955 | 98.2833 | 463:31 | 154:30 | 98.2333 | 96.9917
44 | Khanapur | 2 | 2 | 16:55 | 94:40 | 94:10 | 8:50 | 103:00 | 289:15 | 119:55 | 59:57 | 93.078 | 91.9411 | 383:55 | 191:58 | 97.1841 | 96.2625
45 | Bailhongal | 3 | 3 | 1:45 | 10:08 | 54:35 | 19:35 | 74:10 | 383:23 | 75:55 | 25:18 | 96.6771 | 96.5987 | 393:31 | 131:10 | 97.5118 | 97.446
46 | Soundatti | 3 | 3 | 0:36 | 55:32 | 41:45 | 39:40 | 81:25 | 318:31 | 82:01 | 27:20 | 96.3523 | 96.3254 | 374:03 | 124:41 | 97.9328 | 97.5724
47 | Ramdurg | 2 | 2 | 0:00 | 46:52 | 38:00 | 6:05 | 44:05 | 252:11 | 44:05 | 22:02 | 97.0374 | 97.0374 | 299:03 | 149:31 | 97.5449 | 97.0887
48 | Gokak | 11 | 11 | 111:16 | 369:03 | 91:57 | 17:51 | 109:48 | 1067:38 | 221:04 | 20:06 | 98.6584 | 97.2988 | 1436:41 | 130:36 | 98.1102 | 97.457
49 | Mudalagi | 2 | 2 | 23:45 | 74:15 | 28:45 | 9:30 | 38:15 | 250:25 | 62:00 | 31:00 | 97.4294 | 95.8333 | 324:40 | 162:20 | 97.5621 | 96.8393
50 | Konnur | 1 | 1 | 0:00 | 3:45 | 16:10 | 2:40 | 18:50 | 143:25 | 18:50 | 18:50 | 97.4686 | 97.4686 | 147:10 | 147:10 | 97.2076 | 97.1346
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 3:16 | 15:23 | 18:39 | 239:40 | 18:39 | 18:39 | 97.4933 | 97.4933 | 239:40 | 239:40 | 95.3336 | 95.3336
52 | Kudachi | 1 | 1 | 0:00 | 7:15 | 29:35 | 5:20 | 34:55 | 247:40 | 34:55 | 34:55 | 95.3069 | 95.3069 | 254:55 | 254:55 | 95.1778 | 95.0367
53 | Athani | 6 | 6 | 13:16 | 214:08 | 70:17 | 95:06 | 165:23 | 901:54 | 178:39 | 29:47 | 96.2952 | 95.998 | 1116:02 | 186:00 | 97.0733 | 96.3784
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 5:50 | 9:30 | 15:20 | 142:05 | 15:20 | 7:40 | 98.9695 | 98.9695 | 142:05 | 71:02 | 98.6168 | 98.6168
55 | Nippani | 5 | 5 | 0:00 | 60:50 | 52:25 | 22:05 | 74:30 | 541:15 | 74:30 | 14:54 | 97.9973 | 97.9973 | 602:05 | 120:25 | 97.8923 | 97.6554
56 | Sadalaga | 1 | 1 | 0:00 | 7:05 | 34:40 | 6:30 | 41:10 | 190:55 | 41:10 | 41:10 | 94.4668 | 94.4668 | 198:00 | 198:00 | 96.2828 | 96.1449
57 | Muddebihal | 2 | 2 | 6:40 | 25:38 | 44:05 | 29:45 | 73:50 | 530:45 | 80:30 | 40:15 | 95.0381 | 94.5901 | 556:23 | 278:11 | 94.833 | 94.5835
58 | Talikoti | 1 | 1 | 4:05 | 36:35 | 14:50 | 3:30 | 18:20 | 180:40 | 22:25 | 22:25 | 97.5358 | 96.987 | 217:15 | 217:15 | 96.4823 | 95.7701
59 | B.Bagewadi | 1 | 1 | 7:13 | 28:47 | 3:30 | 7:54 | 11:24 | 94:40 | 18:37 | 18:37 | 98.4677 | 97.4978 | 123:27 | 123:27 | 98.1568 | 97.5964
60 | Indi | 3 | 3 | 4:41 | 19:04 | 2:27 | 6:37 | 9:04 | 172:41 | 13:45 | 4:35 | 99.5938 | 99.384 | 191:45 | 63:55 | 98.8793 | 98.7555
61 | Sindagi | 2 | 2 | 12:20 | 137:00 | 20:10 | 10:55 | 31:05 | 229:00 | 43:25 | 21:42 | 97.9111 | 97.0822 | 366:00 | 183:00 | 97.7706 | 96.4369
62 | Guledgudda | 1 | 1 | 0:00 | 21:25 | 7:04 | 9:20 | 16:24 | 129:00 | 16:24 | 16:24 | 97.7957 | 97.7957 | 150:25 | 150:25 | 97.4883 | 97.0713
63 | Ilkal | 8 | 8 | 21:45 | 233:59 | 87:43 | 219:28 | 307:11 | 2147:26 | 328:56 | 41:07 | 94.839 | 94.4736 | 2381:25 | 297:41 | 94.7736 | 94.2041
64 | Kerur | 2 | 2 | 2:38 | 22:18 | 20:02 | 6:21 | 26:23 | 189:58 | 29:01 | 14:30 | 98.2269 | 98.05 | 212:16 | 106:08 | 98.1506 | 97.9335
65 | Hungund | 4 | 4 | 8:20 | 111:54 | 68:50 | 36:19 | 105:09 | 676:59 | 113:29 | 28:22 | 96.4667 | 96.1867 | 788:53 | 197:13 | 96.7047 | 96.16
66 | Gaddankeri | 3 | 3 | 0:12 | 100:11 | 10:12 | 18:16 | 28:28 | 409:44 | 28:40 | 9:33 | 98.7246 | 98.7157 | 509:55 | 169:58 | 97.3408 | 96.6906
67 | Rampur | 1 | 1 | 2:06 | 42:22 | 11:13 | 10:15 | 21:28 | 109:10 | 23:34 | 23:34 | 97.1147 | 96.8324 | 151:32 | 151:32 | 97.8745 | 97.0496
68 | Kaladagi | 2 | 2 | 4:03 | 19:30 | 13:30 | 15:45 | 29:15 | 356:12 | 33:18 | 16:39 | 98.0343 | 97.7621 | 375:42 | 187:51 | 96.5323 | 96.3425
69 | Achanur | 1 | 1 | 0:24 | 12:00 | 9:12 | 8:24 | 17:36 | 316:12 | 18:00 | 18:00 | 97.6344 | 97.5806 | 328:12 | 328:12 | 93.8435 | 93.6098
70 | Shirur | 1 | 1 | 1:18 | 37:35 | 6:03 | 38:27 | 44:30 | 219:19 | 45:48 | 45:48 | 94.0188 | 93.8441 | 256:54 | 256:54 | 95.7298 | 94.9981
71 | Badami | 1 | 1 | 1:15 | 28:49 | 12:13 | 9:08 | 21:21 | 149:55 | 22:36 | 22:36 | 97.1304 | 96.9624 | 178:44 | 178:44 | 97.0811 | 96.52
72 | Kulageri | 1 | 1 | 0:00 | 10:36 | 7:25 | 3:35 | 11:00 | 88:22 | 11:00 | 11:00 | 98.5215 | 98.5215 | 98:58 | 98:58 | 98.2795 | 98.0731
73 | Jamkhandi | 6 | 6 | 21:00 | 105:20 | 79:50 | 26:40 | 106:30 | 738:50 | 127:30 | 21:15 | 97.6142 | 97.1438 | 844:10 | 140:42 | 97.6024 | 97.2606
74 | Mahalingapur | 3 | 3 | 10:35 | 70:44 | 71:22 | 17:51 | 89:13 | 594:13 | 99:48 | 33:16 | 96.0028 | 95.5287 | 664:57 | 221:39 | 96.1435 | 95.6844
75 | Rabakavi | 2 | 2 | 12:55 | 25:45 | 12:30 | 7:15 | 19:45 | 170:04 | 32:40 | 16:20 | 98.6727 | 97.8047 | 195:49 | 97:54 | 98.3444 | 98.0937
76 | Banahatti | 2 | 2 | 3:50 | 45:35 | 14:40 | 1:30 | 16:10 | 325:25 | 20:00 | 10:00 | 98.9135 | 98.6559 | 371:00 | 185:30 | 96.832 | 96.3882
77 | Teradal | 2 | 2 | 6:50 | 35:40 | 33:20 | 10:10 | 43:30 | 381:55 | 50:20 | 25:10 | 97.0766 | 96.6174 | 417:35 | 208:48 | 96.282 | 95.9347
78 | Mudhol | 4 | 4 | 12:44 | 65:19 | 64:01 | 9:11 | 73:12 | 547:01 | 85:56 | 21:29 | 97.5403 | 97.1125 | 612:20 | 153:05 | 97.3373 | 97.0194
79 | Bilagi | 1 | 1 | 33:40 | 44:30 | 14:05 | 4:25 | 18:30 | 121:15 | 52:10 | 52:10 | 97.5134 | 92.9884 | 165:45 | 165:45 | 97.6392 | 96.7728
80 | Lokapur | 2 | 2 | 2:35 | 13:12 | 30:35 | 25:10 | 55:45 | 553:20 | 58:20 | 29:10 | 96.2534 | 96.0797 | 566:32 | 283:16 | 94.6132 | 94.4847
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of November-2020
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of November-2020 |  |  |  | Reliability for cumulative period from April-20 to November-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 13:48 | 147:58 | 520:59 | 251:29 | 772:28 | 4725:35 | 786:16 | 9:57 | 98.6419 | 98.6177 | 4873:33 | 61:41 | 98.9785 | 98.9465
2 | Dharwad(R) | 19 | 19 | 23:00 | 119:31 | 209:00 | 150:58 | 359:58 | 3557:08 | 382:58 | 20:09 | 97.3687 | 97.2005 | 3676:39 | 193:30 | 96.803 | 96.6956
3 | Kundagol | 1 | 1 | 13:15 | 132:15 | 4:25 | 2:00 | 6:25 | 111:55 | 19:40 | 19:40 | 99.1088 | 97.2685 | 244:10 | 244:10 | 98.0889 | 95.8305
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 1:07 | 4:44 | 5:51 | 164:36 | 5:51 | 5:51 | 99.1875 | 99.1875 | 164:36 | 164:36 | 97.1892 | 97.1892
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 7:15 | 10:42 | 17:57 | 169:45 | 17:57 | 17:57 | 97.5069 | 97.5069 | 169:45 | 169:45 | 97.1013 | 97.1013
6 | Kalghatagi | 2 | 2 | 0:00 | 2:20 | 39:05 | 20:40 | 59:45 | 440:15 | 59:45 | 29:52 | 95.8507 | 95.8507 | 442:35 | 221:18 | 96.241 | 96.2211
7 | Alnavar | 1 | 1 | 2:10 | 26:00 | 15:35 | 2:20 | 17:55 | 148:05 | 20:05 | 20:05 | 97.5116 | 97.2106 | 174:05 | 174:05 | 97.4713 | 97.0273
8 | Naragund | 2 | 2 | 15:50 | 41:20 | 9:45 | 61:20 | 71:05 | 534:35 | 86:55 | 43:28 | 95.0637 | 93.9641 | 575:55 | 287:58 | 95.4356 | 95.0827
9 | Shirahatti | 4 | 4 | 0:00 | 18:50 | 18:35 | 48:50 | 67:25 | 791:13 | 67:25 | 16:51 | 97.6591 | 97.6591 | 810:03 | 202:31 | 96.6222 | 96.5418
10 | Laxmeshwar | 5 | 5 | 0:00 | 0:00 | 58:20 | 15:09 | 73:29 | 885:02 | 73:29 | 14:42 | 97.9588 | 97.9588 | 885:02 | 177:00 | 96.9773 | 96.9773
11 | Naregal | 1 | 1 | 3:40 | 20:15 | 19:10 | 0:55 | 20:05 | 158:40 | 23:45 | 23:45 | 97.2106 | 96.7014 | 178:55 | 178:55 | 97.2905 | 96.9447
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 28:35 | 12:55 | 41:30 | 337:30 | 41:30 | 20:45 | 97.1181 | 97.1181 | 337:30 | 168:45 | 97.1183 | 97.1183
13 | Ron | 3 | 3 | 3:00 | 39:30 | 38:10 | 13:15 | 51:25 | 576:45 | 54:25 | 18:08 | 97.6196 | 97.4807 | 616:15 | 205:25 | 96.717 | 96.4922
14 | Mundaragi | 3 | 3 | 6:30 | 75:55 | 15:15 | 17:00 | 32:15 | 655:20 | 38:45 | 12:55 | 98.5069 | 98.206 | 731:15 | 243:45 | 96.2697 | 95.8376
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 13:55 | 2:44 | 16:39 | 349:23 | 16:39 | 16:39 | 97.6875 | 97.6875 | 349:23 | 349:23 | 94.0338 | 94.0338
16 | G.C.T.M | 1 | 1 | 10:35 | 105:05 | 5:50 | 1:00 | 6:50 | 212:20 | 17:25 | 17:25 | 99.0509 | 97.581 | 317:25 | 317:25 | 96.3741 | 94.5796
17 | F.C.S.M | 2 | 2 | 18:05 | 190:15 | 4:00 | 1:35 | 5:35 | 288:14 | 23:40 | 11:50 | 99.6123 | 98.3565 | 478:29 | 239:14 | 97.539 | 95.9146
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 5:23 | 0:55 | 6:18 | 137:06 | 6:18 | 6:18 | 99.125 | 99.125 | 137:06 | 137:06 | 97.6588 | 97.6588
19 | Hole-Alur | 1 | 1 | 6:25 | 68:35 | 9:25 | 1:40 | 11:05 | 146:30 | 17:30 | 17:30 | 98.4606 | 97.5694 | 215:05 | 215:05 | 97.4983 | 96.3271
20 | Savanur | 2 | 2 | 1:10 | 62:30 | 92:30 | 2:25 | 94:55 | 580:10 | 96:05 | 48:02 | 93.4086 | 93.3275 | 642:40 | 321:20 | 95.0464 | 94.5128
21 | Shiggaon | 3 | 3 | 5:15 | 130:45 | 15:50 | 19:00 | 34:50 | 560:00 | 40:05 | 13:22 | 98.3873 | 98.1443 | 690:45 | 230:15 | 96.8124 | 96.0681
22 | Bankapur | 1 | 1 | 19:50 | 167:07 | 6:35 | 6:00 | 12:35 | 230:16 | 32:25 | 32:25 | 98.2523 | 95.4977 | 397:23 | 397:23 | 96.0679 | 93.2141
23 | Hangal | 2 | 2 | 3:00 | 45:35 | 10:25 | 5:30 | 15:55 | 374:20 | 18:55 | 9:28 | 98.8947 | 98.6863 | 419:55 | 209:58 | 96.8038 | 96.4146
24 | Ranebennur | 16 | 16 | 10:10 | 97:54 | 304:05 | 36:39 | 340:44 | 2717:11 | 350:54 | 21:56 | 97.0422 | 96.954 | 2815:05 | 175:57 | 97.1 | 96.9955
25 | Halageri | 2 | 2 | 35:20 | 306:45 | 38:30 | 1:35 | 40:05 | 351:40 | 75:25 | 37:43 | 97.2164 | 94.7627 | 658:25 | 329:12 | 96.9974 | 94.3783
26 | Tuminakatti | 2 | 2 | 0:10 | 7:10 | 12:10 | 2:40 | 14:50 | 119:10 | 15:00 | 7:30 | 98.9699 | 98.9583 | 126:20 | 63:10 | 98.9825 | 98.9213
27 | Kahanderayanahalli | 1 | 1 | 2:35 | 8:09 | 9:50 | 21:50 | 31:40 | 301:10 | 34:15 | 34:15 | 95.6019 | 95.2431 | 309:19 | 309:19 | 94.8571 | 94.718
28 | Rattihalli | 1 | 1 | 0:15 | 9:00 | 15:45 | 5:15 | 21:00 | 163:40 | 21:15 | 21:15 | 97.0833 | 97.0486 | 172:40 | 172:40 | 97.2051 | 97.0515
29 | Hirekerur | 2 | 2 | 3:35 | 86:32 | 16:05 | 5:40 | 21:45 | 372:55 | 25:20 | 12:40 | 98.4896 | 98.2407 | 459:27 | 229:44 | 96.8159 | 96.0771
30 | Byadagi | 8 | 8 | 22:35 | 175:00 | 55:30 | 27:55 | 83:25 | 1670:03 | 106:00 | 13:15 | 98.5518 | 98.1597 | 1845:03 | 230:38 | 96.4352 | 96.0616
31 | Sirsi | 5 | 5 | 2:05 | 38:50 | 41:20 | 10:09 | 51:29 | 407:54 | 53:34 | 10:43 | 98.5699 | 98.512 | 446:44 | 89:21 | 98.6069 | 98.4743
32 | Yellapur | 3 | 3 | 4:05 | 219:31 | 11:25 | 1:35 | 13:00 | 221:25 | 17:05 | 5:42 | 99.3981 | 99.2091 | 440:56 | 146:59 | 98.7397 | 97.4901
33 | Mundagod | 3 | 3 | 1:09 | 685:30 | 37:05 | 13:10 | 50:15 | 863:40 | 51:24 | 17:08 | 97.6736 | 97.6204 | 1549:10 | 516:23 | 95.0839 | 91.1819
34 | Siddapur | 2 | 2 | 19:50 | 355:20 | 9:40 | 6:20 | 16:00 | 292:45 | 35:50 | 17:55 | 98.8889 | 97.5116 | 648:05 | 324:03 | 97.5004 | 94.4665
35 | Dandeli | 8 | 8 | 101:08 | 259:20 | 136:40 | 16:42 | 153:22 | 1281:20 | 254:30 | 31:49 | 97.3374 | 95.5816 | 1540:40 | 192:35 | 97.2649 | 96.7114
36 | Haliyal | 3 | 3 | 0:00 | 37:22 | 14:08 | 2:54 | 17:02 | 353:04 | 17:02 | 5:41 | 99.2114 | 99.2114 | 390:26 | 130:09 | 97.9903 | 97.7776
37 | Ankola | 3 | 3 | 47:48 | 442:57 | 8:14 | 4:12 | 12:26 | 374:29 | 60:14 | 20:05 | 99.4244 | 97.2114 | 817:26 | 272:29 | 97.8684 | 95.347
38 | Kumta | 3 | 3 | 9:00 | 53:06 | 11:11 | 6:15 | 17:26 | 403:44 | 26:26 | 8:49 | 99.1929 | 98.7762 | 456:50 | 152:17 | 97.7019 | 97.3996
39 | Gokarna | 1 | 1 | 11:30 | 97:49 | 0:35 | 0:05 | 0:40 | 51:53 | 12:10 | 12:10 | 99.9074 | 98.3102 | 149:42 | 149:42 | 99.114 | 97.4436
40 | Kasarkod | 1 | 1 | 12:55 | 159:32 | 0:55 | 1:10 | 2:05 | 104:30 | 15:00 | 15:00 | 99.7106 | 97.9167 | 264:02 | 264:02 | 98.2155 | 95.4912
41 | Honnavar | 3 | 3 | 13:00 | 146:06 | 17:39 | 3:07 | 20:46 | 336:15 | 33:46 | 11:15 | 99.0386 | 98.4367 | 482:21 | 160:47 | 98.086 | 97.2544
42 | Murdeshwar | 4 | 4 | 17:48 | 209:12 | 29:07 | 8:18 | 37:25 | 526:43 | 55:13 | 13:48 | 98.7008 | 98.0828 | 735:55 | 183:59 | 97.7514 | 96.8583
43 | Bhatkal | 3 | 3 | 34:33 | 225:51 | 25:15 | 11:45 | 37:00 | 309:13 | 71:33 | 23:51 | 98.287 | 96.6875 | 535:04 | 178:21 | 98.2399 | 96.9543
44 | Khanapur | 2 | 2 | 2:00 | 96:40 | 30:15 | 10:55 | 41:10 | 330:25 | 43:10 | 21:35 | 97.1412 | 97.0023 | 427:05 | 213:32 | 97.1788 | 96.3535
45 | Bailhongal | 3 | 3 | 0:00 | 10:08 | 9:25 | 6:10 | 15:35 | 398:58 | 15:35 | 5:12 | 99.2785 | 99.2785 | 409:06 | 136:22 | 97.729 | 97.6713
46 | Soundatti | 3 | 3 | 0:20 | 55:52 | 18:29 | 3:29 | 21:58 | 340:29 | 22:18 | 7:26 | 98.983 | 98.9676 | 396:21 | 132:07 | 98.0619 | 97.7439
47 | Ramdurg | 2 | 2 | 0:00 | 46:52 | 8:55 | 5:40 | 14:35 | 266:46 | 14:35 | 7:17 | 98.9873 | 98.9873 | 313:38 | 156:49 | 97.7223 | 97.3221
48 | Gokak | 11 | 11 | 14:03 | 383:06 | 27:25 | 15:27 | 42:52 | 1110:30 | 56:55 | 5:10 | 99.4588 | 99.2814 | 1493:36 | 135:47 | 98.276 | 97.6813
49 | Mudalagi | 2 | 2 | 1:20 | 75:35 | 20:35 | 1:30 | 22:05 | 272:30 | 23:25 | 11:42 | 98.4664 | 98.3738 | 348:05 | 174:03 | 97.6733 | 97.028
50 | Konnur | 1 | 1 | 1:15 | 5:00 | 22:00 | 1:10 | 23:10 | 166:35 | 24:25 | 24:25 | 96.7824 | 96.6088 | 171:35 | 171:35 | 97.1553 | 97.07
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 21:27 | 6:33 | 28:00 | 267:40 | 28:00 | 28:00 | 96.1111 | 96.1111 | 267:40 | 267:40 | 95.4292 | 95.4292
52 | Kudachi | 1 | 1 | 0:00 | 7:15 | 35:05 | 6:40 | 41:45 | 289:25 | 41:45 | 41:45 | 94.2014 | 94.2014 | 296:40 | 296:40 | 95.0578 | 94.934
53 | Athani | 6 | 6 | 13:12 | 227:20 | 33:35 | 43:26 | 77:01 | 978:55 | 90:13 | 15:02 | 98.2172 | 97.9117 | 1206:15 | 201:03 | 97.2139 | 96.5669
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 2:25 | 9:15 | 11:40 | 153:45 | 11:40 | 5:50 | 99.1898 | 99.1898 | 153:45 | 76:52 | 98.6872 | 98.6872
55 | Nippani | 5 | 5 | 0:00 | 60:50 | 63:15 | 20:25 | 83:40 | 624:55 | 83:40 | 16:44 | 97.6759 | 97.6759 | 685:45 | 137:09 | 97.8657 | 97.658
56 | Sadalaga | 1 | 1 | 0:00 | 7:05 | 8:10 | 9:05 | 17:15 | 208:10 | 17:15 | 17:15 | 97.6042 | 97.6042 | 215:15 | 215:15 | 96.4452 | 96.3243
57 | Muddebihal | 2 | 2 | 1:50 | 27:28 | 35:40 | 19:30 | 55:10 | 585:55 | 57:00 | 28:30 | 96.169 | 96.0417 | 613:23 | 306:41 | 94.9973 | 94.7628
58 | Talikoti | 1 | 1 | 5:25 | 42:00 | 13:25 | 1:25 | 14:50 | 195:30 | 20:15 | 20:15 | 97.9398 | 97.1875 | 237:30 | 237:30 | 96.6615 | 95.9443
59 | B.Bagewadi | 1 | 1 | 0:00 | 28:47 | 2:20 | 3:29 | 5:49 | 100:29 | 5:49 | 5:49 | 99.1921 | 99.1921 | 129:16 | 129:16 | 98.2841 | 97.7926
60 | Indi | 3 | 3 | 0:40 | 19:44 | 6:29 | 1:31 | 8:00 | 180:41 | 8:40 | 2:53 | 99.6296 | 99.5988 | 200:25 | 66:48 | 98.9715 | 98.8592
61 | Sindagi | 2 | 2 | 5:50 | 142:50 | 9:30 | 2:50 | 12:20 | 241:20 | 18:10 | 9:05 | 99.1435 | 98.7384 | 384:10 | 192:05 | 97.9394 | 96.7199
62 | Guledgudda | 1 | 1 | 0:00 | 21:25 | 3:40 | 2:26 | 6:06 | 135:06 | 6:06 | 6:06 | 99.1528 | 99.1528 | 156:31 | 156:31 | 97.693 | 97.3272
63 | Ilkal | 8 | 8 | 12:30 | 246:29 | 90:13 | 101:38 | 191:51 | 2339:17 | 204:21 | 25:33 | 96.6693 | 96.4523 | 2585:46 | 323:13 | 95.0067 | 94.4805
64 | Kerur | 2 | 2 | 0:10 | 22:28 | 14:56 | 10:37 | 25:33 | 215:31 | 25:43 | 12:52 | 98.2257 | 98.2141 | 237:59 | 118:59 | 98.1599 | 97.968
65 | Hungund | 4 | 4 | 0:54 | 112:48 | 45:36 | 7:26 | 53:02 | 730:01 | 53:56 | 13:29 | 98.1586 | 98.1273 | 842:49 | 210:42 | 96.8835 | 96.4019
66 | Gaddankeri | 3 | 3 | 3:27 | 103:38 | 32:41 | 30:55 | 63:36 | 473:20 | 67:03 | 22:21 | 97.0556 | 96.8958 | 576:58 | 192:19 | 97.3057 | 96.7158
67 | Rampur | 1 | 1 | 2:03 | 44:25 | 2:15 | 0:09 | 2:24 | 111:34 | 4:27 | 4:27 | 99.6667 | 99.3819 | 155:59 | 155:59 | 98.0948 | 97.3364
68 | Kaladagi | 2 | 2 | 1:30 | 21:00 | 23:33 | 28:18 | 51:51 | 408:03 | 53:21 | 26:41 | 96.3993 | 96.2951 | 429:03 | 214:32 | 96.516 | 96.3367
69 | Achanur | 1 | 1 | 1:15 | 13:15 | 13:15 | 4:03 | 17:18 | 333:30 | 18:33 | 18:33 | 97.5972 | 97.4236 | 346:45 | 346:45 | 94.305 | 94.0787
70 | Shirur | 1 | 1 | 12:24 | 49:59 | 0:30 | 3:54 | 4:24 | 223:43 | 16:48 | 16:48 | 99.3889 | 97.6667 | 273:42 | 273:42 | 96.1797 | 95.3262
71 | Badami | 1 | 1 | 0:57 | 29:46 | 16:53 | 17:30 | 34:23 | 184:18 | 35:20 | 35:20 | 95.2245 | 95.0926 | 214:04 | 214:04 | 96.8528 | 96.3445
72 | Kulageri | 1 | 1 | 0:00 | 10:36 | 4:50 | 3:35 | 8:25 | 96:47 | 8:25 | 8:25 | 98.831 | 98.831 | 107:23 | 107:23 | 98.3473 | 98.1663
73 | Jamkhandi | 6 | 6 | 2:00 | 107:20 | 74:05 | 15:45 | 89:50 | 828:40 | 91:50 | 15:18 | 97.9205 | 97.8742 | 936:00 | 156:00 | 97.6415 | 97.3361
74 | Mahalingapur | 3 | 3 | 2:12 | 72:56 | 40:44 | 5:16 | 46:00 | 640:13 | 48:12 | 16:04 | 97.8704 | 97.7685 | 713:09 | 237:43 | 96.3558 | 95.9406
75 | Rabakavi | 2 | 2 | 1:50 | 27:35 | 11:45 | 2:35 | 14:20 | 184:24 | 16:10 | 8:05 | 99.0046 | 98.8773 | 211:59 | 106:00 | 98.4255 | 98.19
76 | Banahatti | 2 | 2 | 0:00 | 45:35 | 9:10 | 0:55 | 10:05 | 335:30 | 10:05 | 5:02 | 99.2998 | 99.2998 | 381:05 | 190:32 | 97.1354 | 96.7462
77 | Teradal | 2 | 2 | 1:40 | 37:20 | 17:35 | 5:30 | 23:05 | 405:00 | 24:45 | 12:22 | 98.397 | 98.2812 | 442:20 | 221:10 | 96.542 | 96.2232
78 | Mudhol | 4 | 4 | 4:27 | 69:46 | 33:21 | 8:40 | 42:01 | 589:02 | 46:28 | 11:37 | 98.5411 | 98.3866 | 658:48 | 164:42 | 97.4853 | 97.1875
79 | Bilagi | 1 | 1 | 0:35 | 45:05 | 11:25 | 1:15 | 12:40 | 133:55 | 13:15 | 13:15 | 98.2407 | 98.1597 | 179:00 | 179:00 | 97.7132 | 96.9433
80 | Lokapur | 2 | 2 | 2:40 | 15:52 | 22:00 | 13:05 | 35:05 | 588:25 | 37:45 | 18:52 | 97.5637 | 97.3785 | 604:17 | 302:09 | 94.976 | 94.8405
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of DECEMBER-2020
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of December-2020 |  |  |  | Reliability for cumulative period from April-20 to December-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 13:48 | 161:46 | 231:53 | 131:44 | 363:37 | 5089:12 | 377:25 | 4:47 | 99.3814 | 99.3579 | 5250:58 | 66:28 | 99.0239 | 98.9929
2 | Dharwad(R) | 19 | 19 | 205:00 | 324:31 | 341:28 | 66:53 | 408:21 | 3965:29 | 613:21 | 32:17 | 97.1113 | 95.6611 | 4290:00 | 225:47 | 96.8377 | 96.5789
3 | Kundagol | 1 | 1 | 2:10 | 134:25 | 9:00 | 20:00 | 29:00 | 140:55 | 31:10 | 31:10 | 96.1022 | 95.8109 | 275:20 | 275:20 | 97.8649 | 95.8283
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 4:00 | 1:24 | 5:24 | 170:00 | 5:24 | 5:24 | 99.2742 | 99.2742 | 170:00 | 170:00 | 97.4242 | 97.4242
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 6:00 | 25:00 | 31:00 | 200:45 | 31:00 | 31:00 | 95.8333 | 95.8333 | 200:45 | 200:45 | 96.9583 | 96.9583
6 | Kalghatagi | 2 | 2 | 0:00 | 2:20 | 129:35 | 4:30 | 134:05 | 574:20 | 134:05 | 67:03 | 90.989 | 90.989 | 576:40 | 288:20 | 95.649 | 95.6313
7 | Alnavar | 1 | 1 | 1:45 | 27:45 | 10:00 | 2:50 | 12:50 | 160:55 | 14:35 | 14:35 | 98.2751 | 98.0399 | 188:40 | 188:40 | 97.5619 | 97.1414
8 | Naragund | 2 | 2 | 0:00 | 41:20 | 21:05 | 24:30 | 45:35 | 580:10 | 45:35 | 22:47 | 96.9366 | 96.9366 | 621:30 | 310:45 | 95.6048 | 95.2917
9 | Shirahatti | 4 | 4 | 0:00 | 18:50 | 25:25 | 52:55 | 78:20 | 869:33 | 78:20 | 19:35 | 97.3678 | 97.3678 | 888:23 | 222:06 | 96.7062 | 96.6349
10 | Laxmeshwar | 5 | 5 | 0:00 | 0:00 | 104:21 | 31:02 | 135:23 | 1020:25 | 135:23 | 27:05 | 96.3607 | 96.3607 | 1020:25 | 204:05 | 96.9078 | 96.9078
11 | Naregal | 1 | 1 | 1:30 | 21:45 | 3:25 | 1:40 | 5:05 | 163:45 | 6:35 | 6:35 | 99.3168 | 99.1151 | 185:30 | 185:30 | 97.5189 | 97.1894
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 17:30 | 8:40 | 26:10 | 363:40 | 26:10 | 13:05 | 98.2415 | 98.2415 | 363:40 | 181:50 | 97.2449 | 97.2449
13 | Ron | 3 | 3 | 6:30 | 46:00 | 6:50 | 5:45 | 12:35 | 589:20 | 19:05 | 6:22 | 99.4362 | 99.145 | 635:20 | 211:47 | 97.0236 | 96.7912
14 | Mundaragi | 4 | 4 | 0:20 | 76:15 | 13:50 | 25:50 | 39:40 | 695:00 | 40:00 | 10:00 | 98.6671 | 98.6559 | 771:15 | 192:49 | 97.3674 | 97.0786
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 5:35 | 0:40 | 6:15 | 355:38 | 6:15 | 6:15 | 99.1599 | 99.1599 | 355:38 | 355:38 | 94.6116 | 94.6116
16 | G.C.T.M | 1 | 1 | 4:10 | 109:15 | 4:40 | 0:20 | 5:00 | 217:20 | 9:10 | 9:10 | 99.328 | 98.7679 | 326:35 | 326:35 | 96.7071 | 95.0518
17 | F.C.S.M | 2 | 2 | 4:10 | 194:25 | 3:20 | 0:00 | 3:20 | 291:34 | 7:30 | 3:45 | 99.776 | 99.496 | 485:59 | 243:00 | 97.7912 | 96.3183
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 33:38 | 7:38 | 41:16 | 178:22 | 41:16 | 41:16 | 94.4534 | 94.4534 | 178:22 | 178:22 | 97.2975 | 97.2975
19 | Hole-Alur | 1 | 1 | 0:50 | 69:25 | 6:50 | 0:05 | 6:55 | 153:25 | 7:45 | 7:45 | 99.0703 | 98.9583 | 222:50 | 222:50 | 97.6755 | 96.6237
20 | Savanur | 2 | 2 | 0:50 | 63:20 | 5:45 | 1:30 | 7:15 | 587:25 | 8:05 | 4:03 | 99.5128 | 99.4568 | 650:45 | 325:22 | 95.5499 | 95.0701
21 | Shiggaon | 2 | 2 | 2:35 | 133:20 | 10:10 | 8:25 | 18:35 | 578:35 | 21:10 | 10:35 | 98.7511 | 98.5775 | 711:55 | 355:58 | 95.6168 | 94.6067
22 | Bankapur | 1 | 1 | 4:03 | 171:10 | 9:36 | 3:10 | 12:46 | 243:02 | 16:49 | 16:49 | 98.2841 | 97.7397 | 414:12 | 414:12 | 96.3177 | 93.7242
23 | Hangal | 2 | 2 | 2:00 | 47:35 | 4:05 | 3:40 | 7:45 | 382:05 | 9:45 | 4:52 | 99.4792 | 99.3448 | 429:40 | 214:50 | 97.1054 | 96.7449
24 | Ranebennur | 16 | 16 | 19:40 | 117:34 | 117:31 | 34:23 | 151:54 | 2869:05 | 171:34 | 10:43 | 98.724 | 98.5587 | 2986:39 | 186:40 | 97.2831 | 97.1717
25 | Halageri | 2 | 2 | 34:55 | 341:40 | 7:50 | 1:00 | 8:50 | 360:30 | 43:45 | 21:52 | 99.4064 | 97.0598 | 702:10 | 351:05 | 97.2689 | 94.6806
26 | Tuminakatti | 2 | 2 | 0:50 | 8:00 | 10:50 | 0:50 | 11:40 | 130:50 | 12:30 | 6:15 | 99.2159 | 99.1599 | 138:50 | 69:25 | 99.0088 | 98.9482
27 | Kahanderayanahalli | 1 | 1 | 2:45 | 10:54 | 22:40 | 9:35 | 32:15 | 333:25 | 35:00 | 35:00 | 95.6653 | 95.2957 | 344:19 | 344:19 | 94.9482 | 94.7831
28 | Rattihalli | 1 | 1 | 1:05 | 10:05 | 20:05 | 7:15 | 27:20 | 191:00 | 28:25 | 28:25 | 96.3262 | 96.1806 | 201:05 | 201:05 | 97.1061 | 96.9533
29 | Hirekerur | 2 | 2 | 7:55 | 94:27 | 15:50 | 5:40 | 21:30 | 394:25 | 29:25 | 14:42 | 98.5551 | 98.0231 | 488:52 | 244:26 | 97.012 | 96.2965
30 | Byadagi | 8 | 8 | 29:40 | 204:40 | 90:20 | 24:20 | 114:40 | 1784:43 | 144:20 | 18:02 | 98.0735 | 97.575 | 1989:23 | 248:40 | 96.6199 | 96.2322
31 | Sirsi | 5 | 5 | 2:05 | 40:55 | 8:20 | 10:35 | 18:55 | 426:49 | 21:00 | 4:12 | 99.4915 | 99.4355 | 467:44 | 93:33 | 98.7066 | 98.5826
32 | Yellapur | 3 | 3 | 22:55 | 242:26 | 21:15 | 5:10 | 26:25 | 247:50 | 49:20 | 16:27 | 98.8165 | 97.7897 | 490:16 | 163:25 | 98.7483 | 97.5239
33 | Mundagod | 3 | 3 | 3:30 | 689:00 | 22:50 | 15:38 | 38:28 | 902:08 | 41:58 | 13:59 | 98.2766 | 98.1198 | 1591:08 | 530:23 | 95.4438 | 91.964
34 | Siddapur | 2 | 2 | 0:00 | 355:20 | 1:30 | 7:05 | 8:35 | 301:20 | 8:35 | 4:18 | 99.4232 | 99.4232 | 656:40 | 328:20 | 97.7172 | 95.0253
35 | Dandeli | 8 | 8 | 4:48 | 264:08 | 20:47 | 94:00 | 114:47 | 1396:07 | 119:35 | 14:57 | 98.0715 | 97.9909 | 1660:15 | 207:32 | 97.3558 | 96.8556
36 | Haliyal | 3 | 3 | 3:50 | 41:12 | 15:46 | 5:14 | 21:00 | 374:04 | 24:50 | 8:17 | 99.0591 | 98.8874 | 415:16 | 138:25 | 98.1108 | 97.9027
37 | Ankola | 3 | 3 | 29:07 | 472:04 | 9:57 | 5:06 | 15:03 | 389:32 | 44:10 | 14:43 | 99.3257 | 98.0212 | 861:36 | 287:12 | 98.0327 | 95.6485
38 | Kumta | 3 | 3 | 0:00 | 53:06 | 6:42 | 3:00 | 9:42 | 413:26 | 9:42 | 3:14 | 99.5654 | 99.5654 | 466:32 | 155:31 | 97.912 | 97.6438
39 | Gokarna | 1 | 1 | 7:22 | 105:11 | 1:00 | 0:40 | 1:40 | 53:33 | 9:02 | 9:02 | 99.776 | 98.7858 | 158:44 | 158:44 | 99.1886 | 97.5949
40 | Kasarkod | 1 | 1 | 18:47 | 178:19 | 1:20 | 2:15 | 3:35 | 108:05 | 22:22 | 22:22 | 99.5184 | 96.9937 | 286:24 | 286:24 | 98.3624 | 95.6606
41 | Honnavar | 3 | 3 | 2:36 | 148:42 | 20:14 | 3:26 | 23:40 | 359:55 | 26:16 | 8:45 | 98.9397 | 98.8232 | 508:37 | 169:32 | 98.1822 | 97.4312
42 | Murdeshwar | 4 | 4 | 3:52 | 213:04 | 23:18 | 14:35 | 37:53 | 564:36 | 41:45 | 10:26 | 98.727 | 98.5971 | 777:40 | 194:25 | 97.8614 | 97.0543
43 | Bhatkal | 3 | 3 | 8:54 | 234:45 | 5:58 | 13:29 | 19:27 | 328:40 | 28:21 | 9:27 | 99.1286 | 98.7298 | 563:25 | 187:48 | 98.3401 | 97.1545
44 | Khanapur | 2 | 2 | 0:00 | 96:40 | 32:20 | 3:10 | 35:30 | 365:55 | 35:30 | 17:45 | 97.6142 | 97.6142 | 462:35 | 231:18 | 97.2279 | 96.4956
45 | Bailhongal | 3 | 3 | 0:00 | 10:08 | 18:15 | 5:45 | 24:00 | 422:58 | 24:00 | 8:00 | 98.9247 | 98.9247 | 433:06 | 144:22 | 97.8638 | 97.8126
46 | Soundatti | 3 | 3 | 6:17 | 62:09 | 20:34 | 2:03 | 22:37 | 363:06 | 28:54 | 9:38 | 98.9867 | 98.7052 | 425:15 | 141:45 | 98.1662 | 97.8523
47 | Ramdurg | 2 | 2 | 4:20 | 51:12 | 13:37 | 1:45 | 15:22 | 282:08 | 19:42 | 9:51 | 98.9673 | 98.6761 | 333:20 | 166:40 | 97.8626 | 97.4747
48 | Gokak | 11 | 11 | 14:18 | 397:24 | 67:34 | 12:41 | 80:15 | 1190:45 | 94:33 | 8:36 | 99.0194 | 98.8447 | 1588:09 | 144:23 | 98.3598 | 97.8125
49 | Mudalagi | 2 | 2 | 0:00 | 75:35 | 17:00 | 6:00 | 23:00 | 295:30 | 23:00 | 11:30 | 98.4543 | 98.4543 | 371:05 | 185:33 | 97.7614 | 97.1888
50 | Konnur | 1 | 1 | 0:25 | 5:25 | 13:50 | 1:50 | 15:40 | 182:15 | 16:05 | 16:05 | 97.8943 | 97.8383 | 187:40 | 187:40 | 97.2386 | 97.1566
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 10:55 | 6:10 | 17:05 | 284:45 | 17:05 | 17:05 | 97.7039 | 97.7039 | 284:45 | 284:45 | 95.6856 | 95.6856
52 | Kudachi | 1 | 1 | 0:50 | 8:05 | 34:15 | 1:05 | 35:20 | 324:45 | 36:10 | 36:10 | 95.2509 | 95.1389 | 332:50 | 332:50 | 95.0795 | 94.9571
53 | Athani | 6 | 6 | 11:38 | 238:58 | 25:39 | 31:47 | 57:26 | 1036:21 | 69:04 | 11:31 | 98.7134 | 98.4528 | 1275:19 | 212:33 | 97.3829 | 96.7795
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 5:10 | 5:50 | 11:00 | 164:45 | 11:00 | 5:30 | 99.2608 | 99.2608 | 164:45 | 82:22 | 98.7519 | 98.7519
55 | Nippani | 5 | 5 | 0:00 | 60:50 | 41:10 | 21:15 | 62:25 | 687:20 | 62:25 | 12:29 | 98.3221 | 98.3221 | 748:10 | 149:38 | 97.9172 | 97.7328
56 | Sadalaga | 1 | 1 | 0:35 | 7:40 | 12:10 | 2:45 | 14:55 | 223:05 | 15:30 | 15:30 | 97.9951 | 97.9167 | 230:45 | 230:45 | 96.6199 | 96.5038
57 | Muddebihal | 2 | 2 | 14:00 | 41:28 | 20:50 | 11:15 | 32:05 | 618:00 | 46:05 | 23:02 | 97.8439 | 96.903 | 659:28 | 329:44 | 95.3182 | 95.004
58 | Talikoti | 1 | 1 | 2:30 | 44:30 | 16:15 | 2:00 | 18:15 | 213:45 | 20:45 | 20:45 | 97.547 | 97.211 | 258:15 | 258:15 | 96.7614 | 96.0871
59 | B.Bagewadi | 1 | 1 | 0:20 | 29:07 | 1:50 | 1:14 | 3:04 | 103:33 | 3:24 | 3:24 | 99.5878 | 99.543 | 132:40 | 132:40 | 98.4311 | 97.9899
60 | Indi | 3 | 3 | 2:46 | 22:30 | 7:03 | 3:26 | 10:29 | 191:10 | 13:15 | 4:25 | 99.5303 | 99.4064 | 213:40 | 71:13 | 99.0345 | 98.9209
61 | Sindagi | 2 | 2 | 0:00 | 142:50 | 8:30 | 3:45 | 12:15 | 253:35 | 12:15 | 6:08 | 99.1767 | 99.1767 | 396:25 | 198:12 | 98.0789 | 96.9968
62 | Guledgudda | 1 | 1 | 0:00 | 21:25 | 8:00 | 2:14 | 10:14 | 145:20 | 10:14 | 10:14 | 98.6246 | 98.6246 | 166:45 | 166:45 | 97.798 | 97.4735
63 | Ilkal | 8 | 8 | 25:35 | 272:04 | 86:21 | 39:49 | 126:10 | 2465:27 | 151:45 | 18:58 | 97.8803 | 97.4504 | 2737:31 | 342:11 | 95.3306 | 94.8153
64 | Kerur | 2 | 2 | 0:00 | 22:28 | 6:55 | 4:09 | 11:04 | 226:35 | 11:04 | 5:32 | 99.2563 | 99.2563 | 249:03 | 124:31 | 98.2835 | 98.1133
65 | Hungund | 4 | 4 | 14:40 | 127:28 | 59:57 | 7:20 | 67:17 | 797:18 | 81:57 | 20:29 | 97.7391 | 97.2463 | 924:46 | 231:11 | 96.9799 | 96.4971
66 | Gaddankeri | 3 | 3 | 10:36 | 114:14 | 15:37 | 27:44 | 43:21 | 516:41 | 53:57 | 17:59 | 98.0578 | 97.5829 | 630:55 | 210:18 | 97.3905 | 96.8136
67 | Rampur | 1 | 1 | 0:00 | 44:25 | 14:07 | 0:43 | 14:50 | 126:24 | 14:50 | 14:50 | 98.0063 | 98.0063 | 170:49 | 170:49 | 98.0848 | 97.4119
68 | Kaladagi | 2 | 2 | 0:18 | 21:18 | 10:21 | 10:48 | 21:09 | 429:12 | 21:27 | 10:44 | 98.5786 | 98.5585 | 450:30 | 225:15 | 96.7485 | 96.5871
69 | Achanur | 1 | 1 | 0:00 | 13:15 | 20:15 | 0:00 | 20:15 | 353:45 | 20:15 | 20:15 | 97.2782 | 97.2782 | 367:00 | 367:00 | 94.6402 | 94.4394
70 | Shirur | 1 | 1 | 8:24 | 58:23 | 1:12 | 4:03 | 5:15 | 228:58 | 13:39 | 13:39 | 99.2944 | 98.1653 | 287:21 | 287:21 | 96.5308 | 95.6462
71 | Badami | 1 | 1 | 0:00 | 29:46 | 6:25 | 7:30 | 13:55 | 198:13 | 13:55 | 13:55 | 98.1295 | 98.1295 | 227:59 | 227:59 | 96.9967 | 96.5457
72 | Kulageri | 1 | 1 | 0:00 | 10:36 | 1:05 | 0:05 | 1:10 | 97:57 | 1:10 | 1:10 | 99.8432 | 99.8432 | 108:33 | 108:33 | 98.5159 | 98.3553
73 | Jamkhandi | 6 | 6 | 10:30 | 117:50 | 40:30 | 6:50 | 47:20 | 876:00 | 57:50 | 9:38 | 98.9397 | 98.7045 | 993:50 | 165:38 | 97.7879 | 97.4903
74 | Mahalingapur | 3 | 3 | 0:45 | 73:41 | 35:35 | 7:55 | 43:30 | 683:43 | 44:15 | 14:45 | 98.0511 | 98.0175 | 757:24 | 252:28 | 96.5469 | 96.1747
75 | Rabakavi | 2 | 2 | 1:10 | 28:45 | 11:15 | 3:10 | 14:25 | 198:49 | 15:35 | 7:48 | 99.0311 | 98.9527 | 227:34 | 113:47 | 98.4938 | 98.276
76 | Banahatti | 2 | 2 | 1:30 | 47:05 | 7:40 | 0:20 | 8:00 | 343:30 | 9:30 | 4:45 | 99.4624 | 99.3616 | 390:35 | 195:18 | 97.3977 | 97.041
77 | Teradal | 2 | 2 | 0:00 | 37:20 | 23:00 | 14:05 | 37:05 | 442:05 | 37:05 | 18:32 | 97.5078 | 97.5078 | 479:25 | 239:43 | 96.6509 | 96.3681
78 | Mudhol | 4 | 4 | 2:04 | 71:50 | 36:45 | 3:38 | 40:23 | 629:25 | 42:27 | 10:37 | 98.643 | 98.5736 | 701:15 | 175:19 | 97.6158 | 97.3438
79 | Bilagi | 1 | 1 | 0:20 | 45:25 | 8:15 | 0:35 | 8:50 | 142:45 | 9:10 | 9:10 | 98.8127 | 98.7679 | 188:10 | 188:10 | 97.8371 | 97.149
80 | Lokapur | 2 | 2 | 0:00 | 15:52 | 38:15 | 16:30 | 54:45 | 643:10 | 54:45 | 27:22 | 96.3206 | 96.3206 | 659:02 | 329:31 | 95.1275 | 95.0073
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of JANUARY-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of January-2021 |  |  |  | Reliability for cumulative period from April-20 to January-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 17:03 | 178:49 | 569:50 | 393:32 | 963:22 | 6052:34 | 980:25 | 12:25 | 98.361 | 98.3319 | 6231:23 | 78:53 | 98.9568 | 98.9259
2 | Dharwad(R) | 19 | 19 | 0:30 | 325:01 | 251:09 | 101:14 | 352:23 | 4317:52 | 352:53 | 18:34 | 97.5072 | 97.5037 | 4642:53 | 244:22 | 96.9056 | 96.6726
3 | Kundagol | 1 | 1 | 21:25 | 155:50 | 2:10 | 5:55 | 8:05 | 149:00 | 29:30 | 29:30 | 98.9135 | 96.0349 | 304:50 | 304:50 | 97.9711 | 95.8492
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 4:08 | 1:15 | 5:23 | 175:23 | 5:23 | 5:23 | 99.2764 | 99.2764 | 175:23 | 175:23 | 97.6119 | 97.6119
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 4:42 | 13:15 | 17:57 | 218:42 | 17:57 | 17:57 | 97.5874 | 97.5874 | 218:42 | 218:42 | 97.0221 | 97.0221
6 | Kalghatagi | 2 | 2 | 0:00 | 2:20 | 24:35 | 12:20 | 36:55 | 611:15 | 36:55 | 18:28 | 97.519 | 97.519 | 613:35 | 306:48 | 95.8384 | 95.8226
7 | Alnavar | 1 | 1 | 1:45 | 29:30 | 18:35 | 2:40 | 21:15 | 182:10 | 23:00 | 23:00 | 97.1438 | 96.9086 | 211:40 | 211:40 | 97.5195 | 97.1178
8 | Naragund | 2 | 2 | 4:50 | 46:10 | 17:10 | 26:15 | 43:25 | 623:35 | 48:15 | 24:08 | 97.0822 | 96.7574 | 669:45 | 334:53 | 95.7545 | 95.4402
9 | Shirahatti | 4 | 4 | 0:00 | 18:50 | 50:10 | 56:30 | 106:40 | 976:13 | 106:40 | 26:40 | 96.4158 | 96.4158 | 995:03 | 248:46 | 96.6768 | 96.6127
10 | Laxmeshwar | 5 | 5 | 0:00 | 0:00 | 34:22 | 40:27 | 74:49 | 1095:14 | 74:49 | 14:58 | 97.9888 | 97.9888 | 1095:14 | 219:03 | 97.0173 | 97.0173
11 | Naregal | 1 | 1 | 0:00 | 21:45 | 2:05 | 3:55 | 6:00 | 169:45 | 6:00 | 6:00 | 99.1935 | 99.1935 | 191:30 | 191:30 | 97.6886 | 97.3924
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 13:45 | 4:40 | 18:25 | 382:05 | 18:25 | 9:12 | 98.7623 | 98.7623 | 382:05 | 191:02 | 97.3987 | 97.3987
13 | Ron | 3 | 3 | 2:30 | 48:30 | 13:20 | 4:15 | 17:35 | 606:55 | 20:05 | 6:42 | 99.2122 | 99.1002 | 655:25 | 218:28 | 97.2453 | 97.0252
14 | Mundaragi | 3 | 3 | 0:00 | 76:15 | 7:30 | 6:35 | 14:05 | 709:05 | 14:05 | 4:42 | 99.369 | 99.369 | 785:20 | 261:47 | 96.7816 | 96.4355
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 2:50 | 1:52 | 4:42 | 360:20 | 4:42 | 4:42 | 99.3683 | 99.3683 | 360:20 | 360:20 | 95.0935 | 95.0935
16 | G.C.T.M | 1 | 1 | 5:55 | 115:10 | 7:15 | 1:55 | 9:10 | 226:30 | 15:05 | 15:05 | 98.7679 | 97.9727 | 341:40 | 341:40 | 96.9158 | 95.3477
17 | F.C.S.M | 2 | 2 | 8:05 | 202:30 | 50:20 | 3:15 | 53:35 | 345:09 | 61:40 | 30:50 | 96.399 | 95.8557 | 547:39 | 273:50 | 97.6501 | 96.2714
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 2:50 | 1:52 | 4:42 | 183:04 | 4:42 | 4:42 | 99.3683 | 99.3683 | 183:04 | 183:04 | 97.5073 | 97.5073
19 | Hole-Alur | 1 | 1 | 7:00 | 76:25 | 10:55 | 0:35 | 11:30 | 164:55 | 18:30 | 18:30 | 98.4543 | 97.5134 | 241:20 | 241:20 | 97.7544 | 96.7139
20 | Savanur | 2 | 2 | 2:05 | 65:25 | 88:10 | 13:55 | 102:05 | 689:30 | 104:10 | 52:05 | 93.1396 | 92.9996 | 754:55 | 377:28 | 95.3057 | 94.8603
21 | Shiggaon | 2 | 2 | 17:23 | 150:43 | 35:35 | 13:40 | 49:15 | 627:50 | 66:38 | 33:19 | 96.6902 | 95.522 | 778:33 | 389:16 | 95.7255 | 94.6994
22 | Bankapur | 1 | 1 | 13:20 | 184:30 | 6:45 | 3:45 | 10:30 | 253:32 | 23:50 | 23:50 | 98.5887 | 96.7966 | 438:02 | 438:02 | 96.5477 | 94.0355
23 | Hangal | 2 | 2 | 2:45 | 50:20 | 24:45 | 6:35 | 31:20 | 413:25 | 34:05 | 17:02 | 97.8943 | 97.7095 | 463:45 | 231:52 | 97.1853 | 96.8427
24 | Ranebennur | 16 | 16 | 15:08 | 132:42 | 183:50 | 81:55 | 265:45 | 3134:50 | 280:53 | 17:33 | 97.7676 | 97.6404 | 3267:32 | 204:13 | 97.3321 | 97.2192
25 | Halageri | 2 | 2 | 15:00 | 356:40 | 19:05 | 8:35 | 27:40 | 388:10 | 42:40 | 21:20 | 98.1407 | 97.1326 | 744:50 | 372:25 | 97.3573 | 94.929
26 | Tuminakatti | 2 | 2 | 0:10 | 8:10 | 4:55 | 1:15 | 6:10 | 137:00 | 6:20 | 3:10 | 99.5856 | 99.5744 | 145:10 | 72:35 | 99.0673 | 99.0117
27 | Kahanderayanahalli | 1 | 1 | 1:15 | 12:09 | 17:55 | 4:15 | 22:10 | 355:35 | 23:25 | 23:25 | 97.0206 | 96.8526 | 367:44 | 367:44 | 95.1582 | 94.9927
28 | Rattihalli | 1 | 1 | 0:10 | 10:15 | 8:15 | 6:05 | 14:20 | 205:20 | 14:30 | 14:30 | 98.0735 | 98.0511 | 215:35 | 215:35 | 97.2041 | 97.0645
29 | Hirekerur | 2 | 2 | 5:25 | 99:52 | 28:10 | 4:00 | 32:10 | 426:35 | 37:35 | 18:48 | 97.8383 | 97.4742 | 526:27 | 263:13 | 97.0957 | 96.4158
30 | Byadagi | 8 | 8 | 30:35 | 235:15 | 89:30 | 28:05 | 117:35 | 1902:18 | 148:10 | 18:31 | 98.0245 | 97.5106 | 2137:33 | 267:12 | 96.7622 | 96.3617
31 | Sirsi | 5 | 5 | 5:00 | 45:55 | 13:13 | 18:57 | 32:10 | 458:59 | 37:10 | 7:26 | 99.1353 | 99.0009 | 504:54 | 100:59 | 98.75 | 98.625
32 | Yellapur | 3 | 3 | 7:45 | 250:11 | 6:20 | 4:50 | 11:10 | 259:00 | 18:55 | 6:18 | 99.4997 | 99.1525 | 509:11 | 169:44 | 98.8244 | 97.6889
33 | Mundagod | 3 | 3 | 0:00 | 689:00 | 53:45 | 38:05 | 91:50 | 993:58 | 91:50 | 30:37 | 95.8856 | 95.8856 | 1682:58 | 560:59 | 95.4885 | 92.3613
34 | Siddapur | 2 | 2 | 0:50 | 356:10 | 1:55 | 6:40 | 8:35 | 309:55 | 9:25 | 4:42 | 99.4232 | 99.3672 | 666:05 | 333:03 | 97.89 | 95.4651
35 | Dandeli | 8 | 8 | 2:48 | 266:56 | 34:14 | 20:58 | 55:12 | 1451:19 | 58:00 | 7:15 | 99.0726 | 99.0255 | 1718:15 | 214:47 | 97.5298 | 97.0754
36 | Haliyal | 3 | 3 | 3:50 | 45:02 | 11:03 | 6:55 | 17:58 | 392:02 | 21:48 | 7:16 | 99.195 | 99.0233 | 437:04 | 145:41 | 98.2206 | 98.0162
37 | Ankola | 3 | 3 | 13:24 | 485:28 | 13:20 | 8:08 | 21:28 | 411:00 | 34:52 | 11:37 | 99.0382 | 98.4379 | 896:28 | 298:49 | 98.1345 | 95.9311
38 | Kumta | 3 | 3 | 4:45 | 57:51 | 13:32 | 7:24 | 20:56 | 434:22 | 25:41 | 8:34 | 99.0621 | 98.8493 | 492:13 | 164:04 | 98.0285 | 97.7659
39 | Gokarna | 1 | 1 | 10:39 | 115:50 | 6:50 | 0:40 | 7:30 | 61:03 | 18:09 | 18:09 | 98.9919 | 97.5605 | 176:53 | 176:53 | 99.1687 | 97.5915
40 | Kasarkod | 1 | 1 | 3:00 | 181:19 | 1:05 | 1:05 | 2:10 | 110:15 | 5:10 | 5:10 | 99.7088 | 99.3056 | 291:34 | 291:34 | 98.4988 | 96.0299
41 | Honnavar | 3 | 3 | 34:39 | 183:21 | 19:22 | 12:06 | 31:28 | 391:23 | 66:07 | 22:02 | 98.5902 | 97.0378 | 574:44 | 191:35 | 98.2236 | 97.3914
42 | Murdeshwar | 4 | 4 | 46:36 | 259:40 | 31:53 | 19:30 | 51:23 | 615:59 | 97:59 | 24:30 | 98.2734 | 96.7075 | 875:39 | 218:55 | 97.9031 | 97.0192
43 | Bhatkal | 3 | 3 | 57:54 | 292:39 | 32:56 | 7:30 | 40:26 | 369:06 | 98:20 | 32:47 | 98.1885 | 95.5944 | 661:45 | 220:35 | 98.3247 | 96.9964
44 | Khanapur | 2 | 2 | 0:00 | 96:40 | 12:45 | 2:20 | 15:05 | 381:00 | 15:05 | 7:32 | 98.9863 | 98.9863 | 477:40 | 238:50 | 97.406 | 96.7479
45 | Bailhongal | 3 | 3 | 0:00 | 10:08 | 14:00 | 9:05 | 23:05 | 446:03 | 23:05 | 7:42 | 98.9658 | 98.9658 | 456:11 | 152:04 | 97.9754 | 97.9295
46 | Soundatti | 3 | 3 | 1:45 | 63:54 | 20:16 | 7:17 | 27:33 | 390:39 | 29:18 | 9:46 | 98.7657 | 98.6873 | 454:33 | 151:31 | 98.2269 | 97.9369
47 | Ramdurg | 2 | 2 | 14:40 | 65:52 | 26:30 | 1:35 | 28:05 | 310:13 | 42:45 | 21:22 | 98.1127 | 97.127 | 376:05 | 188:02 | 97.888 | 97.4395
48 | Gokak | 11 | 11 | 14:53 | 412:17 | 84:19 | 15:21 | 99:40 | 1290:25 | 114:33 | 10:25 | 98.7822 | 98.6003 | 1702:42 | 154:47 | 98.4026 | 97.8923
49 | Mudalagi | 2 | 2 | 0:00 | 75:35 | 14:10 | 3:20 | 17:30 | 313:00 | 17:30 | 8:45 | 98.8239 | 98.8239 | 388:35 | 194:18 | 97.869 | 97.3544
50 | Konnur | 1 | 1 | 0:00 | 5:25 | 10:20 | 1:30 | 11:50 | 194:05 | 11:50 | 11:50 | 98.4095 | 98.4095 | 199:30 | 199:30 | 97.3573 | 97.2835
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 17:57 | 8:41 | 26:38 | 311:23 | 26:38 | 26:38 | 96.4203 | 96.4203 | 311:23 | 311:23 | 95.76 | 95.76
52 | Kudachi | 1 | 1 | 4:50 | 12:55 | 24:00 | 9:20 | 33:20 | 358:05 | 38:10 | 38:10 | 95.5197 | 94.8701 | 371:00 | 371:00 | 95.1241 | 94.9483
53 | Athani | 6 | 6 | 10:20 | 249:18 | 23:24 | 23:47 | 47:11 | 1083:32 | 57:31 | 9:35 | 98.943 | 98.7115 | 1332:50 | 222:08 | 97.541 | 96.9752
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 7:50 | 6:00 | 13:50 | 178:35 | 13:50 | 6:55 | 99.0703 | 99.0703 | 178:35 | 89:17 | 98.7842 | 98.7842
55 | Nippani | 5 | 5 | 0:00 | 60:50 | 65:30 | 36:15 | 101:45 | 789:05 | 101:45 | 20:21 | 97.2648 | 97.2648 | 849:55 | 169:59 | 97.8511 | 97.6854
56 | Sadalaga | 1 | 1 | 0:35 | 8:15 | 12:10 | 2:45 | 14:55 | 238:00 | 15:30 | 15:30 | 97.9951 | 97.9167 | 246:15 | 246:15 | 96.7593 | 96.6469
57 | Muddebihal | 2 | 2 | 0:00 | 41:28 | 21:40 | 18:19 | 39:59 | 657:59 | 39:59 | 20:00 | 97.3129 | 97.3129 | 699:27 | 349:43 | 95.5203 | 95.2379
58 | Talikoti | 1 | 1 | 4:15 | 48:45 | 7:50 | 5:25 | 13:15 | 227:00 | 17:30 | 17:30 | 98.2191 | 97.6478 | 275:45 | 275:45 | 96.909 | 96.2452
59 | B.Bagewadi | 1 | 1 | 0:26 | 29:33 | 4:07 | 1:05 | 5:12 | 108:45 | 5:38 | 5:38 | 99.3011 | 99.2428 | 138:18 | 138:18 | 98.5192 | 98.1168
60 | Indi | 3 | 3 | 0:16 | 22:46 | 11:01 | 1:40 | 12:41 | 203:51 | 12:57 | 4:19 | 99.4318 | 99.4198 | 226:37 | 75:32 | 99.0748 | 98.9714
61 | Sindagi | 2 | 2 | 0:50 | 143:40 | 18:15 | 1:50 | 20:05 | 273:40 | 20:55 | 10:28 | 98.6503 | 98.5943 | 417:20 | 208:40 | 98.1368 | 97.1587
62 | Guledgudda | 1 | 1 | 0:00 | 21:25 | 7:19 | 3:20 | 10:39 | 155:59 | 10:39 | 10:39 | 98.5685 | 98.5685 | 177:24 | 177:24 | 97.876 | 97.5844
63 | Ilkal | 8 | 8 | 50:15 | 322:19 | 123:14 | 33:10 | 156:24 | 2621:51 | 206:39 | 25:50 | 97.3723 | 96.5281 | 2944:10 | 368:01 | 95.5374 | 94.9888
64 | Kerur | 2 | 2 | 0:15 | 22:43 | 6:55 | 4:41 | 11:36 | 238:11 | 11:51 | 5:56 | 99.2204 | 99.2036 | 260:54 | 130:27 | 98.3784 | 98.2237
65 | Hungund | 4 | 4 | 14:05 | 141:33 | 44:30 | 11:53 | 56:23 | 853:41 | 70:28 | 17:37 | 98.1054 | 97.6322 | 995:14 | 248:48 | 97.0939 | 96.6121
66 | Gaddankeri | 3 | 3 | 0:34 | 114:48 | 12:30 | 7:01 | 19:31 | 536:12 | 20:05 | 6:42 | 99.1256 | 99.1002 | 651:00 | 217:00 | 97.5663 | 97.0452
67 | Rampur | 1 | 1 | 0:00 | 44:25 | 4:30 | 0:12 | 4:42 | 131:06 | 4:42 | 4:42 | 99.3683 | 99.3683 | 175:31 | 175:31 | 98.2149 | 97.6101
68 | Kaladagi | 2 | 2 | 2:00 | 23:18 | 18:12 | 31:50 | 50:02 | 479:14 | 52:02 | 26:01 | 96.6375 | 96.5031 | 502:32 | 251:16 | 96.7372 | 96.5786
69 | Achanur | 1 | 1 | 0:00 | 13:15 | 15:09 | 6:36 | 21:45 | 375:30 | 21:45 | 21:45 | 97.0766 | 97.0766 | 388:45 | 388:45 | 94.887 | 94.7066
70 | Shirur | 1 | 1 | 2:15 | 60:38 | 0:12 | 1:00 | 1:12 | 230:10 | 3:27 | 3:27 | 99.8387 | 99.5363 | 290:48 | 290:48 | 96.8659 | 96.0403
71 | Badami | 1 | 1 | 0:45 | 30:31 | 13:24 | 7:04 | 20:28 | 218:41 | 21:13 | 21:13 | 97.2491 | 97.1483 | 249:12 | 249:12 | 97.0223 | 96.6068
72 | Kulageri | 1 | 1 | 1:00 | 11:36 | 0:30 | 0:50 | 1:20 | 99:17 | 2:20 | 2:20 | 99.8208 | 99.6864 | 110:53 | 110:53 | 98.6481 | 98.4902
73 | Jamkhandi | 6 | 6 | 4:30 | 122:20 | 33:40 | 9:20 | 43:00 | 919:00 | 47:30 | 7:55 | 99.0367 | 98.9359 | 1041:20 | 173:33 | 97.9144 | 97.6368
74 | Mahalingapur | 3 | 3 | 0:20 | 74:01 | 26:26 | 2:18 | 28:44 | 712:27 | 29:04 | 9:41 | 98.7127 | 98.6977 | 786:28 | 262:09 | 96.7663 | 96.4303
75 | Rabakavi | 2 | 2 | 1:35 | 30:20 | 6:45 | 3:40 | 10:25 | 209:14 | 12:00 | 6:00 | 99.3 | 99.1935 | 239:34 | 119:47 | 98.5755 | 98.369
76 | Banahatti | 2 | 2 | 0:10 | 47:15 | 11:25 | 0:00 | 11:25 | 354:55 | 11:35 | 5:47 | 99.2328 | 99.2216 | 402:10 | 201:05 | 97.5836 | 97.2619
77 | Teradal | 2 | 2 | 0:00 | 37:20 | 14:48 | 6:10 | 20:58 | 463:03 | 20:58 | 10:29 | 98.5909 | 98.5909 | 500:23 | 250:12 | 96.8474 | 96.5933
78 | Mudhol | 4 | 4 | 15:32 | 87:22 | 59:08 | 4:50 | 63:58 | 693:23 | 79:30 | 19:52 | 97.8506 | 97.3286 | 780:45 | 195:11 | 97.6396 | 97.3422
79 | Bilagi | 1 | 1 | 0:20 | 45:45 | 5:37 | 0:25 | 6:02 | 148:47 | 6:22 | 6:22 | 99.1891 | 99.1443 | 194:32 | 194:32 | 97.9741 | 97.3511
80 | Lokapur | 2 | 2 | 0:00 | 15:52 | 38:15 | 16:30 | 54:45 | 697:55 | 54:45 | 27:22 | 96.3206 | 96.3206 | 713:47 | 356:54 | 95.2484 | 95.1404
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of FEBRUARY-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of February-2021 |  |  |  | Reliability for cumulative period from April-20 to February-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 1:15 | 180:04 | 370:36 | 151:56 | 522:32 | 6575:06 | 523:47 | 6:38 | 99.0157 | 99.0134 | 6755:10 | 85:31 | 98.9617 | 98.9333
2 | Dharwad(R) | 19 | 19 | 2:15 | 327:16 | 161:08 | 97:21 | 258:29 | 4576:21 | 260:44 | 13:43 | 97.9755 | 97.9579 | 4903:37 | 258:05 | 96.9953 | 96.7804
3 | Kundagol | 1 | 1 | 16:00 | 171:50 | 1:25 | 5:15 | 6:40 | 155:40 | 22:40 | 22:40 | 99.0079 | 96.627 | 327:30 | 327:30 | 98.0581 | 95.9144
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 6:38 | 2:00 | 8:38 | 184:01 | 8:38 | 8:38 | 98.7153 | 98.7153 | 184:01 | 184:01 | 97.7044 | 97.7044
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 5:00 | 2:15 | 7:15 | 225:57 | 7:15 | 7:15 | 98.9211 | 98.9211 | 225:57 | 225:57 | 97.1813 | 97.1813
6 | Kalghatagi | 2 | 2 | 0:00 | 2:20 | 11:25 | 7:45 | 19:10 | 630:25 | 19:10 | 9:35 | 98.5739 | 98.5739 | 632:45 | 316:22 | 96.0678 | 96.0532
7 | Alnavar | 1 | 1 | 4:30 | 34:00 | 9:40 | 1:10 | 10:50 | 193:00 | 15:20 | 15:20 | 98.3879 | 97.7183 | 227:00 | 227:00 | 97.5923 | 97.1682
8 | Naragund | 2 | 2 | 1:20 | 47:30 | 9:05 | 13:50 | 22:55 | 646:30 | 24:15 | 12:08 | 98.2949 | 98.1957 | 694:00 | 347:00 | 95.9674 | 95.6712
9 | Shirahatti | 4 | 4 | 0:00 | 18:50 | 6:20 | 10:55 | 17:15 | 993:28 | 17:15 | 4:19 | 99.3583 | 99.3583 | 1012:18 | 253:04 | 96.9016 | 96.8429
10 | Laxmeshwar | 5 | 5 | 0:00 | 0:00 | 61:41 | 41:34 | 103:15 | 1198:29 | 103:15 | 20:39 | 96.9271 | 96.9271 | 1198:29 | 239:42 | 97.0098 | 97.0098
11 | Naregal | 1 | 1 | 0:00 | 21:45 | 5:50 | 4:00 | 9:50 | 179:35 | 9:50 | 9:50 | 98.5367 | 98.5367 | 201:20 | 201:20 | 97.7597 | 97.4884
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 16:10 | 13:20 | 29:30 | 411:35 | 29:30 | 14:45 | 97.8051 | 97.8051 | 411:35 | 205:47 | 97.4327 | 97.4327
13 | Ron | 3 | 3 | 0:00 | 48:30 | 30:05 | 11:35 | 41:40 | 648:35 | 41:40 | 13:53 | 97.9332 | 97.9332 | 697:05 | 232:22 | 97.303 | 97.1013
14 | Mundaragi | 3 | 3 | 0:00 | 76:15 | 43:52 | 14:14 | 58:06 | 767:11 | 58:06 | 19:22 | 97.1181 | 97.1181 | 843:26 | 281:09 | 96.8098 | 96.4927
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 15:32 | 6:59 | 22:31 | 382:51 | 22:31 | 22:31 | 96.6493 | 96.6493 | 382:51 | 382:51 | 95.2239 | 95.2239
16 | G.C.T.M | 1 | 1 | 18:45 | 133:55 | 9:35 | 0:55 | 10:30 | 237:00 | 29:15 | 29:15 | 98.4375 | 95.6473 | 370:55 | 370:55 | 97.0434 | 95.3728
17 | F.C.S.M | 2 | 2 | 32:30 | 235:00 | 50:45 | 1:20 | 52:05 | 397:14 | 84:35 | 42:18 | 96.1248 | 93.7066 | 632:14 | 316:07 | 97.5222 | 96.0564
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 12:15 | 4:50 | 17:05 | 200:09 | 17:05 | 17:05 | 97.4578 | 97.4578 | 200:09 | 200:09 | 97.5031 | 97.5031
19 | Hole-Alur | 1 | 1 | 13:25 | 89:50 | 10:50 | 0:20 | 11:10 | 176:05 | 24:35 | 24:35 | 98.3383 | 96.3418 | 265:55 | 265:55 | 97.8034 | 96.6827
20 | Savanur | 2 | 2 | 0:00 | 65:25 | 16:20 | 12:55 | 29:15 | 718:45 | 29:15 | 14:38 | 97.8237 | 97.8237 | 784:10 | 392:05 | 95.5168 | 95.1087
21 | Shiggaon | 2 | 2 | 7:20 | 158:03 | 7:20 | 15:20 | 22:40 | 650:30 | 30:00 | 15:00 | 98.3135 | 97.7679 | 808:33 | 404:16 | 95.9425 | 94.9566
22 | Bankapur | 1 | 1 | 4:55 | 189:25 | 8:35 | 4:50 | 13:25 | 266:57 | 18:20 | 18:20 | 98.0035 | 97.2718 | 456:22 | 456:22 | 96.6698 | 94.3068
23 | Hangal | 2 | 2 | 1:10 | 51:30 | 31:15 | 8:10 | 39:25 | 452:50 | 40:35 | 20:18 | 97.0672 | 96.9804 | 504:20 | 252:10 | 97.1754 | 96.8542
24 | Ranebennur | 16 | 16 | 56:17 | 188:59 | 90:31 | 39:12 | 129:43 | 3264:33 | 186:00 | 11:38 | 98.7936 | 98.2701 | 3453:32 | 215:51 | 97.4547 | 97.3073
25 | Halageri | 2 | 2 | 14:10 | 370:50 | 22:50 | 0:50 | 23:40 | 411:50 | 37:50 | 18:55 | 98.2391 | 97.185 | 782:40 | 391:20 | 97.4312 | 95.1181
26 | Tuminakatti | 2 | 2 | 0:00 | 8:10 | 22:00 | 1:35 | 23:35 | 160:35 | 23:35 | 11:48 | 98.2453 | 98.2453 | 168:45 | 84:22 | 98.9984 | 98.9474
27 | Kahanderayanahalli | 1 | 1 | 2:19 | 14:28 | 12:25 | 5:15 | 17:40 | 373:15 | 19:59 | 19:59 | 97.371 | 97.0263 | 387:43 | 387:43 | 95.3437 | 95.1632
28 | Rattihalli | 1 | 1 | 1:55 | 12:10 | 16:20 | 4:50 | 21:10 | 226:30 | 23:05 | 23:05 | 96.8502 | 96.565 | 238:40 | 238:40 | 97.1744 | 97.0226
29 | Hirekerur | 2 | 2 | 14:55 | 114:47 | 22:00 | 3:50 | 25:50 | 452:25 | 40:45 | 20:22 | 98.0779 | 96.968 | 567:12 | 283:36 | 97.178 | 96.4621
30 | Byadagi | 8 | 8 | 20:50 | 256:05 | 45:30 | 39:25 | 84:55 | 1987:13 | 105:45 | 13:13 | 98.4204 | 98.0329 | 2243:18 | 280:25 | 96.9012 | 96.5018
31 | Sirsi | 5 | 5 | 5:00 | 50:55 | 12:20 | 18:10 | 30:30 | 489:29 | 35:30 | 7:06 | 99.0923 | 98.9435 | 540:24 | 108:05 | 98.7787 | 98.6517
32 | Yellapur | 3 | 3 | 11:05 | 261:16 | 5:40 | 4:50 | 10:30 | 269:30 | 21:35 | 7:12 | 99.4792 | 98.9294 | 530:46 | 176:55 | 98.8793 | 97.7929
33 | Mundagod | 3 | 3 | 0:00 | 689:00 | 14:30 | 36:25 | 50:55 | 1044:53 | 50:55 | 16:58 | 97.4744 | 97.4744 | 1733:53 | 577:58 | 95.655 | 92.7899
34 | Siddapur | 2 | 2 | 35:00 | 391:10 | 7:48 | 5:25 | 13:13 | 323:08 | 48:13 | 24:06 | 99.0166 | 96.4125 | 714:18 | 357:09 | 97.9844 | 95.5445
35 | Dandeli | 8 | 8 | 5:44 | 272:40 | 117:50 | 27:42 | 145:32 | 1596:51 | 151:16 | 18:54 | 97.2929 | 97.1863 | 1869:31 | 233:41 | 97.5099 | 97.0847
36 | Haliyal | 3 | 3 | 0:13 | 45:15 | 12:30 | 5:22 | 17:52 | 409:54 | 18:05 | 6:02 | 99.1138 | 99.103 | 455:09 | 151:43 | 98.2955 | 98.1073
37 | Ankola | 3 | 3 | 25:49 | 511:17 | 7:38 | 5:10 | 12:48 | 423:48 | 38:37 | 12:52 | 99.3651 | 98.0845 | 935:05 | 311:42 | 98.2377 | 96.1116
38 | Kumta | 3 | 3 | 0:21 | 58:12 | 3:49 | 7:24 | 11:13 | 445:35 | 11:34 | 3:51 | 99.4436 | 99.4263 | 503:47 | 167:56 | 98.1471 | 97.9051
39 | Gokarna | 1 | 1 | 8:55 | 124:45 | 5:55 | 0:10 | 6:05 | 67:08 | 15:00 | 15:00 | 99.0947 | 97.7679 | 191:53 | 191:53 | 99.1625 | 97.6062
40 | Kasarkod | 1 | 1 | 9:23 | 190:42 | 6:41 | 0:31 | 7:12 | 117:27 | 16:35 | 16:35 | 98.9286 | 97.5322 | 308:09 | 308:09 | 98.5348 | 96.1558
41 | Honnavar | 3 | 3 | 1:45 | 185:06 | 10:46 | 9:21 | 20:07 | 411:30 | 21:52 | 7:17 | 99.0021 | 98.9153 | 596:36 | 198:52 | 98.2888 | 97.5191
42 | Murdeshwar | 4 | 4 | 2:40 | 262:20 | 27:51 | 7:01 | 34:52 | 650:51 | 37:32 | 9:23 | 98.7029 | 98.6037 | 913:11 | 228:18 | 97.9702 | 97.152
43 | Bhatkal | 3 | 3 | 15:00 | 307:39 | 24:00 | 4:35 | 28:35 | 397:41 | 43:35 | 14:32 | 98.5822 | 97.8381 | 705:20 | 235:07 | 98.3463 | 97.067
44 | Khanapur | 2 | 2 | 13:50 | 110:30 | 15:00 | 4:55 | 19:55 | 400:55 | 33:45 | 16:52 | 98.5181 | 97.4888 | 511:25 | 255:42 | 97.4993 | 96.81
45 | Bailhongal | 3 | 3 | 3:09 | 13:17 | 102:10 | 4:30 | 106:40 | 552:43 | 109:49 | 36:36 | 94.709 | 94.5527 | 566:00 | 188:40 | 97.7016 | 97.6464
46 | Soundatti | 3 | 3 | 7:14 | 71:08 | 14:33 | 6:55 | 21:28 | 412:07 | 28:42 | 9:34 | 98.9352 | 98.5764 | 483:15 | 161:05 | 98.2863 | 97.9905
47 | Ramdurg | 2 | 2 | 3:46 | 69:38 | 27:45 | 3:50 | 31:35 | 341:48 | 35:21 | 17:41 | 97.65 | 97.3698 | 411:26 | 205:43 | 97.868 | 97.4337
48 | Gokak | 11 | 11 | 4:20 | 416:37 | 35:54 | 6:52 | 42:46 | 1333:11 | 47:06 | 4:17 | 99.4214 | 99.3628 | 1749:48 | 159:04 | 98.488 | 98.0156
49 | Mudalagi | 2 | 2 | 0:30 | 76:05 | 15:00 | 0:40 | 15:40 | 328:40 | 16:10 | 8:05 | 98.8343 | 98.7971 | 404:45 | 202:23 | 97.9499 | 97.4754
50 | Konnur | 1 | 1 | 0:00 | 5:25 | 17:05 | 1:55 | 19:00 | 213:05 | 19:00 | 19:00 | 97.1726 | 97.1726 | 218:30 | 218:30 | 97.3418 | 97.2742
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 18:05 | 3:34 | 21:39 | 333:02 | 21:39 | 21:39 | 96.7783 | 96.7783 | 333:02 | 333:02 | 95.8454 | 95.8454
52 | Kudachi | 1 | 1 | 5:10 | 18:05 | 21:40 | 1:35 | 23:15 | 381:20 | 28:25 | 28:25 | 96.5402 | 95.7713 | 399:25 | 399:25 | 95.2428 | 95.0173
53 | Athani | 6 | 6 | 16:18 | 265:36 | 29:31 | 58:10 | 87:41 | 1171:13 | 103:59 | 17:20 | 97.8253 | 97.421 | 1436:49 | 239:28 | 97.5648 | 97.0126
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 19:55 | 5:20 | 25:15 | 203:50 | 25:15 | 12:38 | 98.1213 | 98.1213 | 203:50 | 101:55 | 98.7286 | 98.7286
55 | Nippani | 5 | 5 | 0:00 | 60:50 | 23:15 | 11:00 | 34:15 | 823:20 | 34:15 | 6:51 | 98.9807 | 98.9807 | 884:10 | 176:50 | 97.9458 | 97.794
56 | Sadalaga | 1 | 1 | 0:00 | 8:15 | 17:40 | 1:50 | 19:30 | 257:30 | 19:30 | 19:30 | 97.0982 | 97.0982 | 265:45 | 265:45 | 96.7877 | 96.6848
57 | Muddebihal | 2 | 2 | 1:50 | 43:18 | 32:25 | 22:50 | 55:15 | 713:14 | 57:05 | 28:32 | 95.8891 | 95.7527 | 756:32 | 378:16 | 95.5512 | 95.2811
58 | Talikoti | 1 | 1 | 11:05 | 59:50 | 15:40 | 2:25 | 18:05 | 245:05 | 29:10 | 29:10 | 97.309 | 95.6597 | 304:55 | 304:55 | 96.9426 | 96.1961
59 | B.Bagewadi | 1 | 1 | 8:32 | 38:05 | 3:05 | 1:10 | 4:15 | 113:00 | 12:47 | 12:47 | 99.3676 | 98.0977 | 151:05 | 151:05 | 98.5903 | 98.1152
60 | Indi | 3 | 3 | 2:12 | 24:58 | 36:47 | 1:46 | 38:33 | 242:24 | 40:45 | 13:35 | 98.0878 | 97.9787 | 267:22 | 89:07 | 98.992 | 98.8882
61 | Sindagi | 2 | 2 | 1:20 | 145:00 | 15:50 | 2:45 | 18:35 | 292:15 | 19:55 | 9:58 | 98.6173 | 98.5181 | 437:15 | 218:38 | 98.1771 | 97.2726
62 | Guledgudda | 1 | 1 | 0:00 | 21:25 | 5:05 | 3:17 | 8:22 | 164:21 | 8:22 | 8:22 | 98.755 | 98.755 | 185:46 | 185:46 | 97.9497 | 97.6826
63 | Ilkal | 8 | 8 | 32:45 | 355:04 | 88:10 | 17:02 | 105:12 | 2727:03 | 137:57 | 17:15 | 98.0432 | 97.434 | 3082:07 | 385:16 | 95.7475 | 95.1938
64 | Kerur | 2 | 2 | 0:37 | 23:20 | 5:14 | 0:05 | 5:19 | 243:30 | 5:56 | 2:58 | 99.6044 | 99.5585 | 266:50 | 133:25 | 98.4812 | 98.3356
65 | Hungund | 4 | 4 | 14:32 | 156:05 | 16:10 | 5:28 | 21:38 | 875:19 | 36:10 | 9:02 | 99.1952 | 98.6545 | 1031:24 | 257:51 | 97.2701 | 96.7833
66 | Gaddankeri | 3 | 3 | 19:28 | 134:16 | 6:57 | 23:32 | 30:29 | 566:41 | 49:57 | 16:39 | 98.4879 | 97.5223 | 700:57 | 233:39 | 97.6435 | 97.0852
67 | Rampur | 1 | 1 | 3:06 | 47:31 | 10:06 | 0:42 | 10:48 | 141:54 | 13:54 | 13:54 | 98.3929 | 97.9315 | 189:25 | 189:25 | 98.2298 | 97.637
68 | Kaladagi | 2 | 2 | 0:00 | 23:18 | 17:15 | 5:45 | 23:00 | 502:14 | 23:00 | 11:30 | 98.2887 | 98.2887 | 525:32 | 262:46 | 96.8673 | 96.722
69 | Achanur | 1 | 1 | 3:06 | 16:21 | 30:21 | 3:12 | 33:33 | 409:03 | 36:39 | 36:39 | 95.0074 | 94.5461 | 425:24 | 425:24 | 94.8971 | 94.6931
70 | Shirur | 1 | 1 | 1:18 | 61:56 | 0:00 | 3:21 | 3:21 | 233:31 | 4:39 | 4:39 | 99.5015 | 99.308 | 295:27 | 295:27 | 97.0869 | 96.3142
71 | Badami | 1 | 1 | 0:00 | 30:31 | 9:34 | 7:05 | 16:39 | 235:20 | 16:39 | 16:39 | 97.5223 | 97.5223 | 265:51 | 265:51 | 97.0642 | 96.6835
72 | Kulageri | 1 | 1 | 0:20 | 11:56 | 4:51 | 4:30 | 9:21 | 108:38 | 9:41 | 9:41 | 98.6086 | 98.559 | 120:34 | 120:34 | 98.6448 | 98.4959
73 | Jamkhandi | 6 | 6 | 2:00 | 124:20 | 43:40 | 6:15 | 49:55 | 968:55 | 51:55 | 8:39 | 98.762 | 98.7124 | 1093:15 | 182:12 | 97.9855 | 97.7269
74 | Mahalingapur | 3 | 3 | 0:36 | 74:37 | 32:40 | 9:50 | 42:30 | 754:57 | 43:06 | 14:22 | 97.8919 | 97.8621 | 829:34 | 276:31 | 96.8607 | 96.5504
75 | Rabakavi | 2 | 2 | 0:00 | 30:20 | 5:55 | 2:40 | 8:35 | 217:49 | 8:35 | 4:18 | 99.3614 | 99.3614 | 248:09 | 124:04 | 98.6414 | 98.4522
76 | Banahatti | 2 | 2 | 0:00 | 47:15 | 8:10 | 1:05 | 9:15 | 364:10 | 9:15 | 4:38 | 99.3118 | 99.3118 | 411:25 | 205:43 | 97.7285 | 97.4338
77 | Teradal | 2 | 2 | 0:00 | 37:20 | 16:15 | 3:35 | 19:50 | 482:53 | 19:50 | 9:55 | 98.5243 | 98.5243 | 520:13 | 260:06 | 96.988 | 96.7551
78 | Mudhol | 4 | 4 | 11:15 | 98:37 | 38:47 | 4:36 | 43:23 | 736:46 | 54:38 | 13:39 | 98.386 | 97.9675 | 835:23 | 208:51 | 97.7022 | 97.3946
79 | Bilagi | 1 | 1 | 0:30 | 46:15 | 17:35 | 1:00 | 18:35 | 167:22 | 19:05 | 19:05 | 97.2346 | 97.1602 | 213:37 | 213:37 | 97.9121 | 97.3351
80 | Lokapur | 2 | 2 | 0:00 | 15:52 | 44:25 | 21:50 | 66:15 | 764:10 | 66:15 | 33:08 | 95.0707 | 95.0707 | 780:02 | 390:01 | 95.2335 | 95.1345
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of MARCH-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of March-2021 |  |  |  | Reliability for cumulative period from April-20 to March-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 63:45 | 243:49 | 394:33 | 182:58 | 577:31 | 7152:37 | 641:16 | 8:07 | 99.0174 | 98.909 | 7396:26 | 93:38 | 98.9664 | 98.9312
2 | Dharwad(R) | 19 | 19 | 14:00 | 341:16 | 205:13 | 105:13 | 310:26 | 4886:47 | 324:26 | 17:05 | 97.804 | 97.7049 | 5228:03 | 275:10 | 97.0639 | 96.8589
3 | Kundagol | 1 | 1 | 4:20 | 176:10 | 0:45 | 8:00 | 8:45 | 164:25 | 13:05 | 13:05 | 98.8239 | 98.2415 | 340:35 | 340:35 | 98.1231 | 96.1121
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 18:12 | 3:27 | 21:39 | 205:40 | 21:39 | 21:39 | 97.0901 | 97.0901 | 205:40 | 205:40 | 97.6522 | 97.6522
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 9:00 | 5:15 | 14:15 | 240:12 | 14:15 | 14:15 | 98.0847 | 98.0847 | 240:12 | 240:12 | 97.258 | 97.258
6 | Kalghatagi | 2 | 2 | 0:00 | 2:20 | 66:05 | 9:20 | 75:25 | 705:50 | 75:25 | 37:42 | 94.9317 | 94.9317 | 708:10 | 354:05 | 95.9713 | 95.958
7 | Alnavar | 1 | 1 | 8:25 | 42:25 | 11:25 | 0:25 | 11:50 | 204:50 | 20:15 | 20:15 | 98.4095 | 97.2782 | 247:15 | 247:15 | 97.6617 | 97.1775
8 | Naragund | 2 | 2 | 9:20 | 56:50 | 32:50 | 25:45 | 58:35 | 705:05 | 67:55 | 33:58 | 96.0629 | 95.4357 | 761:55 | 380:58 | 95.9756 | 95.6512
9 | Shirahatti | 4 | 4 | 0:00 | 18:50 | 15:55 | 30:05 | 46:00 | 1039:28 | 46:00 | 11:30 | 98.4543 | 98.4543 | 1058:18 | 264:34 | 97.0335 | 96.9797
10 | Laxmeshwar | 5 | 5 | 0:00 | 0:00 | 20:20 | 17:27 | 37:47 | 1236:16 | 37:47 | 7:33 | 98.9843 | 98.9843 | 1236:16 | 247:15 | 97.1775 | 97.1775
11 | Naregal | 1 | 1 | 0:00 | 21:45 | 9:05 | 10:15 | 19:20 | 198:55 | 19:20 | 19:20 | 97.4014 | 97.4014 | 220:40 | 220:40 | 97.7293 | 97.481
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 34:10 | 21:20 | 55:30 | 467:05 | 55:30 | 27:45 | 96.2702 | 96.2702 | 467:05 | 233:32 | 97.334 | 97.334
13 | Ron | 3 | 3 | 0:00 | 48:30 | 34:55 | 31:35 | 66:30 | 715:05 | 66:30 | 22:10 | 97.0206 | 97.0206 | 763:35 | 254:32 | 97.279 | 97.0944
14 | Mundaragi | 3 | 3 | 0:00 | 76:15 | 31:30 | 25:10 | 56:40 | 823:51 | 56:40 | 18:53 | 97.4612 | 97.4612 | 900:06 | 300:02 | 96.8651 | 96.575
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 15:32 | 6:59 | 22:31 | 405:22 | 22:31 | 22:31 | 96.9736 | 96.9736 | 405:22 | 405:22 | 95.3725 | 95.3725
16 | G.C.T.M | 1 | 1 | 18:45 | 152:40 | 9:35 | 0:55 | 10:30 | 247:30 | 29:15 | 29:15 | 98.5887 | 96.0685 | 400:10 | 400:10 | 97.1747 | 95.4319
17 | F.C.S.M | 2 | 2 | 32:30 | 267:30 | 50:45 | 1:20 | 52:05 | 449:19 | 84:35 | 42:18 | 96.4998 | 94.3156 | 716:49 | 358:25 | 97.4354 | 95.9086
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 12:15 | 4:50 | 17:05 | 217:14 | 17:05 | 17:05 | 97.7039 | 97.7039 | 217:14 | 217:14 | 97.5202 | 97.5202
19 | Hole-Alur | 1 | 1 | 20:40 | 110:30 | 20:15 | 5:15 | 25:30 | 201:35 | 46:10 | 46:10 | 96.5726 | 93.7948 | 312:05 | 312:05 | 97.6988 | 96.4374
20 | Savanur | 2 | 2 | 4:02 | 69:27 | 12:05 | 7:45 | 19:50 | 738:35 | 23:52 | 11:56 | 98.6671 | 98.3961 | 808:02 | 404:01 | 95.7843 | 95.3879
21 | Shiggaon | 2 | 2 | 17:55 | 175:58 | 26:55 | 18:28 | 45:23 | 695:53 | 63:18 | 31:39 | 96.95 | 95.746 | 871:51 | 435:56 | 96.0281 | 95.0237
22 | Bankapur | 1 | 1 | 17:05 | 206:30 | 14:25 | 8:05 | 22:30 | 289:27 | 39:35 | 39:35 | 96.9758 | 94.6797 | 495:57 | 495:57 | 96.6958 | 94.3385
23 | Hangal | 2 | 2 | 2:50 | 54:20 | 30:15 | 12:30 | 42:45 | 495:35 | 45:35 | 22:48 | 97.127 | 96.9366 | 549:55 | 274:58 | 97.1713 | 96.8612
24 | Ranebennur | 16 | 16 | 65:34 | 254:33 | 207:21 | 27:02 | 234:23 | 3498:56 | 299:57 | 18:45 | 98.0311 | 97.4803 | 3753:29 | 234:36 | 97.5036 | 97.322
25 | Halageri | 2 | 2 | 24:30 | 395:20 | 12:40 | 4:15 | 16:55 | 428:45 | 41:25 | 20:42 | 98.8631 | 97.2166 | 824:05 | 412:02 | 97.5528 | 95.2963
26 | Tuminakatti | 2 | 2 | 1:45 | 9:55 | 7:50 | 0:55 | 8:45 | 169:20 | 10:30 | 5:15 | 99.412 | 99.2944 | 179:15 | 89:38 | 99.0335 | 98.9769
27 | Kahanderayanahalli | 1 | 1 | 5:28 | 19:56 | 1:30 | 1:20 | 2:50 | 376:05 | 8:18 | 8:18 | 99.6192 | 98.8844 | 396:01 | 396:01 | 95.7068 | 95.4793
28 | Rattihalli | 1 | 1 | 4:20 | 16:30 | 13:30 | 7:35 | 21:05 | 247:35 | 25:25 | 25:25 | 97.1662 | 96.5838 | 264:05 | 264:05 | 97.1737 | 96.9854
29 | Hirekerur | 2 | 2 | 17:05 | 131:52 | 12:55 | 21:55 | 34:50 | 487:15 | 51:55 | 25:57 | 97.6591 | 96.511 | 619:07 | 309:34 | 97.2189 | 96.4662
30 | Byadagi | 8 | 8 | 55:10 | 311:15 | 66:45 | 40:00 | 106:45 | 2093:58 | 161:55 | 20:14 | 98.2065 | 97.2796 | 2405:13 | 300:39 | 97.012 | 96.5679
31 | Sirsi | 5 | 5 | 3:20 | 54:15 | 24:26 | 25:14 | 49:40 | 539:09 | 53:00 | 10:36 | 98.6649 | 98.5753 | 593:24 | 118:41 | 98.7691 | 98.6452
32 | Yellapur | 3 | 3 | 19:35 | 280:51 | 6:50 | 3:45 | 10:35 | 280:05 | 30:10 | 10:03 | 99.5258 | 98.6484 | 560:56 | 186:59 | 98.9342 | 97.8656
33 | Mundagod | 3 | 3 | 10:30 | 699:30 | 20:20 | 12:00 | 32:20 | 1077:13 | 42:50 | 14:17 | 98.5514 | 98.0809 | 1776:43 | 592:14 | 95.901 | 93.2393
34 | Siddapur | 2 | 2 | 5:40 | 396:50 | 8:30 | 6:10 | 14:40 | 337:48 | 20:20 | 10:10 | 99.0143 | 98.6335 | 734:38 | 367:19 | 98.0719 | 95.8069
35 | Dandeli | 8 | 8 | 53:16 | 325:56 | 125:48 | 15:44 | 141:32 | 1738:23 | 194:48 | 24:21 | 97.6221 | 96.7272 | 2064:19 | 258:02 | 97.5194 | 97.0543
36 | Haliyal | 3 | 3 | 0:34 | 45:49 | 44:20 | 9:50 | 54:10 | 464:04 | 54:44 | 18:15 | 97.5732 | 97.5478 | 509:53 | 169:58 | 98.2341 | 98.0598
37 | Ankola | 3 | 3 | 28:57 | 540:14 | 5:23 | 3:25 | 8:48 | 432:36 | 37:45 | 12:35 | 99.6057 | 98.3087 | 972:50 | 324:17 | 98.3539 | 96.2982
38 | Kumta | 3 | 3 | 9:06 | 67:18 | 11:53 | 9:54 | 21:47 | 467:22 | 30:53 | 10:18 | 99.024 | 98.6163 | 534:40 | 178:13 | 98.2216 | 97.9655
39 | Gokarna | 1 | 1 | 6:15 | 131:00 | 2:45 | 0:10 | 2:55 | 70:03 | 9:10 | 9:10 | 99.608 | 98.7679 | 201:03 | 201:03 | 99.2003 | 97.7049
40 | Kasarkod | 1 | 1 | 47:11 | 237:53 | 8:50 | 1:40 | 10:30 | 127:57 | 57:41 | 57:41 | 98.5887 | 92.2469 | 365:50 | 365:50 | 98.5394 | 95.8238
41 | Honnavar | 3 | 3 | 10:06 | 195:12 | 17:33 | 8:30 | 26:03 | 437:33 | 36:09 | 12:03 | 98.8329 | 98.3804 | 632:45 | 210:55 | 98.335 | 97.5923
42 | Murdeshwar | 4 | 4 | 13:36 | 275:56 | 54:32 | 5:07 | 59:39 | 710:30 | 73:15 | 18:19 | 97.9956 | 97.5386 | 986:26 | 246:36 | 97.9723 | 97.1848
43 | Bhatkal | 3 | 3 | 26:33 | 334:12 | 9:30 | 3:52 | 13:22 | 411:03 | 39:55 | 13:18 | 99.4011 | 98.2116 | 745:15 | 248:25 | 98.4359 | 97.1642
44 | Khanapur | 2 | 2 | 0:10 | 110:40 | 11:10 | 4:40 | 15:50 | 416:45 | 16:00 | 8:00 | 98.9359 | 98.9247 | 527:25 | 263:43 | 97.6213 | 96.9896
45 | Bailhongal | 3 | 3 | 0:00 | 13:17 | 46:30 | 8:25 | 54:55 | 607:38 | 54:55 | 18:18 | 97.5396 | 97.5396 | 620:55 | 206:58 | 97.6878 | 97.6373
46 | Soundatti | 3 | 3 | 21:38 | 92:46 | 21:48 | 3:33 | 25:21 | 437:28 | 46:59 | 15:40 | 98.8642 | 97.895 | 530:14 | 176:45 | 98.3354 | 97.9824
47 | Ramdurg | 2 | 2 | 2:20 | 71:58 | 11:06 | 4:55 | 16:01 | 357:49 | 18:21 | 9:10 | 98.9236 | 98.7668 | 429:47 | 214:54 | 97.9577 | 97.5469
48 | Gokak | 11 | 11 | 23:13 | 439:50 | 74:31 | 15:16 | 89:47 | 1422:58 | 113:00 | 10:16 | 98.9029 | 98.6193 | 1862:48 | 169:21 | 98.5233 | 98.0668
49 | Mudalagi | 2 | 2 | 0:00 | 76:05 | 12:45 | 1:55 | 14:40 | 343:20 | 14:40 | 7:20 | 99.0143 | 99.0143 | 419:25 | 209:43 | 98.0403 | 97.6061
50 | Konnur | 1 | 1 | 0:05 | 5:30 | 18:45 | 4:05 | 22:50 | 235:55 | 22:55 | 22:55 | 96.931 | 96.9198 | 241:25 | 241:25 | 97.3069 | 97.2441
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 22:38 | 10:39 | 33:17 | 366:19 | 33:17 | 33:17 | 95.5264 | 95.5264 | 366:19 | 366:19 | 95.8183 | 95.8183
52 | Kudachi | 1 | 1 | 5:20 | 23:25 | 30:55 | 6:25 | 37:20 | 418:40 | 42:40 | 42:40 | 94.9821 | 94.2652 | 442:05 | 442:05 | 95.2207 | 94.9534
53 | Athani | 6 | 6 | 40:30 | 306:06 | 43:59 | 27:21 | 71:20 | 1242:33 | 111:50 | 18:38 | 98.402 | 97.4948 | 1548:39 | 258:07 | 97.6359 | 97.0536
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 2:45 | 10:45 | 13:30 | 217:20 | 13:30 | 6:45 | 99.0927 | 99.0927 | 217:20 | 108:40 | 98.7595 | 98.7595
55 | Nippani | 5 | 5 | 0:00 | 60:50 | 44:55 | 23:10 | 68:05 | 891:25 | 68:05 | 13:37 | 98.1698 | 98.1698 | 952:15 | 190:27 | 97.9648 | 97.8259
56 | Sadalaga | 1 | 1 | 1:45 | 10:00 | 6:40 | 3:00 | 9:40 | 267:10 | 11:25 | 11:25 | 98.7007 | 98.4655 | 277:10 | 277:10 | 96.9502 | 96.836
57 | Muddebihal | 2 | 2 | 38:40 | 81:58 | 77:50 | 17:20 | 95:10 | 808:24 | 133:50 | 66:55 | 93.6044 | 91.0058 | 890:22 | 445:11 | 95.3858 | 94.918
58 | Talikoti | 1 | 1 | 7:10 | 67:00 | 7:05 | 3:40 | 10:45 | 255:50 | 17:55 | 17:55 | 98.5551 | 97.5918 | 322:50 | 322:50 | 97.0795 | 96.3147
59 | B.Bagewadi | 1 | 1 | 5:12 | 43:17 | 3:35 | 2:20 | 5:55 | 118:55 | 11:07 | 11:07 | 99.2047 | 98.5058 | 162:12 | 162:12 | 98.6425 | 98.1484
60 | Indi | 3 | 3 | 2:28 | 27:26 | 31:14 | 7:37 | 38:51 | 281:15 | 41:19 | 13:46 | 98.2594 | 98.1489 | 308:41 | 102:54 | 98.9298 | 98.8254
61 | Sindagi | 2 | 2 | 1:20 | 146:20 | 18:35 | 1:25 | 20:00 | 312:15 | 21:20 | 10:40 | 98.6559 | 98.5663 | 458:35 | 229:18 | 98.2178 | 97.3825
62 | Guledgudda | 1 | 1 | 1:30 | 22:55 | 7:25 | 2:35 | 10:00 | 174:21 | 11:30 | 11:30 | 98.6559 | 98.4543 | 197:16 | 197:16 | 98.0097 | 97.7481
63 | Ilkal | 8 | 8 | 52:35 | 407:39 | 130:34 | 22:55 | 153:29 | 2880:32 | 206:04 | 25:46 | 97.4213 | 96.5379 | 3288:11 | 411:01 | 95.8896 | 95.308
64 | Kerur | 2 | 2 | 3:55 | 27:15 | 6:03 | 4:00 | 10:03 | 253:33 | 13:58 | 6:59 | 99.3246 | 99.0614 | 280:48 | 140:24 | 98.5528 | 98.3973
65 | Hungund | 4 | 4 | 20:52 | 176:57 | 31:48 | 18:58 | 50:46 | 926:05 | 71:38 | 17:54 | 98.2941 | 97.593 | 1103:02 | 275:46 | 97.3571 | 96.8521
66 | Gaddankeri | 3 | 3 | 23:48 | 158:04 | 9:52 | 11:47 | 21:39 | 588:20 | 45:27 | 15:09 | 99.03 | 97.9637 | 746:24 | 248:48 | 97.7613 | 97.1598
67 | Rampur | 1 | 1 | 1:06 | 48:37 | 8:09 | 0:33 | 8:42 | 150:36 | 9:48 | 9:48 | 98.8306 | 98.6828 | 199:13 | 199:13 | 98.2808 | 97.7258
68 | Kaladagi | 2 | 2 | 1:00 | 24:18 | 15:48 | 10:24 | 26:12 | 528:26 | 27:12 | 13:36 | 98.2392 | 98.172 | 552:44 | 276:22 | 96.9838 | 96.8451
69 | Achanur | 1 | 1 | 1:18 | 17:39 | 29:12 | 10:06 | 39:18 | 448:21 | 40:36 | 40:36 | 94.7177 | 94.543 | 466:00 | 466:00 | 94.8818 | 94.6804
70 | Shirur | 1 | 1 | 5:00 | 66:56 | 3:24 | 2:03 | 5:27 | 238:58 | 10:27 | 10:27 | 99.2675 | 98.5954 | 305:54 | 305:54 | 97.2721 | 96.508
71 | Badami | 1 | 1 | 4:38 | 35:09 | 10:38 | 2:43 | 13:21 | 248:41 | 17:59 | 17:59 | 98.2056 | 97.5829 | 283:50 | 283:50 | 97.1611 | 96.7599
72 | Kulageri | 1 | 1 | 2:50 | 14:46 | 4:45 | 0:15 | 5:00 | 113:38 | 7:50 | 7:50 | 99.328 | 98.9471 | 128:24 | 128:24 | 98.7028 | 98.5342
73 | Jamkhandi | 6 | 6 | 7:30 | 131:50 | 37:25 | 8:05 | 45:30 | 1014:25 | 53:00 | 8:50 | 98.9807 | 98.8127 | 1146:15 | 191:02 | 98.07 | 97.8192
74 | Mahalingapur | 3 | 3 | 1:08 | 75:45 | 38:48 | 4:35 | 43:23 | 798:20 | 44:31 | 14:50 | 98.0563 | 98.0055 | 874:05 | 291:22 | 96.9622 | 96.674
75 | Rabakavi | 2 | 2 | 3:50 | 34:10 | 10:30 | 5:35 | 16:05 | 233:54 | 19:55 | 9:58 | 98.9191 | 98.6615 | 268:04 | 134:02 | 98.665 | 98.4699
76 | Banahatti | 2 | 2 | 0:00 | 47:15 | 17:30 | 0:35 | 18:05 | 382:15 | 18:05 | 9:02 | 98.7847 | 98.7847 | 429:30 | 214:45 | 97.8182 | 97.5485
77 | Teradal | 2 | 2 | 0:00 | 37:20 | 16:51 | 3:34 | 20:25 | 503:18 | 20:25 | 10:13 | 98.6279 | 98.6279 | 540:38 | 270:19 | 97.1273 | 96.9142
78 | Mudhol | 4 | 4 | 2:52 | 101:29 | 64:25 | 12:06 | 76:31 | 813:17 | 79:23 | 19:51 | 97.4289 | 97.3325 | 914:46 | 228:42 | 97.679 | 97.3894
79 | Bilagi | 1 | 1 | 1:45 | 48:00 | 11:50 | 1:10 | 13:00 | 180:22 | 14:45 | 14:45 | 98.2527 | 98.0175 | 228:22 | 228:22 | 97.941 | 97.3931
80 | Lokapur | 2 | 2 | 4:20 | 20:12 | 26:55 | 7:20 | 34:15 | 798:25 | 38:35 | 19:18 | 97.6983 | 97.407 | 818:37 | 409:18 | 95.4428 | 95.3275
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]

## RURAL (Incl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2020
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2020 |  |  |  | Reliability for cumulative period from Apr-20 to Apr-20
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 151:31 | 151:31 | 3564:05 | 964:32 | 4528:37 | 4528:37 | 4680:08 | 106:22 | 85.7051 | 85.2269 | 4680:08 | 106:22 | 85.7051 | 85.2269
2 | Dharwad Rural | 80 | 80 | 297:31 | 297:31 | 12769:40 | 4214:55 | 16984:35 | 16984:35 | 17282:06 | 216:02 | 70.5129 | 69.9964 | 17282:06 | 216:02 | 70.5129 | 69.9964
3 | Gadag | 84 | 84 | 352:35 | 352:35 | 14236:54 | 2025:10 | 16262:04 | 16262:04 | 16614:39 | 197:48 | 73.1117 | 72.5287 | 16614:39 | 197:48 | 73.1117 | 72.5287
4 | Ron | 53 | 53 | 118:35 | 118:35 | 6344:10 | 1632:40 | 7976:50 | 7976:50 | 8095:25 | 152:45 | 79.0963 | 78.7856 | 8095:25 | 152:45 | 79.0963 | 78.7856
5 | Haveri | 193 | 193 | 1518:18 | 1518:18 | 2437.3 | 3519:51 | 2583.9604 | 2583.9604 | 2647.2229 | 329:11 | 55.372 | 54.2794 | 2647.2229 | 329:11 | 55.372 | 54.2794
6 | Ranebennur | 177 | 177 | 963:05 | 963:05 | 2389.9868 | 3830:01 | 2549.5708 | 2549.5708 | 2589.6993 | 351:09 | 51.9855 | 51.2298 | 2589.6993 | 351:09 | 51.9855 | 51.2298
7 | Sirsi | 51 | 51 | 535:59 | 535:59 | 736:46 | 1745:16 | 2482:02 | 2482:02 | 3018:01 | 59:11 | 93.2406 | 91.781 | 3018:01 | 59:11 | 93.2406 | 91.781
8 | Dandeli | 19 | 19 | 6:31 | 6:31 | 285:47 | 423:49 | 709:36 | 709:36 | 716:07 | 37:41 | 94.8129 | 94.7652 | 716:07 | 37:41 | 94.8129 | 94.7652
9 | Karwar | 30 | 30 | 152:48 | 152:48 | 266:49 | 375:24 | 642:13 | 642:13 | 795:01 | 26:30 | 97.0268 | 96.3194 | 795:01 | 26:30 | 97.0268 | 96.3194
10 | Honnavar | 38 | 38 | 212:57 | 212:57 | 482:36 | 497:36 | 980:12 | 980:12 | 1193:09 | 31:24 | 96.4174 | 95.6391 | 1193:09 | 31:24 | 96.4174 | 95.6391
11 | Belagavi | 131 | 131 | 476:54 | 476:54 | 19369:46 | 2587:41 | 21957:27 | 21957:27 | 22434:21 | 171:15 | 76.7203 | 76.2146 | 22434:21 | 171:15 | 76.7203 | 76.2146
12 | Bailhongal | 189 | 189 | 816:28 | 816:28 | 1611.3063 | 5364:28 | 1834.8257 | 1834.8257 | 1868.8451 | 237:19 | 67.6398 | 67.0398 | 1868.8451 | 237:19 | 67.6398 | 67.0398
13 | Ramdurg | 73 | 73 | 298:25 | 298:25 | 21805:23 | 3241:18 | 1043.6118 | 1043.6118 | 1056.0458 | 347:12 | 52.3465 | 51.7787 | 1056.0458 | 347:12 | 52.3465 | 51.7787
14 | Ghataprabha | 157 | 157 | 485:40 | 485:40 | 1630.159 | 1278:11 | 1683.4167 | 1683.4167 | 1703.6528 | 260:26 | 64.2587 | 63.829 | 1703.6528 | 260:26 | 64.2587 | 63.829
15 | Raibag | 160 | 160 | 459:18 | 459:18 | 1571.5972 | 1319:03 | 1626.5576 | 1626.5576 | 1645.6951 | 246:51 | 66.1134 | 65.7147 | 1645.6951 | 246:51 | 66.1134 | 65.7147
16 | Athani | 180 | 180 | 688:57 | 688:57 | 1544.9785 | 1954:08 | 1626.4007 | 1626.4007 | 1655.1069 | 220:41 | 69.8815 | 69.3499 | 1655.1069 | 220:41 | 69.8815 | 69.3499
17 | Chikkodi | 183 | 183 | 418:21 | 418:21 | 1936.784 | 1536:28 | 2000.8035 | 2000.8035 | 2018.2347 | 264:41 | 63.5555 | 63.238 | 2018.2347 | 264:41 | 63.5555 | 63.238
18 | Vijayapur | 145 | 145 | 285:52 | 285:52 | 1355.2826 | 2939:40 | 1477.7687 | 1477.7687 | 1489.6799 | 246:34 | 66.0283 | 65.7545 | 1489.6799 | 246:34 | 66.0283 | 65.7545
19 | Indi | 235 | 235 | 1177:32 | 1177:32 | 2788.0868 | 5344:03 | 3010.7556 | 3010.7556 | 3059.8194 | 312:30 | 57.2942 | 56.5983 | 3059.8194 | 312:30 | 57.2942 | 56.5983
20 | B.Bagewadi | 125 | 125 | 388:52 | 388:52 | 1278.0806 | 2822:53 | 1395.7007 | 1395.7007 | 1411.9035 | 271:05 | 62.7813 | 62.3492 | 1411.9035 | 271:05 | 62.7813 | 62.3492
21 | Bagalkot | 179 | 179 | 617:27 | 617:27 | 1643.6326 | 4732:05 | 1840.8028 | 1840.8028 | 1866.5299 | 250:16 | 65.7206 | 65.2415 | 1866.5299 | 250:16 | 65.7206 | 65.2415
22 | Jamkhandi | 225 | 225 | 823:01 | 823:01 | 2572.1354 | 1526:39 | 2635.7458 | 2635.7458 | 2670.0382 | 284:48 | 60.9519 | 60.4439 | 2670.0382 | 284:48 | 60.9519 | 60.4439
23 | Mudhol | 161 | 161 | 119:39 | 119:39 | 2138.6319 | 1792:52 | 2213.3347 | 2213.3347 | 2218.3201 | 330:41 | 54.1753 | 54.072 | 2218.3201 | 330:41 | 54.1753 | 54.072
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2020
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2020 |  |  |  | Reliability for cumulative period from Apr-20 to May-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 285:49 | 437:20 | 5282:00 | 1610:23 | 6892:23 | 11421:00 | 7178:12 | 163:08 | 78.9456 | 78.0725 | 11858:20 | 269:30 | 82.2699 | 81.591
2 | Dharwad Rural | 80 | 80 | 297:31 | 595:02 | 13060:53 | 3237:12 | 16298:05 | 1386.7778 | 16595:36 | 207:27 | 72.6175 | 72.1176 | 1411.5708 | 423:28 | 71.5824 | 71.0744
3 | Gadag | 84 | 84 | 413:40 | 766:15 | 14983:49 | 7046:39 | 22030:28 | 1595.5222 | 22444:08 | 267:12 | 64.749 | 64.0871 | 1627.4493 | 464:59 | 68.8618 | 68.2387
4 | Ron | 53 | 53 | 400:12 | 518:47 | 6513:35 | 2540:17 | 9053:52 | 17030:42 | 9454:04 | 178:23 | 77.0393 | 76.0244 | 17549:29 | 331:07 | 78.051 | 77.3824
5 | Haveri | 193 | 193 | 2522:55 | 4041:13 | 2296.2583 | 12904:24 | 2833.9417 | 5417.9021 | 2939.0632 | 365:29 | 52.6334 | 50.8764 | 5586.2861 | 694:40 | 53.9803 | 52.55
6 | Ranebennur | 177 | 177 | 1854:39 | 2817:44 | 2294.3639 | 8271:10 | 2638.9958 | 5188.5667 | 2716.2729 | 368:18 | 51.9046 | 50.4962 | 5305.9722 | 719:27 | 51.9444 | 50.857
7 | Sirsi | 51 | 51 | 833:20 | 1369:19 | 1130:56 | 2389:34 | 3520:30 | 6002:32 | 4353:50 | 85:22 | 90.7219 | 88.5256 | 7371:51 | 144:33 | 91.9606 | 90.1266
8 | Dandeli | 20 | 20 | 184:11 | 190:42 | 448:21 | 694:18 | 1142:39 | 1852:15 | 1326:50 | 66:20 | 92.3209 | 91.0831 | 2042:57 | 102:09 | 93.674 | 93.0227
9 | Karwar | 31 | 31 | 316:24 | 469:12 | 539:36 | 401:49 | 941:25 | 1583:38 | 1257:49 | 40:34 | 95.9182 | 94.5464 | 2052:50 | 66:13 | 96.5106 | 95.4767
10 | Honnavar | 38 | 38 | 679:59 | 892:56 | 716:19 | 645:55 | 1362:14 | 2342:26 | 2042:13 | 53:45 | 95.1817 | 92.7765 | 3235:22 | 85:08 | 95.7894 | 94.1843
11 | Belagavi | 131 | 131 | 593:52 | 1070:46 | 19721:37 | 1959:00 | 21680:37 | 1818.2528 | 22274:29 | 170:02 | 77.7553 | 77.1459 | 1862.8681 | 341:17 | 77.2462 | 76.6879
12 | Bailhongal | 189 | 189 | 1454:18 | 2270:46 | 1545.9271 | 4678:50 | 1740.8785 | 3575.7042 | 1801.4743 | 228:46 | 70.2871 | 69.2529 | 3670.3194 | 466:04 | 68.9851 | 68.1645
13 | Ramdurg | 74 | 74 | 372:15 | 670:40 | 23469:29 | 2062:35 | 1063.8361 | 2107.4479 | 1079.3465 | 350:04 | 53.6253 | 52.9491 | 2135.3924 | 692:34 | 53.3131 | 52.694
14 | Ghataprabha | 157 | 157 | 598:41 | 1084:21 | 1852.7785 | 3104:29 | 1982.1319 | 3665.5486 | 2007.0771 | 306:49 | 59.2741 | 58.7615 | 3710.7299 | 567:15 | 61.7255 | 61.2537
15 | Raibag | 163 | 163 | 956:50 | 1416:08 | 1809.8354 | 1919:37 | 1889.8194 | 3516.3771 | 1929.6875 | 284:08 | 62.6001 | 61.8111 | 3575.3826 | 526:26 | 64.6346 | 64.0412
16 | Athani | 182 | 182 | 1180:23 | 1869:20 | 1691.1347 | 2389:06 | 1790.6806 | 3417.0812 | 1839.8632 | 242:37 | 68.2616 | 67.3899 | 3494.9701 | 460:53 | 69.221 | 68.5195
17 | Chikkodi | 185 | 185 | 365:07 | 783:28 | 1898.3576 | 1544:39 | 1962.7181 | 3963.5215 | 1977.9312 | 256:36 | 65.7765 | 65.5112 | 3996.166 | 518:25 | 64.878 | 64.5887
18 | Vijayapur | 147 | 147 | 653:00 | 938:52 | 1415.1535 | 4439:23 | 1600.1278 | 3077.8965 | 1627.3361 | 265:41 | 64.8864 | 64.2893 | 3117.016 | 508:54 | 65.6753 | 65.239
19 | Indi | 246 | 246 | 2118:08 | 3295:40 | 3076.2451 | 5427:59 | 3302.4111 | 6313.1667 | 3390.6667 | 330:48 | 56.6954 | 55.5381 | 6450.4861 | 629:19 | 57.9291 | 57.014
20 | B.Bagewadi | 127 | 127 | 693:53 | 1082:45 | 1376.9014 | 2988:28 | 1501.4208 | 2897.1215 | 1530.3326 | 289:12 | 61.8638 | 61.1295 | 2942.2361 | 556:01 | 62.6033 | 62.021
21 | Bagalkot | 179 | 179 | 1587:22 | 2204:49 | 1701.3389 | 4665:25 | 1895.7313 | 3736.534 | 1961.8715 | 263:03 | 65.8365 | 64.6446 | 3828.4014 | 513:18 | 65.7795 | 64.9382
22 | Jamkhandi | 201 | 201 | 415:08 | 1238:09 | 2328.4042 | 2394:38 | 2428.1806 | 5063.9264 | 2445.4778 | 292:00 | 61.0306 | 60.753 | 5115.516 | 610:48 | 58.6989 | 58.2782
23 | Mudhol | 190 | 190 | 293:28 | 413:07 | 2584.8354 | 2725:07 | 2698.3819 | 4911.7167 | 2710.6097 | 342:24 | 54.1871 | 53.9795 | 4928.9299 | 622:36 | 57.6211 | 57.4726
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2020
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2020 |  |  |  | Reliability for cumulative period from Apr-20 to June-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 327:45 | 765:05 | 5066:51 | 1288:58 | 6355:49 | 17776:49 | 6683:34 | 151:54 | 79.9374 | 78.9029 | 18541:54 | 421:24 | 81.501 | 80.7048
2 | Dharwad Rural | 80 | 80 | 97:15 | 692:17 | 13363:54 | 3143:32 | 16507:26 | 2074.5875 | 16604:41 | 207:34 | 71.3413 | 71.1724 | 2103.4326 | 631:02 | 71.5029 | 71.1067
3 | Gadag | 84 | 84 | 490:10 | 1256:25 | 14383:24 | 2720:56 | 17104:20 | 2308.2028 | 17594:30 | 209:27 | 71.719 | 70.9086 | 2360.5535 | 674:27 | 69.8037 | 69.1189
4 | Ron | 53 | 53 | 314:53 | 833:40 | 6368:50 | 1902:48 | 8271:38 | 1054.2639 | 8586:31 | 162:01 | 78.3238 | 77.4986 | 1089 | 493:08 | 78.1409 | 77.4207
5 | Haveri | 195 | 195 | 1695:50 | 5737:03 | 2103.3028 | 13879:25 | 2681.6118 | 8099.5139 | 2752.2715 | 338:44 | 54.1605 | 52.9526 | 8338.5576 | 1026:17 | 54.3561 | 53.009
6 | Ranebennur | 179 | 179 | 809:49 | 3627:33 | 2272.8986 | 8654:25 | 2633.4993 | 7822.066 | 2667.2417 | 357:37 | 50.959 | 50.3307 | 7973.2139 | 1069:02 | 51.9795 | 51.0515
7 | Sirsi | 52 | 52 | 806:50 | 2176:09 | 1146:56 | 2672:33 | 3819:29 | 9822:01 | 4626:19 | 88:58 | 89.7984 | 87.6434 | 11998:10 | 230:44 | 91.3514 | 89.4353
8 | Dandeli | 20 | 20 | 196:36 | 387:18 | 394:18 | 867:50 | 1262:08 | 3114:23 | 1458:44 | 72:56 | 91.2352 | 89.8699 | 3501:41 | 175:05 | 92.87 | 91.9833
9 | Karwar | 31 | 31 | 438:19 | 907:31 | 465:22 | 1178:00 | 1643:22 | 3227:00 | 2081:41 | 67:09 | 92.6372 | 90.6735 | 4134:31 | 133:22 | 95.2337 | 93.8932
10 | Honnavar | 38 | 38 | 379:36 | 1272:32 | 703:47 | 1281:27 | 1985:14 | 4327:40 | 2364:50 | 62:14 | 92.744 | 91.3566 | 5600:12 | 147:22 | 94.7854 | 93.2521
11 | Belagavi | 132 | 132 | 655:35 | 1726:21 | 20089:12 | 3627:46 | 23716:58 | 2806.4597 | 1015.5229 | 184:38 | 75.0453 | 74.3555 | 2878.391 | 523:21 | 76.6362 | 76.0374
12 | Bailhongal | 191 | 191 | 754:08 | 3024:54 | 1478.3229 | 5532:56 | 1708.8618 | 5284.566 | 1740.284 | 218:40 | 70.1769 | 69.6286 | 5410.6035 | 679:52 | 69.5957 | 68.8706
13 | Ramdurg | 75 | 75 | 794:45 | 1465:25 | 22450:13 | 2560:26 | 1042.1104 | 3149.5583 | 1075.225 | 344:04 | 53.684 | 52.2122 | 3210.6174 | 1027:24 | 53.8526 | 52.958
14 | Ghataprabha | 157 | 157 | 636:07 | 1720:28 | 1783.7035 | 2743:49 | 1898.0292 | 5563.5778 | 1924.534 | 294:12 | 59.7021 | 59.1394 | 5635.2639 | 861:26 | 61.0585 | 60.5567
15 | Raibag | 162 | 162 | 648:22 | 2064:30 | 1749.5493 | 2210:42 | 1841.6618 | 5358.0389 | 1868.6771 | 276:50 | 62.1057 | 61.5499 | 5444.0597 | 806:32 | 63.6546 | 63.0711
16 | Athani | 184 | 184 | 1219:29 | 3088:49 | 1564.5785 | 2317:15 | 1661.1306 | 5078.2118 | 1711.9424 | 223:18 | 69.9071 | 68.9866 | 5206.9125 | 679:10 | 69.6715 | 68.9028
17 | Chikkodi | 185 | 185 | 215:40 | 999:08 | 1741.4111 | 2462:13 | 1844.0035 | 5807.525 | 1852.9896 | 240:23 | 66.7747 | 66.6128 | 5849.1556 | 758:49 | 65.5033 | 65.256
18 | Vijayapur | 151 | 151 | 445:08 | 1384:00 | 1409.4542 | 6962:21 | 1699.5521 | 4777.4486 | 1718.0993 | 273:05 | 62.4823 | 62.0729 | 4835.1153 | 768:30 | 65.2322 | 64.8125
19 | Indi | 247 | 247 | 995:08 | 4290:48 | 3028.1361 | 8910:58 | 3399.4264 | 9712.5931 | 3440.8903 | 334:20 | 54.1238 | 53.5642 | 9891.3764 | 961:06 | 56.7887 | 55.9933
20 | B.Bagewadi | 127 | 127 | 753:49 | 1836:34 | 1291.8493 | 5711:05 | 1529.8111 | 4426.9326 | 1561.2201 | 295:02 | 59.8475 | 59.0231 | 4503.4562 | 851:03 | 61.6948 | 61.0327
21 | Bagalkot | 179 | 179 | 879:22 | 3084:11 | 1654.4875 | 6415:37 | 1921.8049 | 5658.3389 | 1958.4451 | 262:35 | 64.2122 | 63.5299 | 5786.8465 | 775:53 | 65.2628 | 64.4739
22 | Jamkhandi | 199 | 199 | 969:45 | 2207:54 | 2202.2701 | 3956:25 | 2367.1208 | 7431.0472 | 2407.5271 | 290:21 | 60.3497 | 59.6729 | 7523.0431 | 907:18 | 58.9649 | 58.4569
23 | Mudhol | 192 | 192 | 603:59 | 1017:06 | 2497.9368 | 3763:33 | 2654.7514 | 7566.4681 | 2679.9174 | 334:59 | 53.9106 | 53.4737 | 7608.8472 | 951:06 | 56.6937 | 56.4512
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of July-2020
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2020 |  |  |  | Reliability for cumulative period from Apr-20 to July-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 91:55 | 857:00 | 5241:03 | 1458:44 | 6699:47 | 1019.8583 | 6791:42 | 147:39 | 80.4237 | 80.1552 | 1055.5667 | 550:44 | 81.8272 | 81.1909
2 | Dharwad Rural | 81 | 81 | 62:10 | 754:27 | 13546:26 | 1960:06 | 15506:32 | 2720.6931 | 15568:42 | 192:12 | 74.269 | 74.1658 | 2752.1285 | 815:27 | 72.4682 | 72.1501
3 | Gadag | 87 | 87 | 68:20 | 1324:45 | 14863:01 | 3143:13 | 18006:14 | 3058.4625 | 18074:34 | 207:45 | 72.1817 | 72.0761 | 3113.6604 | 858:56 | 71.1846 | 70.6646
4 | Ron | 53 | 53 | 66:00 | 899:40 | 6368:25 | 1287:55 | 7656:20 | 1373.2778 | 7722:20 | 145:42 | 80.5835 | 80.4161 | 1410.7639 | 638:50 | 78.7616 | 78.1818
5 | Haveri | 195 | 195 | 794:30 | 6531:33 | 2358.4875 | 9220:40 | 2742.6819 | 10842.1958 | 2775.7861 | 341:38 | 54.6289 | 54.0813 | 11114.3437 | 1367:55 | 54.4254 | 53.2814
6 | Ranebennur | 179 | 179 | 726:41 | 4354:14 | 2433.4764 | 5766:06 | 2673.7306 | 10495.7965 | 2704.009 | 362:33 | 51.816 | 51.2703 | 10677.2229 | 1431:35 | 51.9379 | 51.1071
7 | Sirsi | 51 | 51 | 171:13 | 2347:22 | 421:18 | 1903:53 | 2325:11 | 12147:12 | 2496:24 | 48:57 | 93.8721 | 93.4208 | 14494:34 | 284:12 | 91.8654 | 90.2935
8 | Dandeli | 20 | 20 | 69:01 | 456:19 | 273:20 | 684:35 | 957:55 | 4072:18 | 1026:56 | 51:21 | 93.5624 | 93.0986 | 4528:37 | 226:26 | 93.0459 | 92.2667
9 | Karwar | 31 | 31 | 296:55 | 1204:26 | 437:12 | 767:39 | 1204:51 | 4431:51 | 1501:46 | 48:27 | 94.7761 | 93.4887 | 5636:17 | 181:49 | 95.1174 | 93.7905
10 | Honnavar | 39 | 39 | 371:28 | 1644:00 | 482:31 | 697:12 | 1179:43 | 5507:23 | 1551:11 | 39:46 | 95.9343 | 94.654 | 7151:23 | 183:22 | 95.1771 | 93.7374
11 | Belagavi | 131 | 131 | 215:01 | 1941:22 | 18562:59 | 1895:01 | 20458:00 | 3658.8764 | 20673:01 | 157:49 | 79.0097 | 78.7891 | 3739.7667 | 685:09 | 77.1063 | 76.6001
12 | Bailhongal | 191 | 191 | 389:41 | 3414:35 | 1677.175 | 4785:37 | 1876.5757 | 7161.1417 | 1892.8125 | 237:50 | 68.3064 | 68.0322 | 7303.416 | 917:42 | 69.2681 | 68.6576
13 | Ramdurg | 75 | 75 | 68:59 | 1534:24 | 1004.8444 | 1971:53 | 1087.0062 | 4236.5646 | 1089.8806 | 348:46 | 53.247 | 53.1234 | 4300.4979 | 1376:10 | 53.6987 | 53
14 | Ghataprabha | 157 | 157 | 430:23 | 2150:51 | 1550.7486 | 2254:39 | 1644.6924 | 7208.2701 | 1662.625 | 254:10 | 66.2073 | 65.8388 | 7297.8889 | 1115:36 | 62.3668 | 61.8989
15 | Raibag | 163 | 163 | 656:43 | 2721:13 | 1654.0819 | 1208:40 | 1704.4431 | 7062.4819 | 1731.8062 | 254:59 | 66.2687 | 65.7272 | 7175.866 | 1056:34 | 64.4852 | 63.915
16 | Athani | 184 | 184 | 739:15 | 3828:04 | 1503.5833 | 1805:47 | 1578.8243 | 6657.0361 | 1609.6264 | 209:57 | 72.3208 | 71.7807 | 6816.5389 | 889:07 | 70.3446 | 69.6341
17 | Chikkodi | 185 | 185 | 214:03 | 1213:11 | 1784.0694 | 1324:50 | 1839.2708 | 7646.7958 | 1848.1896 | 239:46 | 67.929 | 67.7735 | 7697.3451 | 998:34 | 66.1196 | 65.8957
18 | Vijayapur | 152 | 152 | 161:25 | 1545:25 | 1411.0521 | 5409:51 | 1636.4625 | 6413.9111 | 1643.1882 | 259:27 | 65.2703 | 65.1276 | 6478.3035 | 1022:53 | 65.4125 | 65.0652
19 | Indi | 247 | 247 | 1397:50 | 5688:38 | 3001.0514 | 8449:41 | 3353.1215 | 13065.7146 | 3411.3646 | 331:28 | 56.2084 | 55.4478 | 13302.741 | 1292:34 | 56.6413 | 55.8547
20 | B.Bagewadi | 128 | 128 | 582:08 | 2418:42 | 1344.6257 | 5496:40 | 1573.6535 | 6000.5861 | 1597.909 | 299:36 | 60.3414 | 59.7301 | 6101.3653 | 1144:00 | 61.5741 | 60.9288
21 | Bagalkot | 180 | 180 | 358:01 | 3442:12 | 1707.7674 | 5713:33 | 1945.8319 | 7604.1708 | 1960.7493 | 261:26 | 65.1285 | 64.8611 | 7747.5958 | 1033:01 | 65.3726 | 64.7195
22 | Jamkhandi | 200 | 200 | 548:11 | 2756:05 | 2186.2125 | 2400:38 | 2286.2389 | 9717.2861 | 2309.0799 | 277:05 | 63.1252 | 62.7568 | 9832.1229 | 1179:51 | 60.1751 | 59.7044
23 | Mudhol | 190 | 190 | 501:23 | 1518:29 | 2640.9708 | 2912:38 | 2762.3306 | 10328.7986 | 2783.2215 | 351:34 | 53.1013 | 52.7467 | 10392.0687 | 1312:41 | 55.4409 | 55.168
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of August-2020
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of August-2020 |  |  |  | Reliability for cumulative period from Apr-20 to August-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 177:45 | 1034:45 | 4022:11 | 2345:43 | 6367:54 | 1285.1875 | 6545:39 | 145:28 | 80.98 | 80.4491 | 1328.3021 | 708:26 | 81.3335 | 80.7073
2 | Dharwad Rural | 81 | 81 | 218:40 | 973:07 | 12370:35 | 4565:48 | 16936:23 | 3426.3757 | 17155:03 | 211:47 | 71.8964 | 71.5335 | 3466.9222 | 1027:14 | 72.3523 | 72.0252
3 | Gadag | 89 | 89 | 187:50 | 1512:35 | 15005:01 | 2685:07 | 17690:08 | 3795.5514 | 17877:58 | 200:53 | 73.2842 | 73.0005 | 3858.5757 | 1040:31 | 72.1264 | 71.6635
4 | Ron | 53 | 53 | 102:11 | 1001:51 | 6628:05 | 1532:15 | 8160:20 | 1713.2917 | 8262:31 | 155:54 | 79.3053 | 79.0462 | 1755.0354 | 794:44 | 78.8717 | 78.3569
5 | Haveri | 195 | 195 | 1259:32 | 7791:05 | 2204.3785 | 16959:37 | 2911.0292 | 13753.225 | 2963.5097 | 364:44 | 51.844 | 50.9759 | 14077.8535 | 1732:40 | 53.9024 | 52.8143
6 | Ranebennur | 182 | 182 | 596:05 | 4950:19 | 2413.0674 | 7266:27 | 2715.8361 | 13211.6326 | 2740.6729 | 361:24 | 51.8639 | 51.4237 | 13417.8958 | 1769:24 | 52.5546 | 51.8139
7 | Sirsi | 52 | 52 | 856:30 | 3203:52 | 757:55 | 3678:37 | 4436:32 | 16583:44 | 5293:02 | 101:47 | 88.5325 | 86.3187 | 19787:36 | 380:32 | 91.3149 | 89.637
8 | Dandeli | 20 | 20 | 217:18 | 673:37 | 303:43 | 599:40 | 903:23 | 4975:41 | 1120:41 | 56:02 | 93.9289 | 92.4685 | 5649:18 | 282:28 | 93.2248 | 92.3076
9 | Karwar | 31 | 31 | 541:11 | 1745:37 | 627:06 | 1006:49 | 1633:55 | 6065:46 | 2175:06 | 70:10 | 92.9157 | 90.5693 | 7811:23 | 251:59 | 94.6713 | 93.1378
10 | Honnavar | 39 | 39 | 631:09 | 2275:09 | 702:35 | 1064:34 | 1767:09 | 7274:32 | 2398:18 | 61:30 | 93.9097 | 91.7346 | 9549:41 | 244:52 | 94.9203 | 93.3316
11 | Belagavi | 131 | 131 | 651:05 | 2592:27 | 18727:51 | 6935:16 | 1069.2965 | 4728.1729 | 1096.425 | 200:52 | 73.6691 | 73.0011 | 4836.1917 | 886:01 | 76.4099 | 75.8709
12 | Bailhongal | 191 | 191 | 447:15 | 3861:50 | 1618.9132 | 7927:01 | 1949.2056 | 9110.3472 | 1967.841 | 247:16 | 67.0798 | 66.7651 | 9271.2569 | 1164:58 | 68.8247 | 68.2741
13 | Ramdurg | 75 | 75 | 177:55 | 1712:19 | 1025.6222 | 2546:48 | 1131.7389 | 5368.3035 | 1139.1521 | 364:32 | 51.3231 | 51.0042 | 5439.65 | 1740:41 | 53.2174 | 52.5956
14 | Ghataprabha | 157 | 157 | 88:49 | 2239:40 | 1490.5632 | 2249:57 | 1584.3111 | 8792.5813 | 1588.0118 | 242:45 | 67.4479 | 67.3719 | 8885.9007 | 1358:21 | 63.3963 | 63.0078
15 | Raibag | 163 | 163 | 149:05 | 2870:18 | 1491.7542 | 1757:26 | 1564.9806 | 8627.4625 | 1571.1924 | 231:20 | 69.0287 | 68.9058 | 8747.0583 | 1287:55 | 65.4057 | 64.9262
16 | Athani | 183 | 183 | 406:06 | 4234:10 | 1336.0653 | 1324:04 | 1391.2347 | 8048.2708 | 1408.1556 | 184:41 | 75.4762 | 75.1779 | 8224.6944 | 1078:39 | 71.2551 | 70.625
17 | Chikkodi | 185 | 185 | 179:45 | 1392:56 | 1783.8306 | 2082:52 | 1870.6167 | 9517.4125 | 1878.1063 | 243:39 | 67.3824 | 67.2519 | 9575.4514 | 1242:13 | 66.3755 | 66.1705
18 | Vijayapur | 151 | 151 | 355:38 | 1901:03 | 1323.8389 | 4212:38 | 1499.3653 | 7913.2764 | 1514.1833 | 240:40 | 67.9691 | 67.6526 | 7992.4868 | 1270:20 | 65.7478 | 65.405
19 | Indi | 247 | 247 | 1218:43 | 6907:21 | 2956.7944 | 6855:37 | 3242.4451 | 16308.1597 | 3293.225 | 319:59 | 57.6538 | 56.9907 | 16595.966 | 1612:34 | 56.8464 | 56.0849
20 | B.Bagewadi | 129 | 129 | 391:21 | 2810:03 | 1301.6646 | 4454:59 | 1487.2889 | 7487.875 | 1503.5951 | 279:44 | 62.8085 | 62.4007 | 7604.9604 | 1414:53 | 62.0617 | 61.4685
21 | Bagalkot | 180 | 180 | 494:07 | 3936:19 | 1680.5931 | 5580:21 | 1913.1076 | 9517.2785 | 1933.6958 | 257:50 | 65.7149 | 65.346 | 9681.2917 | 1290:50 | 65.442 | 64.8464
22 | Jamkhandi | 202 | 202 | 182:43 | 2938:48 | 2193.4764 | 1566:54 | 2258.7639 | 11976.05 | 2266.3771 | 269:16 | 63.929 | 63.8075 | 12098.5 | 1437:27 | 61.2501 | 60.8539
23 | Mudhol | 190 | 190 | 281:15 | 1799:44 | 2649.0479 | 2220:36 | 2741.5729 | 13070.3715 | 2753.2917 | 347:47 | 53.4538 | 53.2548 | 13145.3604 | 1660:28 | 55.0383 | 54.7803
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of September-2020
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of September-2020 |  |  |  | Reliability for cumulative period from Apr-20 to Sept-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 294:35 | 1329:20 | 3325:45 | 2180:31 | 5506:16 | 1514.6153 | 5800:51 | 128:54 | 83.0053 | 82.0961 | 1570.0042 | 837:20 | 81.6076 | 80.935
2 | Dharwad Rural | 81 | 81 | 185:11 | 1158:18 | 13124:44 | 2481:43 | 15606:27 | 4076.6444 | 15791:38 | 194:58 | 73.24 | 72.9224 | 4124.9069 | 1222:12 | 72.4978 | 72.1723
3 | Gadag | 92 | 92 | 345:05 | 1857:40 | 15308:17 | 3182:54 | 18491:11 | 4566.0174 | 18836:16 | 204:45 | 72.0846 | 71.5636 | 4643.4201 | 1211:20 | 72.8794 | 72.4197
4 | Ron | 53 | 53 | 175:10 | 1177:01 | 6253:05 | 1812:06 | 8065:11 | 2049.341 | 8240:21 | 155:29 | 78.8648 | 78.4058 | 2098.3833 | 950:13 | 78.8706 | 78.365
5 | Haveri | 195 | 195 | 1488:37 | 9279:42 | 2227.3889 | 12128:34 | 2732.7458 | 16485.9708 | 2794.7715 | 343:58 | 53.2864 | 52.2261 | 16872.625 | 2076:38 | 53.8014 | 52.7179
6 | Ranebennur | 182 | 182 | 1021:52 | 5972:11 | 2266.8951 | 9021:28 | 2642.7896 | 15854.4222 | 2685.3674 | 354:07 | 51.5973 | 50.8174 | 16103.2632 | 2123:30 | 52.3977 | 51.6506
7 | Sirsi | 52 | 52 | 199:16 | 3403:08 | 580:23 | 1898:05 | 2478:28 | 19062:12 | 2677:44 | 51:30 | 93.3802 | 92.8479 | 22465:20 | 432:02 | 91.6534 | 90.1634
8 | Dandeli | 20 | 20 | 160:36 | 834:13 | 424:50 | 525:36 | 950:26 | 5926:07 | 1111:02 | 55:33 | 93.3998 | 92.2845 | 6760:20 | 338:01 | 93.2535 | 92.3038
9 | Karwar | 32 | 32 | 388:35 | 2134:12 | 382:03 | 478:39 | 860:42 | 6926:28 | 1249:17 | 39:02 | 96.2643 | 94.5778 | 9060:40 | 283:09 | 95.0717 | 93.5531
10 | Honnavar | 39 | 39 | 338:32 | 2613:41 | 599:21 | 703:47 | 1303:08 | 8577:40 | 1641:40 | 42:06 | 95.3592 | 94.1536 | 11191:21 | 286:57 | 94.9923 | 93.4664
11 | Belagavi | 131 | 131 | 688:00 | 3280:27 | 18766:02 | 2591:29 | 21357:30 | 5618.069 | 22045:30 | 168:17 | 77.3563 | 76.6269 | 5754.7542 | 1054:18 | 76.565 | 75.9949
12 | Bailhongal | 191 | 191 | 1531:02 | 5392:52 | 1560.9542 | 6413:50 | 1828.1972 | 10938.5444 | 1891.9903 | 237:44 | 68.0943 | 66.981 | 11163.2472 | 1402:43 | 68.705 | 68.0621
13 | Ramdurg | 75 | 75 | 400:50 | 2113:09 | 22083:52 | 2575:58 | 1027.4931 | 6395.7965 | 1044.1944 | 334:09 | 54.3336 | 53.5914 | 6483.8444 | 2074:50 | 53.4004 | 52.7589
14 | Ghataprabha | 157 | 157 | 400:05 | 2639:45 | 1344.3083 | 2787:38 | 1460.4597 | 10253.041 | 1477.1299 | 225:48 | 68.9924 | 68.6384 | 10363.0306 | 1584:09 | 64.3137 | 63.9308
15 | Raibag | 166 | 166 | 196:40 | 3066:58 | 1550.8444 | 2009:37 | 1634.5785 | 10262.041 | 1642.7729 | 237:31 | 67.1771 | 67.0126 | 10389.8312 | 1502:09 | 66.2188 | 65.7982
16 | Athani | 183 | 183 | 916:40 | 5150:50 | 1259.509 | 2650:24 | 1369.9424 | 9418.2132 | 1408.1368 | 184:40 | 75.0466 | 74.3509 | 9632.8312 | 1263:19 | 71.8767 | 71.2358
17 | Chikkodi | 184 | 184 | 250:10 | 1643:06 | 1698.2667 | 1877:58 | 1776.5153 | 11293.9278 | 1786.9389 | 233:05 | 67.8168 | 67.6279 | 11362.3903 | 1482:03 | 66.459 | 66.2557
18 | Vijayapur | 151 | 151 | 400:18 | 2301:21 | 1272.9944 | 5742:49 | 1512.2785 | 9425.5549 | 1528.9576 | 243:01 | 66.6164 | 66.2482 | 9521.4444 | 1513:21 | 65.8902 | 65.5432
19 | Indi | 249 | 249 | 1017:16 | 7924:37 | 2881.5764 | 8384:42 | 3230.9389 | 19539.0986 | 3273.325 | 315:30 | 56.7478 | 56.1804 | 19869.291 | 1915:07 | 57.1201 | 56.3954
20 | B.Bagewadi | 129 | 129 | 627:17 | 3437:20 | 1265.1035 | 5621:27 | 1499.3306 | 8987.2056 | 1525.4674 | 283:48 | 61.2576 | 60.5822 | 9130.4278 | 1698:41 | 61.9299 | 61.3232
21 | Bagalkot | 180 | 180 | 775:18 | 4711:37 | 1623.2132 | 6709:56 | 1902.7937 | 11420.0722 | 1935.0979 | 258:01 | 64.7631 | 64.1649 | 11616.3896 | 1548:51 | 65.3307 | 64.7347
22 | Jamkhandi | 202 | 202 | 278:26 | 3217:14 | 2119.8521 | 2376:41 | 2218.8806 | 14194.9306 | 2230.4819 | 265:00 | 63.3848 | 63.1934 | 14328.9819 | 1702:27 | 61.6 | 61.2374
23 | Mudhol | 190 | 190 | 215:43 | 2015:27 | 2454.0868 | 3548:24 | 2601.9368 | 15672.3083 | 2610.925 | 329:48 | 54.352 | 54.1943 | 15756.2854 | 1990:16 | 54.9258 | 54.6843
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of October-2020
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of October-2020 |  |  |  | Reliability for cumulative period from April-20 to October-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 364:25 | 1693:45 | 4564:42 | 1823:11 | 6387:53 | 1780.7771 | 6752:18 | 150:03 | 80.9203 | 79.8318 | 1851.35 | 987:23 | 81.508 | 80.7752
2 | Dharwad Rural | 81 | 81 | 337:00 | 1495:18 | 12613:47 | 2664:18 | 15278:05 | 4713.2312 | 15615:05 | 192:47 | 74.6481 | 74.0889 | 4775.5354 | 1414:58 | 72.8093 | 72.4499
3 | Gadag | 92 | 92 | 104:55 | 1962:35 | 16780:56 | 2864:05 | 19645:01 | 5384.5597 | 19749:56 | 214:40 | 71.2994 | 71.1461 | 5466.334 | 1426:00 | 72.6505 | 72.2352
4 | Ron | 53 | 53 | 219:50 | 1396:51 | 6770:10 | 1359:30 | 8129:40 | 2388.0771 | 8349:30 | 157:32 | 79.3831 | 78.8256 | 2446.2792 | 1107:45 | 78.9448 | 78.4317
5 | Haveri | 195 | 195 | 1729:35 | 11009:17 | 2396.1514 | 11377:47 | 2870.2257 | 19356.1965 | 2942.2917 | 362:08 | 52.519 | 51.3269 | 19814.9167 | 2438:46 | 53.6156 | 52.5164
6 | Ranebennur | 181 | 181 | 935:20 | 6907:31 | 2409.9285 | 6526:50 | 2681.8799 | 18536.3021 | 2720.8521 | 360:47 | 52.2032 | 51.5086 | 18824.1153 | 2496:01 | 52.1446 | 51.4016
7 | Sirsi | 53 | 53 | 478:30 | 3881:38 | 719:53 | 1428:07 | 2148:00 | 21210:12 | 2626:30 | 49:33 | 94.5526 | 93.3392 | 1045.4931 | 473:26 | 92.2081 | 90.7821
8 | Dandeli | 21 | 21 | 161:31 | 995:44 | 232:41 | 408:49 | 641:30 | 6567:37 | 803:01 | 38:14 | 95.8941 | 94.8604 | 7563:21 | 360:10 | 93.9108 | 92.9875
9 | Karwar | 32 | 32 | 314:41 | 2448:53 | 322:20 | 306:29 | 628:49 | 7555:17 | 943:30 | 29:29 | 97.3588 | 96.037 | 10004:10 | 312:38 | 95.403 | 93.913
10 | Honnavar | 39 | 39 | 391:13 | 3004:54 | 380:13 | 361:44 | 741:57 | 9319:37 | 1133:10 | 29:03 | 97.443 | 96.0947 | 12324:31 | 316:01 | 95.3473 | 93.8471
11 | Belagavi | 131 | 131 | 376:45 | 3657:12 | 19825:58 | 2121:14 | 21947:12 | 6532.5356 | 22323:57 | 170:25 | 77.4817 | 77.0952 | 6684.9188 | 1224:43 | 76.6978 | 76.1542
12 | Bailhongal | 191 | 191 | 2061:25 | 7454:17 | 1870.0326 | 5845:47 | 2113.6069 | 13052.1514 | 2199.4993 | 276:23 | 64.3032 | 62.8526 | 13362.7465 | 1679:05 | 68.0673 | 67.3075
13 | Ramdurg | 75 | 75 | 941:03 | 3054:12 | 22674:31 | 2726:09 | 1058.3611 | 7454.1576 | 1097.5715 | 351:13 | 54.4791 | 52.7926 | 7581.416 | 2426:03 | 53.5567 | 52.7638
14 | Ghataprabha | 157 | 157 | 581:37 | 3221:22 | 1348.5028 | 3387:34 | 1489.6514 | 11742.6924 | 1513.8854 | 231:25 | 69.3928 | 68.8949 | 11876.916 | 1815:35 | 65.0494 | 64.6499
15 | Raibag | 166 | 166 | 878:42 | 3945:40 | 1598.2021 | 2527:38 | 1703.5201 | 11965.5611 | 1740.1326 | 251:35 | 66.8962 | 66.1848 | 12129.9639 | 1753:44 | 66.317 | 65.8542
16 | Athani | 183 | 183 | 502:50 | 5653:40 | 1309.8937 | 2536:59 | 1415.6014 | 10833.8146 | 1436.5528 | 188:24 | 75.0467 | 74.6774 | 11069.384 | 1451:43 | 72.3359 | 71.7344
17 | Chikkodi | 184 | 184 | 363:00 | 2006:06 | 1806.3208 | 2601:29 | 1914.716 | 13208.6438 | 1929.841 | 251:43 | 66.432 | 66.1669 | 13292.2313 | 1733:46 | 66.4551 | 66.2428
18 | Vijayapur | 152 | 152 | 762:12 | 3063:33 | 1344.7715 | 6450:58 | 1613.5618 | 11039.1167 | 1645.3201 | 259:47 | 65.7563 | 65.0823 | 11166.7646 | 1763:10 | 66.0627 | 65.6703
19 | Indi | 249 | 249 | 1277:27 | 9202:04 | 2789.2778 | 8745:00 | 3153.6528 | 22692.7514 | 3206.8799 | 309:06 | 59.1443 | 58.4547 | 23076.1708 | 2224:13 | 57.4133 | 56.6937
20 | B.Bagewadi | 130 | 130 | 608:39 | 4045:59 | 1296.8063 | 5881:08 | 1541.8535 | 10529.059 | 1567.2139 | 289:20 | 61.7406 | 61.1113 | 10697.6417 | 1974:57 | 62.1529 | 61.5469
21 | Bagalkot | 181 | 181 | 352:20 | 5063:57 | 1645.041 | 6610:17 | 1920.4694 | 13340.5417 | 1935.15 | 256:36 | 65.7731 | 65.5115 | 13551.5396 | 1796:53 | 65.5586 | 65.0138
22 | Jamkhandi | 202 | 202 | 544:37 | 3761:51 | 2158.0535 | 2653:17 | 2268.6069 | 16463.5375 | 2291.2993 | 272:14 | 63.7718 | 63.4095 | 16620.2812 | 1974:41 | 61.9146 | 61.552
23 | Mudhol | 192 | 192 | 2129:13 | 4144:40 | 2535.3174 | 3740:55 | 2691.1889 | 18363.4972 | 2779.9063 | 347:29 | 54.7851 | 53.2946 | 18536.1917 | 2317:01 | 55.3069 | 54.8866
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of November-2020
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of November-2020 |  |  |  | Reliability for cumulative period from April-20 to November-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 195:25 | 1889:10 | 5145:03 | 724:15 | 5869:18 | 2025.3313 | 6064:43 | 134:46 | 81.8849 | 81.2817 | 2104.0465 | 1122:09 | 81.5544 | 80.8375
2 | Dharwad Rural | 81 | 81 | 141:35 | 1636:53 | 13139:07 | 1351:13 | 14490:20 | 5316.9951 | 14631:55 | 180:38 | 75.1537 | 74.911 | 5385.1986 | 1595:37 | 73.0976 | 72.7525
3 | Gadag | 92 | 92 | 147:00 | 2109:35 | 15623:51 | 1199:15 | 16823:06 | 6085.5222 | 16970:06 | 184:27 | 74.6028 | 74.3809 | 6173.4215 | 1610:27 | 72.8906 | 72.499
4 | Ron | 53 | 53 | 200:05 | 1596:56 | 6254:25 | 704:10 | 6958:35 | 2678.0181 | 7158:40 | 135:04 | 81.7647 | 81.2404 | 2744.5569 | 1242:49 | 79.2915 | 78.777
5 | Haveri | 195 | 195 | 1263:40 | 12272:57 | 2534.0501 | 3430:03 | 2676.9689 | 22033.1654 | 2729.6216 | 335:57 | 54.2398 | 53.3398 | 22544.5383 | 2774:43 | 53.6924 | 52.6176
6 | Ranebennur | 182 | 182 | 768:53 | 7676:24 | 2411.5486 | 2513:32 | 2516.2792 | 21052.5813 | 2548.316 | 336:02 | 53.9143 | 53.3275 | 21372.4313 | 2818:21 | 52.5928 | 51.8726
7 | Sirsi | 53 | 53 | 186:03 | 4067:41 | 554:16 | 882:41 | 1436:57 | 22647:09 | 1623:00 | 30:37 | 96.2344 | 95.7469 | 1113.1181 | 504:03 | 92.7031 | 91.3925
8 | Dandeli | 21 | 21 | 58:04 | 1053:48 | 208:31 | 179:30 | 388:01 | 6955:38 | 446:05 | 21:15 | 97.4338 | 97.0497 | 8009:26 | 381:24 | 94.3439 | 93.487
9 | Karwar | 32 | 32 | 581:37 | 3030:30 | 285:06 | 309:33 | 594:39 | 8149:56 | 1176:16 | 36:45 | 97.4191 | 94.8947 | 11180:26 | 349:23 | 95.6509 | 94.0337
10 | Honnavar | 39 | 39 | 340:09 | 3345:03 | 399:02 | 288:50 | 687:52 | 10007:29 | 1028:01 | 26:22 | 97.5503 | 96.339 | 13352:32 | 342:22 | 95.6181 | 94.1535
11 | Belagavi | 133 | 133 | 210:16 | 3867:28 | 18894:32 | 1243:13 | 20137:45 | 7371.6086 | 20348:01 | 153:00 | 78.9706 | 78.751 | 7532.7528 | 1359:18 | 77.2846 | 76.788
12 | Bailhongal | 191 | 191 | 383:18 | 7837:35 | 1631.2528 | 2804:39 | 1748.1132 | 14800.2646 | 1764.084 | 221:40 | 69.4919 | 69.2132 | 15126.8306 | 1900:45 | 68.2425 | 67.5418
13 | Ramdurg | 75 | 75 | 251:40 | 3305:52 | 23127:50 | 702:30 | 23830:20 | 8447.0882 | 1003.4167 | 321:06 | 55.8698 | 55.4037 | 8584.8326 | 2747:09 | 53.841 | 53.0883
14 | Ghataprabha | 156 | 156 | 284:53 | 3506:15 | 1482.3917 | 1003:10 | 1524.1903 | 13266.8826 | 1536.0604 | 236:19 | 67.4318 | 67.1782 | 13412.9764 | 2063:32 | 65.1459 | 64.762
15 | Raibag | 168 | 168 | 304:11 | 4249:51 | 1534.4806 | 1019:00 | 1576.9389 | 13542.5 | 1589.6132 | 227:05 | 68.7115 | 68.4601 | 13719.5771 | 1959:56 | 66.9631 | 66.5311
16 | Athani | 183 | 183 | 582:07 | 6235:47 | 1323.6375 | 1461:03 | 1384.5146 | 12218.3292 | 1408.7694 | 184:45 | 74.7812 | 74.3394 | 12478.1535 | 1636:29 | 72.6365 | 72.0547
17 | Chikkodi | 185 | 185 | 131:25 | 2137:31 | 1746.1111 | 946:44 | 1785.5583 | 14994.2021 | 1791.034 | 232:21 | 67.8278 | 67.7291 | 15083.2653 | 1956:45 | 66.7829 | 66.5856
18 | Vijayapur | 152 | 152 | 87:10 | 3150:43 | 1320.2104 | 2736:01 | 1434.2111 | 12473.3278 | 1437.8431 | 227:02 | 68.548 | 68.4684 | 12604.6076 | 1990:12 | 66.3683 | 66.0143
19 | Indi | 249 | 249 | 520:36 | 9722:40 | 2878.0847 | 2941:32 | 3000.6486 | 25693.4 | 3022.3403 | 291:19 | 59.8307 | 59.5403 | 26098.5111 | 2515:31 | 57.7105 | 57.0437
20 | B.Bagewadi | 130 | 130 | 234:20 | 4280:19 | 1319.0285 | 1827:48 | 1395.1868 | 11924.2458 | 1404.9507 | 259:23 | 64.226 | 63.9756 | 12102.5924 | 2234:19 | 62.4078 | 61.8455
21 | Bagalkot | 181 | 181 | 428:09 | 5492:06 | 1699.0139 | 3398:38 | 1840.6236 | 15181.1653 | 1858.4632 | 246:26 | 66.1027 | 65.7742 | 15410.0028 | 2043:19 | 65.6255 | 65.1073
22 | Jamkhandi | 205 | 205 | 212:58 | 3974:49 | 2166.8056 | 1004:04 | 2208.6417 | 18672.1792 | 2217.5153 | 259:37 | 64.0871 | 63.9428 | 18837.7965 | 2205:24 | 62.6706 | 62.3395
23 | Mudhol | 192 | 192 | 162:45 | 4307:25 | 2539.5299 | 1311:00 | 2594.1549 | 20957.6521 | 2600.9361 | 325:07 | 54.9626 | 54.8449 | 21137.1278 | 2642:08 | 55.2646 | 54.8815
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of December-2020
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of December-2020 |  |  |  | Reliability for cumulative period from April-20 to December-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 89:05 | 1978:15 | 5381:28 | 456:13 | 5837:41 | 2268.5681 | 5926:46 | 131:42 | 82.5637 | 82.2976 | 2350.9951 | 1253:52 | 81.6681 | 81.0021
2 | Dharwad Rural | 82 | 82 | 209:00 | 1845:53 | 14652:55 | 861:21 | 15514:16 | 5963.4229 | 15723:16 | 191:45 | 74.5701 | 74.2275 | 6040.3347 | 1767:54 | 73.5547 | 73.2136
3 | Gadag | 93 | 93 | 37:32 | 2147:07 | 16770:55 | 1857:58 | 18628:53 | 6861.7257 | 18666:25 | 200:43 | 73.0765 | 73.0223 | 6951.1889 | 1793:51 | 73.1702 | 72.8204
4 | Ron | 53 | 53 | 80:00 | 1676:56 | 6363:35 | 246:35 | 6610:10 | 2953.4417 | 6690:10 | 126:14 | 83.2365 | 83.0337 | 3023.3139 | 1369:03 | 79.7362 | 79.2569
5 | Haveri | 196 | 196 | 498:31 | 12771:28 | 2647.491 | 2073:04 | 2733.8688 | 24767.0341 | 2754.6403 | 337:18 | 55.0055 | 54.6636 | 25299.1786 | 3097:52 | 54.05 | 53.0627
6 | Ranebennur | 182 | 182 | 672:50 | 8349:14 | 2563.8799 | 2244:51 | 2657.4153 | 23709.9965 | 2685.45 | 354:08 | 52.8994 | 52.4025 | 24057.8813 | 3172:28 | 52.6274 | 51.9323
7 | Sirsi | 53 | 53 | 131:13 | 4198:54 | 465:20 | 672:45 | 1138:05 | 23785:14 | 1269:18 | 23:57 | 97.1138 | 96.781 | 1166.0056 | 528:00 | 93.2003 | 92
8 | Dandeli | 21 | 21 | 33:10 | 1086:58 | 163:08 | 233:44 | 396:52 | 7352:30 | 430:02 | 20:29 | 97.4599 | 97.2476 | 8439:28 | 401:53 | 94.6952 | 93.9109
9 | Karwar | 32 | 32 | 265:41 | 3296:11 | 283:09 | 259:24 | 542:33 | 8692:29 | 808:14 | 25:15 | 97.7211 | 96.6052 | 11988:40 | 374:39 | 95.8842 | 94.3235
10 | Honnavar | 39 | 39 | 238:06 | 3583:09 | 354:47 | 270:00 | 624:47 | 10632:16 | 862:53 | 22:08 | 97.8468 | 97.0262 | 14215:25 | 364:30 | 95.8694 | 94.4773
11 | Belagavi | 135 | 135 | 182:14 | 4049:42 | 19662:01 | 1058:44 | 20720:45 | 8234.9731 | 20902:59 | 154:50 | 79.37 | 79.1886 | 8403.7104 | 1494:00 | 77.8183 | 77.3637
12 | Bailhongal | 190 | 190 | 474:17 | 8311:52 | 1678.1111 | 1252:17 | 1730.2896 | 16530.5542 | 1750.0514 | 221:04 | 70.6233 | 70.2878 | 16876.8819 | 2131:49 | 68.3626 | 67.6997
13 | Ramdurg | 75 | 75 | 75:30 | 3381:22 | 1013.4451 | 366:50 | 1028.7299 | 9475.8181 | 1031.8757 | 330:12 | 55.7536 | 55.6182 | 9616.7083 | 3077:21 | 54.0566 | 53.3735
14 | Ghataprabha | 156 | 156 | 296:34 | 3802:49 | 1534.3576 | 651:25 | 1561.5 | 14828.3826 | 1573.8569 | 242:08 | 67.7109 | 67.4554 | 14986.8333 | 2305:40 | 65.435 | 65.0657
15 | Raibag | 168 | 168 | 163:50 | 4413:41 | 1542.55 | 488:12 | 1562.8917 | 15105.3917 | 1569.7181 | 224:15 | 69.9906 | 69.8595 | 15289.2951 | 2184:11 | 67.3043 | 66.9063
16 | Athani | 185 | 185 | 556:46 | 6792:33 | 1371.259 | 523:11 | 1393.0583 | 13611.3875 | 1416.2569 | 183:44 | 75.7095 | 75.305 | 13894.4104 | 1802:31 | 73.2454 | 72.6891
17 | Chikkodi | 185 | 185 | 263:35 | 2401:06 | 1853.6194 | 528:17 | 1875.6313 | 16869.8333 | 1886.6139 | 244:45 | 67.295 | 67.1035 | 16969.8792 | 2201:30 | 66.8406 | 66.644
18 | Vijayapur | 153 | 153 | 457:01 | 3607:44 | 1513.4931 | 799:34 | 1546.8083 | 14020.1361 | 1565.8507 | 245:37 | 67.3876 | 66.9861 | 14170.4583 | 2222:49 | 66.6782 | 66.321
19 | Indi | 250 | 250 | 363:37 | 10086:17 | 3003.984 | 1659:55 | 3073.1472 | 28766.5472 | 3088.2979 | 296:29 | 60.3465 | 60.151 | 29186.809 | 2801:56 | 58.1577 | 57.5465
20 | B.Bagewadi | 134 | 134 | 292:45 | 4573:04 | 1396.6792 | 921:39 | 1435.0812 | 13359.3271 | 1447.2792 | 259:13 | 65.453 | 65.1594 | 13549.8715 | 2426:51 | 63.7467 | 63.2297
21 | Bagalkot | 181 | 181 | 454:12 | 5946:18 | 1763.316 | 1564:55 | 1828.5208 | 17009.6861 | 1847.4458 | 244:58 | 67.4119 | 67.0746 | 17257.4486 | 2288:17 | 65.8268 | 65.3291
22 | Jamkhandi | 205 | 205 | 197:25 | 4172:14 | 2209.684 | 642:58 | 2236.4743 | 20908.6535 | 2244.7 | 262:48 | 64.8076 | 64.6782 | 21082.4965 | 2468:12 | 62.9115 | 62.6031
23 | Mudhol | 192 | 192 | 140:35 | 4448:00 | 2601.7819 | 646:08 | 2628.7042 | 23586.3562 | 2634.5618 | 329:19 | 55.8349 | 55.7365 | 23771.6896 | 2971:28 | 55.3289 | 54.9779
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of January-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of January-2021 |  |  |  | Reliability for cumulative period from April-20 to January-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 284:25 | 2262:40 | 5691:04 | 535:57 | 6227:01 | 2528.0271 | 6511:26 | 144:42 | 81.4008 | 80.5513 | 2622.3049 | 1398:34 | 81.6411 | 80.9564
2 | Dharwad Rural | 82 | 82 | 191:48 | 2037:41 | 14392:05 | 1933:59 | 16326:04 | 6643.6757 | 16517:52 | 201:26 | 73.2395 | 72.9251 | 6728.5792 | 1969:20 | 73.5227 | 73.1844
3 | Gadag | 93 | 93 | 83:55 | 2231:02 | 12879:37 | 1603:29 | 14483:06 | 7465.1882 | 14567:01 | 156:38 | 79.0682 | 78.947 | 7558.1479 | 1950:29 | 73.7677 | 73.441
4 | Ron | 53 | 53 | 99:10 | 1776:06 | 6290:10 | 505:45 | 6795:55 | 3236.6049 | 6895:05 | 130:06 | 82.7655 | 82.514 | 3310.609 | 1499:09 | 80.0431 | 79.5868
5 | Haveri | 196 | 196 | 986:20 | 13757:48 | 2580.3792 | 4161:16 | 2753.7653 | 27520.7994 | 2794.8625 | 342:14 | 54.678 | 54.0016 | 28094.0411 | 3440:05 | 54.1136 | 53.1579
6 | Ranebennur | 182 | 182 | 754:20 | 9103:34 | 2471.5576 | 3499:19 | 2617.3625 | 26327.359 | 2648.7931 | 349:17 | 53.6093 | 53.0522 | 26706.6743 | 3521:46 | 52.7269 | 52.0458
7 | Sirsi | 53 | 53 | 103:46 | 4302:40 | 429:43 | 1258:15 | 1687:58 | 1061.3833 | 1791:44 | 33:48 | 95.7193 | 95.4561 | 1240.6611 | 561:49 | 93.4555 | 92.3501
8 | Dandeli | 21 | 21 | 84:31 | 1171:29 | 270:16 | 231:02 | 501:18 | 7853:48 | 585:49 | 27:54 | 96.7915 | 96.2505 | 9025:17 | 429:47 | 94.9075 | 94.1479
9 | Karwar | 33 | 33 | 150:22 | 3446:33 | 358:46 | 359:58 | 718:44 | 9411:13 | 869:06 | 26:20 | 97.0726 | 96.4602 | 12857:46 | 389:38 | 96.1167 | 94.6946
10 | Honnavar | 40 | 40 | 375:00 | 3958:09 | 333:28 | 376:54 | 710:22 | 11342:38 | 1085:22 | 27:08 | 97.613 | 96.3529 | 15300:47 | 382:31 | 96.1388 | 94.7914
11 | Belagavi | 135 | 135 | 416:11 | 4465:53 | 19606:06 | 1214:32 | 20820:38 | 9102.4995 | 21236:49 | 157:19 | 79.2706 | 78.8562 | 9288.5778 | 1651:18 | 77.9654 | 77.5149
12 | Bailhongal | 190 | 190 | 891:29 | 9203:21 | 1649.2861 | 2937:42 | 1771.6903 | 18302.2444 | 1808.8354 | 228:29 | 69.9204 | 69.2897 | 18685.7174 | 2360:18 | 68.5204 | 67.8608
13 | Ramdurg | 76 | 76 | 299:56 | 3681:18 | 23280:47 | 1298:32 | 1024.1382 | 10499.9562 | 1036.6354 | 327:22 | 56.5306 | 56.0002 | 10653.3438 | 3364:13 | 54.8505 | 54.191
14 | Ghataprabha | 157 | 157 | 58:25 | 3861:14 | 1546.084 | 943:03 | 1585.3778 | 16413.7604 | 1587.8118 | 242:43 | 67.426 | 67.376 | 16574.6451 | 2533:42 | 65.8346 | 65.4997
15 | Raibag | 169 | 169 | 254:11 | 4667:52 | 1566.5326 | 922:33 | 1604.9722 | 16710.3639 | 1615.5632 | 229:26 | 69.3649 | 69.1628 | 16904.8583 | 2400:41 | 67.687 | 67.3109
16 | Athani | 185 | 185 | 325:11 | 7117:44 | 1337.6069 | 506:17 | 1358.7021 | 14970.0896 | 1372.2514 | 178:01 | 76.3086 | 76.0723 | 15266.6618 | 1980:32 | 73.5558 | 73.0319
17 | Chikkodi | 186 | 186 | 165:45 | 2566:51 | 1899.816 | 1187:24 | 1949.291 | 18819.1243 | 1956.1972 | 252:25 | 66.1934 | 66.0736 | 18926.0764 | 2442:04 | 66.9353 | 66.7474
18 | Vijayapur | 153 | 153 | 289:03 | 3896:47 | 1545.9611 | 1317:13 | 1600.8451 | 15620.9812 | 1612.8889 | 253:00 | 66.2483 | 65.9943 | 15783.3472 | 2475:49 | 66.6347 | 66.2879
19 | Indi | 248 | 248 | 303:37 | 10389:54 | 2984.7556 | 1416:48 | 3043.7889 | 31810.3361 | 3056.4396 | 295:47 | 60.4086 | 60.244 | 32243.2486 | 3120:19 | 58.0825 | 57.5121
20 | B.Bagewadi | 135 | 135 | 112:56 | 4686:00 | 1475.0493 | 1022:35 | 1517.6569 | 14876.984 | 1522.3625 | 270:39 | 63.7358 | 63.6234 | 15072.234 | 2679:30 | 63.987 | 63.5143
21 | Bagalkot | 180 | 180 | 362:51 | 6309:09 | 1806.1951 | 1980:00 | 1888.6951 | 18898.3812 | 1903.8139 | 253:51 | 66.1524 | 65.8815 | 19161.2625 | 2554:50 | 65.6892 | 65.2119
22 | Jamkhandi | 205 | 205 | 605:47 | 4778:01 | 2227.2583 | 865:22 | 2263.3153 | 23171.9687 | 2288.5562 | 267:56 | 64.3853 | 63.9881 | 23371.0528 | 2736:07 | 63.0608 | 62.7434
23 | Mudhol | 192 | 192 | 233:35 | 4681:35 | 2618.6 | 1124:27 | 2665.4521 | 26251.8083 | 2675.1847 | 334:24 | 55.2175 | 55.054 | 26446.8743 | 3305:52 | 55.3176 | 54.9856
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of FEBRUARY-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of February-2021 |  |  |  | Reliability for cumulative period from April-20 to February-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 285:55 | 2548:35 | 5485:24 | 746:57 | 6232:21 | 2787.7083 | 6518:16 | 144:51 | 79.3904 | 78.4449 | 2893.8993 | 1543:25 | 81.4524 | 80.7458
2 | Dharwad Rural | 82 | 82 | 146:04 | 2183:45 | 12933:27 | 1181:10 | 14114:37 | 7231.7847 | 14260:41 | 173:55 | 74.3855 | 74.1204 | 7322.7743 | 2143:15 | 73.5951 | 73.2628
3 | Gadag | 93 | 93 | 149:15 | 2380:17 | 13518:27 | 884:55 | 14403:22 | 8065.3285 | 14552:37 | 156:29 | 76.9531 | 76.7143 | 8164.5069 | 2106:58 | 74.0347 | 73.7154
4 | Ron | 53 | 53 | 130:25 | 1906:31 | 5777:25 | 335:45 | 6113:10 | 3491.3201 | 6243:35 | 117:48 | 82.8359 | 82.4697 | 3570.7583 | 1616:57 | 80.2773 | 79.8285
5 | Haveri | 196 | 196 | 1581:47 | 15339:35 | 2370.7576 | 3411:52 | 2512.9187 | 30033.7182 | 2578.8264 | 315:46 | 54.2107 | 53.0097 | 30672.8675 | 3755:52 | 54.1218 | 53.1454
6 | Ranebennur | 182 | 182 | 726:42 | 9830:16 | 2246.034 | 3128:28 | 2376.3868 | 28703.7458 | 2406.666 | 317:22 | 53.3676 | 52.7734 | 29113.3403 | 3839:07 | 52.7806 | 52.1068
7 | Sirsi | 53 | 53 | 358:31 | 4661:11 | 439:11 | 1099:19 | 1538:30 | 1125.4875 | 1897:01 | 35:48 | 95.6803 | 94.6737 | 1319.7035 | 597:36 | 93.642 | 92.5449
8 | Dandeli | 21 | 21 | 47:18 | 1218:47 | 332:00 | 212:17 | 544:17 | 8398:05 | 591:35 | 28:10 | 96.1431 | 95.8079 | 9616:52 | 457:57 | 95.0111 | 94.2871
9 | Karwar | 33 | 33 | 205:48 | 3652:21 | 255:49 | 288:18 | 544:07 | 9955:20 | 749:55 | 22:43 | 97.5464 | 96.6183 | 13607:41 | 412:21 | 96.2366 | 94.8559
10 | Honnavar | 40 | 40 | 220:52 | 4179:01 | 326:36 | 245:05 | 571:41 | 11914:19 | 792:33 | 19:49 | 97.8732 | 97.0515 | 16093:20 | 402:20 | 96.2842 | 94.9809
11 | Belagavi | 135 | 135 | 342:59 | 4808:52 | 18615:37 | 970:57 | 19586:34 | 9918.6065 | 19929:33 | 147:38 | 78.4099 | 78.0318 | 10118.9757 | 1798:56 | 78.0026 | 77.5583
12 | Bailhongal | 190 | 190 | 913:31 | 10116:52 | 1512.2576 | 1562:22 | 1577.3562 | 19879.6007 | 1615.4194 | 204:03 | 70.3504 | 69.635 | 20301.1368 | 2564:21 | 68.6738 | 68.0096
13 | Ramdurg | 76 | 76 | 194:18 | 3875:36 | 21864:39 | 899:24 | 22764:03 | 11448.4583 | 22958:21 | 302:05 | 55.4275 | 55.0471 | 11609.9417 | 3666:18 | 54.8989 | 54.2628
14 | Ghataprabha | 158 | 158 | 269:15 | 4130:29 | 1412.8722 | 809:16 | 1446.5917 | 17860.3521 | 1457.8104 | 221:26 | 67.3013 | 67.0477 | 18032.4556 | 2739:06 | 66.1556 | 65.8295
15 | Raibag | 169 | 169 | 571:33 | 5239:25 | 1415.3521 | 671:04 | 1443.3132 | 18153.6771 | 1467.1278 | 208:21 | 69.4989 | 68.9956 | 18371.9861 | 2609:02 | 67.8389 | 67.4521
16 | Athani | 185 | 185 | 381:05 | 7498:49 | 1279.8118 | 584:27 | 1304.1639 | 16274.2535 | 1320.0424 | 171:15 | 74.8231 | 74.5166 | 16586.7042 | 2151:47 | 73.662 | 73.1563
17 | Chikkodi | 186 | 186 | 183:30 | 2750:21 | 1725.8889 | 602:21 | 1750.9868 | 20570.1111 | 1758.6326 | 226:55 | 66.3789 | 66.2321 | 20684.709 | 2669:00 | 66.8886 | 66.7042
18 | Vijayapur | 153 | 153 | 470:31 | 4367:18 | 1404.1403 | 670:20 | 1432.0708 | 17053.0521 | 1451.6757 | 227:43 | 66.5716 | 66.114 | 17235.0229 | 2703:32 | 66.6294 | 66.2733
19 | Indi | 249 | 249 | 375:22 | 10765:16 | 2644.5063 | 1386:34 | 2702.2799 | 34512.616 | 2717.9201 | 261:58 | 61.241 | 61.0166 | 34961.1687 | 3369:45 | 58.5015 | 57.9622
20 | B.Bagewadi | 135 | 135 | 453:43 | 5139:43 | 1344.0104 | 924:40 | 1382.5382 | 16259.5222 | 1401.4431 | 249:09 | 63.4249 | 62.9248 | 16473.6771 | 2928:39 | 63.9398 | 63.4649
21 | Bagalkot | 181 | 181 | 411:51 | 6721:00 | 1590.9326 | 1353:26 | 1647.3257 | 20545.7069 | 1664.4861 | 220:42 | 67.4955 | 67.1569 | 20825.7486 | 2761:26 | 66.0143 | 65.5511
22 | Jamkhandi | 206 | 206 | 154:28 | 4932:29 | 2047.4312 | 767:07 | 2079.3944 | 25251.3632 | 2085.8306 | 243:01 | 63.9495 | 63.8379 | 25456.8833 | 2965:51 | 63.2996 | 63.0009
23 | Mudhol | 192 | 192 | 184:37 | 4866:12 | 2386.8681 | 599:59 | 2411.8674 | 28663.6757 | 2419.5597 | 302:27 | 55.1364 | 54.9933 | 28866.434 | 3608:18 | 55.3024 | 54.9862
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of MARCH-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the month of March-2021 |  |  |  | Reliability for cumulative period from April-20 to March-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 288:50 | 2837:25 | 6147:09 | 558:57 | 6706:06 | 3067.1292 | 6994:56 | 155:27 | 79.9698 | 79.1071 | 3185.3549 | 1698:51 | 81.3265 | 80.6067
2 | Dharwad Rural | 82 | 82 | 347:05 | 2530:50 | 15724:36 | 951:13 | 16675:49 | 7926.6104 | 17022:54 | 207:36 | 72.6662 | 72.0973 | 8032.0618 | 2350:51 | 73.5162 | 73.1638
3 | Gadag | 94 | 94 | 163:15 | 2543:32 | 16686:22 | 853:44 | 17540:06 | 8796.166 | 17703:21 | 188:20 | 74.9198 | 74.6864 | 8902.1465 | 2272:53 | 74.3627 | 74.0538
4 | Ron | 53 | 53 | 316:45 | 2223:16 | 12527:46 | 1017:46 | 13545:32 | 4055.7174 | 13862:17 | 261:33 | 65.6484 | 64.8451 | 4148.3535 | 1878:30 | 79.0348 | 78.5559
5 | Haveri | 197 | 197 | 1726:45 | 17066:20 | 2642.8542 | 2763:02 | 2757.9806 | 32791.6987 | 2829.9285 | 344:46 | 54.839 | 53.6609 | 33502.7959 | 4081:34 | 54.3958 | 53.4069
6 | Ranebennur | 182 | 182 | 1101:38 | 10931:54 | 2524.7153 | 2593:21 | 2632.7715 | 31336.5174 | 2678.6729 | 353:14 | 53.3362 | 52.5226 | 31792.0132 | 4192:21 | 52.8278 | 52.1421
7 | Sirsi | 54 | 54 | 336:03 | 4997:14 | 635:33 | 1077:41 | 1713:14 | 1196.8722 | 2049:17 | 37:57 | 95.7357 | 94.8992 | 1405.0903 | 624:29 | 93.9276 | 92.8712
8 | Dandeli | 22 | 22 | 46:22 | 1265:09 | 367:48 | 274:28 | 642:16 | 9040:21 | 688:38 | 31:18 | 96.0761 | 95.7928 | 10305:30 | 468:26 | 95.3091 | 94.6526
9 | Karwar | 33 | 33 | 577:44 | 4230:05 | 329:21 | 195:43 | 525:04 | 10480:24 | 1102:48 | 33:25 | 97.8614 | 95.5083 | 14710:29 | 445:46 | 96.3746 | 94.9113
10 | Honnavar | 40 | 40 | 485:13 | 4664:14 | 466:01 | 216:04 | 682:05 | 12596:24 | 1167:18 | 29:11 | 97.7081 | 96.0776 | 17260:38 | 431:31 | 96.4051 | 95.074
11 | Belagavi | 135 | 135 | 355:48 | 5164:40 | 22586:19 | 1032:58 | 23619:17 | 10902.7433 | 23975:05 | 177:36 | 76.4842 | 76.1299 | 11117.9375 | 1976:31 | 77.8737 | 77.437
12 | Bailhongal | 191 | 191 | 1804:51 | 11921:43 | 1799.8681 | 1518:46 | 1863.15 | 21742.7507 | 1938.3521 | 243:34 | 68.5332 | 67.2631 | 22239.4889 | 2794:29 | 68.8119 | 68.0994
13 | Ramdurg | 76 | 76 | 319:05 | 4194:41 | 1024.4097 | 835:45 | 1059.2326 | 12507.691 | 1072.5278 | 338:42 | 55.0411 | 54.4767 | 12682.4694 | 4004:59 | 54.911 | 54.2809
14 | Ghataprabha | 159 | 159 | 178:05 | 4308:34 | 1634.8792 | 638:35 | 1661.4868 | 19521.8389 | 1668.9069 | 251:55 | 66.2916 | 66.1411 | 19701.3625 | 2973:47 | 66.362 | 66.0526
15 | Raibag | 169 | 169 | 447:50 | 5687:15 | 1735.2646 | 890:37 | 1772.3736 | 19926.0507 | 1791.0333 | 254:21 | 66.1696 | 65.8135 | 20163.0194 | 2863:23 | 67.6971 | 67.3129
16 | Athani | 197 | 197 | 750:04 | 8248:53 | 1472.0889 | 589:12 | 1496.6389 | 17770.8924 | 1527.8917 | 186:08 | 75.4931 | 74.9813 | 18114.5958 | 2206:51 | 75.2856 | 74.8076
17 | Chikkodi | 186 | 186 | 428:20 | 3178:41 | 2088.3563 | 1201:07 | 2138.4028 | 22708.5139 | 2156.25 | 278:14 | 62.9136 | 62.6041 | 22840.959 | 2947:13 | 66.551 | 66.3559
18 | Vijayapur | 158 | 158 | 1226:24 | 5593:42 | 1799.2451 | 1103:50 | 1845.2382 | 18898.2903 | 1896.3382 | 288:03 | 62.3267 | 61.2834 | 19131.3611 | 2906:02 | 67.2303 | 66.8261
19 | Indi | 249 | 249 | 1473:24 | 12238:40 | 3076.8903 | 1409:47 | 3135.6313 | 37648.2472 | 3197.0229 | 308:09 | 59.3778 | 58.5824 | 38158.1917 | 3677:54 | 58.576 | 58.0149
20 | B.Bagewadi | 138 | 138 | 1732:14 | 6871:57 | 1523.2375 | 1020:27 | 1565.7563 | 17825.2785 | 1637.9326 | 284:51 | 63.3998 | 61.7127 | 18111.6097 | 3149:51 | 64.6113 | 64.0429
21 | Bagalkot | 181 | 181 | 851:59 | 7572:59 | 1897.2764 | 1469:28 | 1958.5042 | 22504.2111 | 1994.0035 | 264:24 | 65.0953 | 64.4626 | 22819.7521 | 3025:49 | 65.9363 | 65.4586
22 | Jamkhandi | 206 | 206 | 217:51 | 5150:20 | 2546.4083 | 689:23 | 2575.1326 | 27826.4958 | 2584.2097 | 301:04 | 59.6753 | 59.5332 | 28041.0931 | 3266:55 | 62.9918 | 62.7064
23 | Mudhol | 192 | 192 | 216:26 | 5082:38 | 2703.5715 | 985:06 | 2744.6174 | 31408.2931 | 2753.6354 | 344:12 | 53.8875 | 53.736 | 31620.0694 | 3952:31 | 55.1822 | 54.88
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]

## RURAL(Excl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2020 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of April-2020 |  |  |  | Reliability for cumulative period from Apr-20 to Apr-20
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 151:31 | 151:31 | 873:30 | 964:32 | 1838:02 | 1838:02 | 1989:33 | 45:13 | 94.1981 | 93.7199 | 1989:33 | 45:13 | 94.1981 | 93.7199
2 | Dharwad Rural | 80 | 80 | 297:31 | 297:31 | 1746:17 | 4214:55 | 5961:12 | 5961:12 | 6258:43 | 78:14 | 89.6507 | 89.1342 | 6258:43 | 78:14 | 89.6507 | 89.1342
3 | Gadag | 84 | 84 | 352:35 | 352:35 | 1474:59 | 2025:10 | 3500:09 | 3500:09 | 3852:44 | 45:52 | 94.2127 | 93.6297 | 3852:44 | 45:52 | 94.2127 | 93.6297
4 | Ron | 53 | 53 | 118:35 | 118:35 | 781:15 | 1632:40 | 2413:55 | 2413:55 | 2532:30 | 47:47 | 93.6742 | 93.3635 | 2532:30 | 47:47 | 93.6742 | 93.3635
5 | Haveri | 193 | 193 | 1518:18 | 1518:18 | 2612:36 | 3519:51 | 6132:27 | 6132:27 | 7650:45 | 39:38 | 95.5869 | 94.4943 | 7650:45 | 39:38 | 95.5869 | 94.4943
6 | Ranebennur | 177 | 177 | 963:05 | 963:05 | 3162:56 | 3830:01 | 6992:57 | 6992:57 | 7956:02 | 44:57 | 94.5128 | 93.757 | 7956:02 | 44:57 | 94.5128 | 93.757
7 | Sirsi | 51 | 51 | 535:59 | 535:59 | 736:46 | 1745:16 | 2482:02 | 2482:02 | 3018:01 | 59:11 | 93.2406 | 91.781 | 3018:01 | 59:11 | 93.2406 | 91.781
8 | Dandeli | 19 | 19 | 6:31 | 6:31 | 285:47 | 423:49 | 709:36 | 709:36 | 716:07 | 37:41 | 94.8129 | 94.7652 | 716:07 | 37:41 | 94.8129 | 94.7652
9 | Karwar | 30 | 30 | 152:48 | 152:48 | 266:49 | 375:24 | 642:13 | 642:13 | 795:01 | 26:30 | 97.0268 | 96.3194 | 795:01 | 26:30 | 97.0268 | 96.3194
10 | Honnavar | 38 | 38 | 212:57 | 212:57 | 482:36 | 497:36 | 980:12 | 980:12 | 1193:09 | 31:24 | 96.4174 | 95.6391 | 1193:09 | 31:24 | 96.4174 | 95.6391
11 | Belagavi | 131 | 131 | 476:54 | 476:54 | 2805:36 | 2587:41 | 5393:17 | 5393:17 | 5870:11 | 44:49 | 94.2819 | 93.7763 | 5870:11 | 44:49 | 94.2819 | 93.7763
12 | Bailhongal | 189 | 189 | 816:28 | 816:28 | 3484:41 | 5364:28 | 8849:09 | 8849:09 | 9665:37 | 51:08 | 93.4971 | 92.8971 | 9665:37 | 51:08 | 93.4971 | 92.8971
13 | Ramdurg | 73 | 73 | 298:25 | 298:25 | 2143:52 | 3241:18 | 5385:10 | 5385:10 | 5683:35 | 77:51 | 89.7542 | 89.1865 | 5683:35 | 77:51 | 89.7542 | 89.1865
14 | Ghataprabha | 157 | 157 | 485:40 | 485:40 | 1275:20 | 1278:11 | 2553:31 | 2553:31 | 3039:11 | 19:21 | 97.7411 | 97.3114 | 3039:11 | 19:21 | 97.7411 | 97.3114
15 | Raibag | 160 | 160 | 459:18 | 459:18 | 3174:38 | 1319:03 | 4493:41 | 4493:41 | 4952:59 | 30:57 | 96.0992 | 95.7005 | 4952:59 | 30:57 | 96.0992 | 95.7005
16 | Athani | 180 | 180 | 688:57 | 688:57 | 3163:28 | 1954:08 | 5117:36 | 5117:36 | 5806:33 | 32:16 | 96.0512 | 95.5196 | 5806:33 | 32:16 | 96.0512 | 95.5196
17 | Chikkodi | 183 | 183 | 418:21 | 418:21 | 1235:25 | 1536:28 | 2771:53 | 2771:53 | 3190:14 | 17:26 | 97.8963 | 97.5788 | 3190:14 | 17:26 | 97.8963 | 97.5788
18 | Vijayapur | 145 | 145 | 285:52 | 285:52 | 1316:12 | 2939:40 | 4255:52 | 4255:52 | 4541:44 | 31:19 | 95.9235 | 95.6497 | 4541:44 | 31:19 | 95.9235 | 95.6497
19 | Indi | 235 | 235 | 1177:32 | 1177:32 | 3284:03 | 5344:03 | 8628:06 | 8628:06 | 9805:38 | 41:44 | 94.9007 | 94.2047 | 9805:38 | 41:44 | 94.9007 | 94.2047
20 | B.Bagewadi | 125 | 125 | 388:52 | 388:52 | 1487:20 | 2822:53 | 4310:13 | 4310:13 | 4699:05 | 37:36 | 95.2109 | 94.7788 | 4699:05 | 37:36 | 95.2109 | 94.7788
21 | Bagalkot | 179 | 179 | 617:27 | 617:27 | 2909:36 | 4732:05 | 7641:41 | 7641:41 | 8259:08 | 46:08 | 94.0707 | 93.5916 | 8259:08 | 46:08 | 94.0707 | 93.5916
22 | Jamkhandi | 225 | 225 | 823:01 | 823:01 | 2197:48 | 1526:39 | 3724:27 | 3724:27 | 4547:28 | 20:13 | 97.701 | 97.1929 | 4547:28 | 20:13 | 97.701 | 97.1929
23 | Mudhol | 161 | 161 | 119:39 | 119:39 | 1260:52 | 1792:52 | 3053:44 | 3053:44 | 3173:23 | 19:43 | 97.3657 | 97.2624 | 3173:23 | 19:43 | 97.3657 | 97.2624
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2020 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of May-2020 |  |  |  | Reliability for cumulative period from Apr-20 to May-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 285:49 | 437:20 | 1613:58 | 1610:23 | 3224:21 | 5062:23 | 3510:10 | 79:47 | 90.1504 | 89.2774 | 5499:43 | 125:00 | 92.1411 | 91.4622
2 | Dharwad Rural | 80 | 80 | 297:31 | 595:02 | 2049:11 | 3237:12 | 5286:23 | 11247:35 | 5583:54 | 69:48 | 91.1183 | 90.6184 | 11842:37 | 148:02 | 90.3965 | 89.8885
3 | Gadag | 84 | 84 | 413:40 | 766:15 | 2834:43 | 7046:39 | 9881:22 | 13381:31 | 10295:02 | 122:34 | 84.1888 | 83.5269 | 14147:46 | 168:26 | 89.1186 | 88.4955
4 | Ron | 53 | 53 | 400:12 | 518:47 | 1170:35 | 2540:17 | 3710:52 | 6124:47 | 4111:04 | 77:34 | 90.5892 | 89.5743 | 6643:34 | 125:21 | 92.1064 | 91.4378
5 | Haveri | 193 | 193 | 2522:55 | 4041:13 | 4436:26 | 12904:24 | 17340:50 | 23473:17 | 19863:45 | 102:55 | 87.9235 | 86.1665 | 1146.4375 | 142:34 | 91.6924 | 90.2621
6 | Ranebennur | 177 | 177 | 1854:39 | 2817:44 | 4936:57 | 8271:10 | 13208:07 | 20201:04 | 15062:46 | 85:06 | 89.9701 | 88.5618 | 23018:48 | 130:03 | 92.2042 | 91.1168
7 | Sirsi | 51 | 51 | 833:20 | 1369:19 | 1130:56 | 2389:34 | 3520:30 | 6002:32 | 4353:50 | 85:22 | 90.7219 | 88.5256 | 7371:51 | 144:33 | 91.9606 | 90.1266
8 | Dandeli | 20 | 20 | 184:11 | 190:42 | 448:21 | 694:18 | 1142:39 | 1852:15 | 1326:50 | 66:20 | 92.3209 | 91.0831 | 2042:57 | 102:09 | 93.674 | 93.0227
9 | Karwar | 31 | 31 | 316:24 | 469:12 | 539:36 | 401:49 | 941:25 | 1583:38 | 1257:49 | 40:34 | 95.9182 | 94.5464 | 2052:50 | 66:13 | 96.5106 | 95.4767
10 | Honnavar | 38 | 38 | 679:59 | 892:56 | 716:19 | 645:55 | 1362:14 | 2342:26 | 2042:13 | 53:45 | 95.1817 | 92.7765 | 3235:22 | 85:08 | 95.7894 | 94.1843
11 | Belagavi | 131 | 131 | 593:52 | 1070:46 | 2751:52 | 1959:00 | 4710:52 | 10104:09 | 5304:44 | 40:30 | 95.1666 | 94.5572 | 11174:55 | 85:18 | 94.7315 | 94.1732
12 | Bailhongal | 189 | 189 | 1454:18 | 2270:46 | 3777:48 | 4678:50 | 8456:38 | 17305:47 | 9910:56 | 52:26 | 93.986 | 92.9518 | 19576:33 | 103:35 | 93.7456 | 92.9249
13 | Ramdurg | 74 | 74 | 372:15 | 670:40 | 2002:35 | 2062:35 | 4065:10 | 9450:20 | 4437:25 | 59:58 | 92.6163 | 91.9402 | 10121:00 | 136:46 | 91.2768 | 90.6578
14 | Ghataprabha | 157 | 157 | 598:41 | 1084:21 | 1854:52 | 3104:29 | 4959:21 | 7512:52 | 5558:02 | 35:24 | 95.7543 | 95.2417 | 8597:13 | 54:46 | 96.7314 | 96.2596
15 | Raibag | 163 | 163 | 956:50 | 1416:08 | 4464:09 | 1919:37 | 6383:46 | 10877:27 | 7340:36 | 45:02 | 94.736 | 93.947 | 12293:35 | 75:25 | 95.4417 | 94.8483
16 | Athani | 182 | 182 | 1180:23 | 1869:20 | 3570:38 | 2389:06 | 5959:44 | 11077:20 | 7140:07 | 39:14 | 95.5987 | 94.727 | 12946:40 | 71:08 | 95.8426 | 95.141
17 | Chikkodi | 185 | 185 | 365:07 | 783:28 | 1686:55 | 1544:39 | 3231:34 | 6003:27 | 3596:41 | 19:26 | 97.6522 | 97.3869 | 6786:55 | 36:41 | 97.7834 | 97.4941
18 | Vijayapur | 147 | 147 | 653:00 | 938:52 | 1920:44 | 4439:23 | 6360:07 | 10615:59 | 7013:07 | 47:42 | 94.1847 | 93.5876 | 11554:51 | 78:36 | 95.0671 | 94.6308
19 | Indi | 246 | 246 | 2118:08 | 3295:40 | 4097:35 | 5427:59 | 9525:34 | 18153:40 | 11643:42 | 47:20 | 94.7955 | 93.6382 | 21449:20 | 87:12 | 94.9593 | 94.0442
20 | B.Bagewadi | 127 | 127 | 693:53 | 1082:45 | 2076:12 | 2988:28 | 5064:40 | 9374:53 | 5758:33 | 45:21 | 94.6399 | 93.9055 | 10457:38 | 82:21 | 94.9578 | 94.3754
21 | Bagalkot | 179 | 179 | 1587:22 | 2204:49 | 4461:39 | 4665:25 | 9127:04 | 16768:45 | 10714:26 | 59:51 | 93.1466 | 91.9547 | 18973:34 | 106:00 | 93.6011 | 92.7597
22 | Jamkhandi | 201 | 201 | 415:08 | 1238:09 | 2653:25 | 2394:38 | 5048:03 | 8772:30 | 5463:11 | 27:11 | 96.6244 | 96.3468 | 10010:39 | 49:48 | 97.0188 | 96.5981
23 | Mudhol | 190 | 190 | 293:28 | 413:07 | 2059:31 | 2725:07 | 4784:38 | 7838:22 | 5078:06 | 26:44 | 96.6153 | 96.4077 | 8251:29 | 43:26 | 97.1821 | 97.0335
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2020 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of June-2020 |  |  |  | Reliability for cumulative period from Apr-20 to June-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 327:45 | 765:05 | 1270:38 | 1288:58 | 2559:36 | 7621:59 | 2887:21 | 65:37 | 91.9205 | 90.8859 | 8387:04 | 190:37 | 92.0684 | 91.2722
2 | Dharwad Rural | 80 | 80 | 97:15 | 692:17 | 2070:48 | 3143:32 | 5214:20 | 16461:55 | 5311:35 | 66:24 | 90.9473 | 90.7785 | 17154:12 | 214:26 | 90.5781 | 90.1819
3 | Gadag | 84 | 84 | 490:10 | 1256:25 | 2088:10 | 2720:56 | 4809:06 | 18190:37 | 5299:16 | 63:05 | 92.0484 | 91.238 | 19447:02 | 231:31 | 90.0845 | 89.3996
4 | Ron | 53 | 53 | 314:53 | 833:40 | 1106:50 | 1902:48 | 3009:38 | 9134:25 | 3324:31 | 62:44 | 92.1131 | 91.288 | 9968:05 | 188:05 | 92.1086 | 91.3884
5 | Haveri | 195 | 195 | 1695:50 | 5737:03 | 3969:48 | 13879:25 | 17849:13 | 1721.7708 | 19545:03 | 100:14 | 87.2869 | 86.079 | 1960.8146 | 241:20 | 90.2971 | 88.95
6 | Ranebennur | 179 | 179 | 809:49 | 3627:33 | 4922:50 | 8654:25 | 13577:15 | 1407.4299 | 14387:04 | 80:22 | 89.4652 | 88.8369 | 1558.5778 | 208:58 | 91.3596 | 90.4317
7 | Sirsi | 52 | 52 | 806:50 | 2176:09 | 1146:56 | 2672:33 | 3819:29 | 9822:01 | 4626:19 | 88:58 | 89.7984 | 87.6434 | 11998:10 | 230:44 | 91.3514 | 89.4353
8 | Dandeli | 20 | 20 | 196:36 | 387:18 | 391:18 | 867:50 | 1259:08 | 3111:23 | 1455:44 | 72:47 | 91.256 | 89.8907 | 3498:41 | 174:56 | 92.8769 | 91.9902
9 | Karwar | 31 | 31 | 438:19 | 907:31 | 465:22 | 1178:00 | 1643:22 | 3227:00 | 2081:41 | 67:09 | 92.6372 | 90.6735 | 4134:31 | 133:22 | 95.2337 | 93.8932
10 | Honnavar | 38 | 38 | 379:36 | 1272:32 | 703:47 | 1281:27 | 1985:14 | 4327:40 | 2364:50 | 62:14 | 92.744 | 91.3566 | 5600:12 | 147:22 | 94.7854 | 93.2521
11 | Belagavi | 132 | 132 | 655:35 | 1726:21 | 2836:20 | 3627:46 | 6464:06 | 16568:15 | 7119:41 | 53:56 | 93.1985 | 92.5088 | 18294:36 | 138:36 | 94.2529 | 93.6541
12 | Bailhongal | 191 | 191 | 754:08 | 3024:54 | 3627:04 | 5532:56 | 9160:00 | 1102.741 | 9914:08 | 51:54 | 93.3392 | 92.7908 | 1228.7785 | 154:24 | 93.6555 | 92.9303
13 | Ramdurg | 75 | 75 | 794:45 | 1465:25 | 2099:58 | 2560:26 | 4660:24 | 14110:44 | 5455:09 | 72:44 | 91.3696 | 89.8979 | 15576:09 | 207:41 | 91.3854 | 90.4908
14 | Ghataprabha | 157 | 157 | 636:07 | 1720:28 | 1619:39 | 2743:49 | 4363:28 | 11876:20 | 4999:35 | 31:51 | 96.1399 | 95.5772 | 13596:48 | 86:36 | 96.5364 | 96.0346
15 | Raibag | 162 | 162 | 648:22 | 2064:30 | 6573:00 | 2210:42 | 8783:42 | 19661:09 | 9432:04 | 58:13 | 92.4694 | 91.9135 | 21725:39 | 134:07 | 94.443 | 93.8595
16 | Athani | 184 | 184 | 1219:29 | 3088:49 | 3691:24 | 2317:15 | 6008:39 | 17085:59 | 7228:08 | 39:17 | 95.4645 | 94.544 | 20174:48 | 109:39 | 95.7482 | 94.9796
17 | Chikkodi | 185 | 185 | 215:40 | 999:08 | 2103:47 | 2462:13 | 4566:00 | 10569:27 | 4781:40 | 25:51 | 96.5721 | 96.4102 | 11568:35 | 62:32 | 97.3841 | 97.1368
18 | Vijayapur | 151 | 151 | 445:08 | 1384:00 | 2342:59 | 6962:21 | 9305:20 | 19921:19 | 9750:28 | 64:34 | 91.441 | 91.0316 | 21305:19 | 141:06 | 93.9593 | 93.5396
19 | Indi | 247 | 247 | 995:08 | 4290:48 | 4754:00 | 8910:58 | 13664:58 | 1325.7764 | 14660:06 | 59:21 | 92.3161 | 91.7566 | 1504.5597 | 146:12 | 94.1016 | 93.3062
20 | B.Bagewadi | 127 | 127 | 753:49 | 1836:34 | 2495:15 | 5711:05 | 8206:20 | 17581:13 | 8960:09 | 70:33 | 91.0254 | 90.2011 | 19417:47 | 152:54 | 93.6614 | 92.9993
21 | Bagalkot | 179 | 179 | 879:22 | 3084:11 | 4600:10 | 6415:37 | 11015:47 | 1157.6889 | 11895:09 | 66:27 | 91.4527 | 90.7704 | 1286.1965 | 172:27 | 92.8928 | 92.1039
22 | Jamkhandi | 199 | 199 | 969:45 | 2207:54 | 3044:58 | 3956:25 | 7001:23 | 15773:53 | 7971:08 | 40:03 | 95.1135 | 94.4367 | 17981:47 | 90:22 | 96.3706 | 95.8626
23 | Mudhol | 192 | 192 | 603:59 | 1017:06 | 2165:52 | 3763:33 | 5929:25 | 13767:47 | 6533:24 | 34:02 | 95.7108 | 95.2739 | 14784:53 | 77:00 | 96.7167 | 96.4741
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of July-2020 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of July-2020 |  |  |  | Reliability for cumulative period from Apr-20 to July-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 91:55 | 857:00 | 1130:50 | 1458:44 | 2589:34 | 10211:33 | 2681:29 | 58:18 | 92.4335 | 92.1649 | 11068:33 | 240:37 | 92.4184 | 91.7821
2 | Dharwad Rural | 81 | 81 | 62:10 | 754:27 | 1258:42 | 1960:06 | 3218:48 | 19680:43 | 3280:58 | 40:30 | 94.6588 | 94.5557 | 20435:10 | 252:17 | 91.7018 | 91.3837
3 | Gadag | 87 | 87 | 68:20 | 1324:45 | 1598:31 | 3143:13 | 4741:44 | 22932:21 | 4810:04 | 55:17 | 92.6744 | 92.5688 | 1010.7125 | 278:49 | 90.9976 | 90.4776
4 | Ron | 53 | 53 | 66:00 | 1322:25 | 796:05 | 1287:55 | 2084:00 | 11218:25 | 2150:00 | 40:34 | 94.715 | 94.5476 | 12118:05 | 228:39 | 92.7709 | 92.1912
5 | Haveri | 195 | 195 | 794:30 | 6531:33 | 3134:35 | 9220:40 | 12355:15 | 2236.5729 | 13149:45 | 67:26 | 91.4838 | 90.9362 | 2508.7208 | 308:46 | 90.5987 | 89.4547
6 | Ranebennur | 179 | 179 | 726:41 | 4354:14 | 3704:11 | 5766:06 | 9470:17 | 1802.025 | 10196:58 | 56:58 | 92.8889 | 92.3432 | 1983.4514 | 265:56 | 91.7482 | 90.9174
7 | Sirsi | 51 | 51 | 171:13 | 2347:22 | 421:18 | 1903:53 | 2325:11 | 12147:12 | 2496:24 | 48:57 | 93.8721 | 93.4208 | 14494:34 | 284:12 | 91.8654 | 90.2935
8 | Dandeli | 20 | 20 | 69:01 | 456:19 | 273:20 | 684:35 | 957:55 | 4069:18 | 1026:56 | 51:21 | 93.5624 | 93.0986 | 4525:37 | 226:17 | 93.0511 | 92.2718
9 | Karwar | 31 | 31 | 296:55 | 1204:26 | 437:12 | 767:39 | 1204:51 | 4431:51 | 1501:46 | 48:27 | 94.7761 | 93.4887 | 5636:17 | 181:49 | 95.1174 | 93.7905
10 | Honnavar | 39 | 39 | 371:28 | 1644:00 | 482:31 | 697:12 | 1179:43 | 5507:23 | 1551:11 | 39:46 | 95.9343 | 94.654 | 7151:23 | 183:22 | 95.1771 | 93.7374
11 | Belagavi | 131 | 131 | 215:01 | 1941:22 | 2577:43 | 1895:01 | 4472:44 | 21040:59 | 4687:45 | 35:47 | 95.4109 | 95.1903 | 22982:21 | 175:26 | 94.5144 | 94.0083
12 | Bailhongal | 191 | 191 | 389:41 | 3414:35 | 2663:52 | 4785:37 | 7449:29 | 1413.1361 | 7839:10 | 41:03 | 94.7577 | 94.4835 | 1555.4104 | 195:27 | 93.9356 | 93.325
13 | Ramdurg | 75 | 75 | 68:59 | 1534:24 | 1296:58 | 1971:53 | 3268:51 | 17379:35 | 3337:50 | 44:30 | 94.1418 | 94.0182 | 18913:59 | 252:11 | 92.0858 | 91.3871
14 | Ghataprabha | 157 | 157 | 430:23 | 2150:51 | 1664:36 | 2254:39 | 3919:15 | 15795:35 | 4349:38 | 27:42 | 96.6447 | 96.2763 | 17946:26 | 114:19 | 96.5639 | 96.096
15 | Raibag | 163 | 163 | 656:43 | 2721:13 | 5697:26 | 1208:40 | 6906:06 | 1106.9688 | 7562:49 | 46:24 | 94.3053 | 93.7638 | 1220.3528 | 179:41 | 94.4334 | 93.8633
16 | Athani | 184 | 184 | 739:15 | 3828:04 | 2691:10 | 1805:47 | 4496:57 | 21582:56 | 5236:12 | 28:27 | 96.7151 | 96.1751 | 1058.7917 | 138:06 | 95.9939 | 95.2834
17 | Chikkodi | 185 | 185 | 214:03 | 1213:11 | 1327:45 | 1324:50 | 2652:35 | 13222:02 | 2866:38 | 15:30 | 98.0728 | 97.9173 | 14435:13 | 78:02 | 97.5591 | 97.3351
18 | Vijayapur | 152 | 152 | 161:25 | 1545:25 | 2065:54 | 5409:51 | 7475:45 | 1141.5444 | 7637:10 | 50:15 | 93.3894 | 93.2467 | 1205.9368 | 190:25 | 93.8441 | 93.4969
19 | Indi | 247 | 247 | 1397:50 | 5688:38 | 3822:44 | 8449:41 | 12272:25 | 1837.1271 | 13670:15 | 55:21 | 93.3218 | 92.5611 | 2074.1535 | 201:32 | 93.9035 | 93.1169
20 | B.Bagewadi | 128 | 128 | 582:08 | 2418:42 | 2045:15 | 5496:40 | 7541:55 | 1046.7972 | 8124:03 | 63:28 | 92.0805 | 91.4692 | 1147.5764 | 215:10 | 93.2966 | 92.6513
21 | Bagalkot | 180 | 180 | 358:01 | 3442:12 | 3822:53 | 5713:33 | 9536:26 | 1555.0403 | 9894:27 | 54:58 | 92.879 | 92.6117 | 1698.4653 | 226:28 | 92.9188 | 92.2656
22 | Jamkhandi | 200 | 200 | 548:11 | 2756:05 | 2027:02 | 2400:38 | 4427:40 | 20201:33 | 4975:51 | 24:53 | 97.0244 | 96.656 | 22957:38 | 114:47 | 96.5503 | 96.0796
23 | Mudhol | 190 | 190 | 501:23 | 1518:29 | 1910:53 | 2912:38 | 4823:31 | 18591:18 | 5324:54 | 28:02 | 96.5878 | 96.2331 | 20109:47 | 105:50 | 96.6582 | 96.3852
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of August-2020 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of August-2020 |  |  |  | Reliability for cumulative period from Apr-20 to August-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 177:45 | 1034:45 | 1257:12 | 2345:43 | 3602:55 | 13814:28 | 3780:40 | 84:01 | 89.2386 | 88.7077 | 14849:13 | 329:59 | 91.6398 | 91.0135
2 | Dharwad Rural | 81 | 81 | 218:40 | 973:07 | 1561:14 | 4565:48 | 6127:02 | 1075.3229 | 6345:42 | 78:21 | 89.833 | 89.4702 | 1115.8694 | 330:38 | 91.3231 | 90.996
3 | Gadag | 89 | 89 | 187:50 | 1512:35 | 2378:28 | 2685:07 | 5063:35 | 1166.4972 | 5251:25 | 59:00 | 92.3529 | 92.0693 | 1229.5215 | 331:33 | 91.4335 | 90.9707
4 | Ron | 53 | 53 | 102:11 | 1424:36 | 1307:35 | 1532:15 | 2839:50 | 14058:15 | 2942:01 | 55:31 | 92.7982 | 92.539 | 15060:06 | 284:09 | 92.7764 | 92.2616
5 | Haveri | 195 | 195 | 1259:32 | 7791:05 | 2825:18 | 16959:37 | 19784:55 | 3060.9444 | 21044:27 | 107:55 | 86.3628 | 85.4946 | 3385.5729 | 416:41 | 89.7404 | 88.6523
6 | Ranebennur | 182 | 182 | 596:05 | 4950:19 | 4362:59 | 7266:27 | 11629:26 | 2286.5847 | 12225:31 | 67:10 | 91.4116 | 90.9713 | 2492.8479 | 328:44 | 91.7885 | 91.0477
7 | Sirsi | 52 | 52 | 856:30 | 3203:52 | 757:55 | 3678:37 | 4436:32 | 16583:44 | 5293:02 | 101:47 | 88.5325 | 86.3187 | 19787:36 | 380:32 | 91.3149 | 89.637
8 | Dandeli | 20 | 20 | 217:18 | 673:37 | 300:43 | 599:40 | 900:23 | 4969:41 | 1117:41 | 55:53 | 93.949 | 92.4887 | 5643:18 | 282:10 | 93.233 | 92.3158
9 | Karwar | 31 | 31 | 541:11 | 1745:37 | 623:21 | 1006:49 | 1630:10 | 6062:01 | 2171:21 | 70:03 | 92.932 | 90.5855 | 7807:38 | 251:52 | 94.6746 | 93.1411
10 | Honnavar | 39 | 39 | 631:09 | 2275:09 | 702:35 | 1064:34 | 1767:09 | 7274:32 | 2398:18 | 61:30 | 93.9097 | 91.7346 | 9549:41 | 244:52 | 94.9203 | 93.3316
11 | Belagavi | 131 | 131 | 651:05 | 2592:27 | 3873:26 | 6935:16 | 10808:42 | 1327.0701 | 11459:47 | 87:29 | 88.9101 | 88.242 | 1435.0889 | 262:55 | 93.3789 | 92.8399
12 | Bailhongal | 191 | 191 | 447:15 | 3861:50 | 3440:07 | 7927:01 | 11367:08 | 1886.7667 | 11814:23 | 61:51 | 92.0008 | 91.6861 | 2047.6764 | 257:18 | 93.5436 | 92.9929
13 | Ramdurg | 75 | 75 | 177:55 | 1712:19 | 1491:23 | 2546:48 | 4038:11 | 21417:46 | 4216:06 | 56:13 | 92.7631 | 92.4443 | 23130:05 | 308:24 | 92.223 | 91.6013
14 | Ghataprabha | 157 | 157 | 88:49 | 2239:40 | 1832:37 | 2249:57 | 4082:34 | 19878:09 | 4171:23 | 26:34 | 96.5049 | 96.4289 | 22117:49 | 140:53 | 96.5519 | 96.1635
15 | Raibag | 163 | 163 | 149:05 | 2870:18 | 5149:10 | 1757:26 | 6906:36 | 1394.7437 | 7055:41 | 43:17 | 94.3049 | 94.1819 | 1514.3396 | 222:58 | 94.4074 | 93.9278
16 | Athani | 183 | 183 | 406:06 | 4234:10 | 2737:06 | 1324:04 | 4061:10 | 1068.5042 | 4467:16 | 24:25 | 97.0172 | 96.7189 | 1244.9278 | 163:16 | 96.1838 | 95.5537
17 | Chikkodi | 185 | 185 | 179:45 | 1392:56 | 2001:31 | 2082:52 | 4084:23 | 17306:25 | 4264:08 | 23:03 | 97.0326 | 96.902 | 18699:21 | 101:05 | 97.4524 | 97.2473
18 | Vijayapur | 151 | 151 | 355:38 | 1901:03 | 2065:09 | 4212:38 | 6277:47 | 1403.1187 | 6633:25 | 43:56 | 94.412 | 94.0954 | 1482.3292 | 235:36 | 93.9267 | 93.5838
19 | Indi | 247 | 247 | 1218:43 | 6907:21 | 3313:29 | 6855:37 | 10169:06 | 2260.8396 | 11387:49 | 46:06 | 94.4663 | 93.8032 | 2548.6458 | 247:39 | 94.0175 | 93.2559
20 | B.Bagewadi | 129 | 129 | 391:21 | 2810:03 | 1837:00 | 4454:59 | 6291:59 | 1308.9632 | 6683:20 | 51:49 | 93.4442 | 93.0365 | 1426.0486 | 265:19 | 93.368 | 92.7747
21 | Bagalkot | 180 | 180 | 494:07 | 3936:19 | 3939:04 | 5580:21 | 9519:25 | 1951.6826 | 10013:32 | 55:38 | 92.8917 | 92.5227 | 2115.6958 | 282:06 | 92.9133 | 92.3177
22 | Jamkhandi | 202 | 202 | 182:43 | 2938:48 | 2362:57 | 1566:54 | 3929:51 | 1005.475 | 4112:34 | 20:22 | 97.3851 | 97.2635 | 1127.925 | 134:01 | 96.7467 | 96.3505
23 | Mudhol | 190 | 190 | 281:15 | 1799:44 | 3657:04 | 2220:36 | 5877:40 | 1019.5403 | 6158:55 | 32:25 | 95.8421 | 95.6431 | 1094.5292 | 138:15 | 96.4928 | 96.2348
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of September-2020 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of September-2020 |  |  |  | Reliability for cumulative period from Apr-20 to Sept-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 294:35 | 1329:20 | 836:02 | 2180:31 | 3016:33 | 16831:01 | 3311:08 | 73:35 | 90.6897 | 89.7805 | 18160:21 | 403:34 | 91.484 | 90.8114
2 | Dharwad Rural | 81 | 81 | 185:11 | 1158:18 | 1610:50 | 2481:43 | 4092:33 | 1245.8458 | 4277:44 | 52:49 | 92.9826 | 92.6651 | 1294.1083 | 383:26 | 91.5952 | 91.2696
3 | Gadag | 92 | 92 | 357:00 | 1869:35 | 2269:43 | 3182:54 | 5452:37 | 1393.6896 | 5809:37 | 63:09 | 91.7684 | 91.2294 | 1471.5889 | 383:54 | 91.722 | 91.2593
4 | Ron | 53 | 53 | 175:10 | 1599:46 | 869:15 | 1812:06 | 2681:21 | 16739:36 | 2856:31 | 53:54 | 92.9734 | 92.5144 | 17916:37 | 338:03 | 92.8087 | 92.3031
5 | Haveri | 195 | 195 | 1488:37 | 9279:42 | 2455:00 | 12128:34 | 14583:34 | 3668.5931 | 16072:11 | 82:25 | 89.6128 | 88.5526 | 4055.2472 | 499:06 | 89.7195 | 88.636
6 | Ranebennur | 182 | 182 | 1021:52 | 5972:11 | 3720:45 | 9021:28 | 12742:13 | 2817.5104 | 13764:05 | 75:38 | 90.2761 | 89.4963 | 3066.3514 | 404:21 | 91.5405 | 90.7934
7 | Sirsi | 52 | 52 | 199:16 | 3403:08 | 580:23 | 1898:05 | 2478:28 | 19062:12 | 2677:44 | 51:30 | 93.3802 | 92.8479 | 22465:20 | 432:02 | 91.6534 | 90.1634
8 | Dandeli | 20 | 20 | 160:36 | 834:13 | 409:40 | 525:36 | 935:16 | 5904:57 | 1095:52 | 54:48 | 93.5051 | 92.3898 | 6739:10 | 336:57 | 93.2776 | 92.3279
9 | Karwar | 32 | 32 | 388:35 | 2134:12 | 382:03 | 478:39 | 860:42 | 6922:43 | 1249:17 | 39:02 | 96.2643 | 94.5778 | 9056:55 | 283:02 | 95.0743 | 93.5558
10 | Honnavar | 39 | 39 | 338:32 | 2613:41 | 599:21 | 703:47 | 1303:08 | 8577:40 | 1641:40 | 42:06 | 95.3592 | 94.1536 | 11191:21 | 286:57 | 94.9923 | 93.4664
11 | Belagavi | 131 | 131 | 688:00 | 3280:27 | 2684:02 | 2591:29 | 5275:31 | 1546.8833 | 5963:31 | 45:31 | 94.4068 | 93.6774 | 1683.5685 | 308:26 | 93.5474 | 92.9772
12 | Bailhongal | 191 | 191 | 1531:02 | 5392:52 | 2385:44 | 6413:50 | 8799:34 | 2253.4153 | 10330:36 | 54:05 | 93.6012 | 92.4879 | 2478.1181 | 311:23 | 93.553 | 92.9101
13 | Ramdurg | 75 | 75 | 400:50 | 2113:09 | 1547:09 | 2575:58 | 4123:07 | 1064.2035 | 4523:57 | 60:19 | 92.3646 | 91.6223 | 1152.2514 | 368:43 | 92.2462 | 91.6047
14 | Ghataprabha | 157 | 157 | 400:05 | 2639:45 | 1430:59 | 2787:38 | 4218:37 | 1004.0319 | 4618:42 | 29:25 | 96.268 | 95.9141 | 1114.0215 | 170:18 | 96.5054 | 96.1226
15 | Raibag | 166 | 166 | 196:40 | 3066:58 | 4359:16 | 2009:37 | 6368:53 | 1660.1139 | 6565:33 | 39:33 | 94.6713 | 94.5067 | 1787.9042 | 258:30 | 94.5351 | 94.1145
16 | Athani | 183 | 183 | 916:40 | 5150:50 | 2505:28 | 2650:24 | 5155:52 | 1283.3319 | 6072:32 | 33:11 | 96.0869 | 95.3912 | 1497.95 | 196:27 | 96.1679 | 95.527
17 | Chikkodi | 184 | 184 | 250:10 | 1643:06 | 1557:33 | 1877:58 | 3435:31 | 20741:56 | 3685:41 | 20:02 | 97.4068 | 97.2179 | 22385:02 | 121:39 | 97.4333 | 97.23
18 | Vijayapur | 151 | 151 | 400:18 | 2301:21 | 1992:24 | 5742:49 | 7735:13 | 1725.4194 | 8135:31 | 53:53 | 92.8852 | 92.517 | 1821.309 | 289:29 | 93.7559 | 93.4089
19 | Indi | 249 | 249 | 1017:16 | 7924:37 | 3275:19 | 8384:42 | 11660:01 | 2746.6736 | 12677:17 | 50:55 | 93.4962 | 92.9288 | 3076.866 | 296:34 | 93.9722 | 93.2476
20 | B.Bagewadi | 129 | 129 | 627:17 | 3437:20 | 1891:05 | 5621:27 | 7512:32 | 1621.9854 | 8139:49 | 63:06 | 91.9116 | 91.2362 | 1765.2076 | 328:25 | 93.1292 | 92.5225
21 | Bagalkot | 180 | 180 | 775:18 | 4711:37 | 3510:59 | 6709:56 | 10220:55 | 2377.5542 | 10996:13 | 61:05 | 92.1135 | 91.5153 | 2573.8715 | 343:11 | 92.7822 | 92.1862
22 | Jamkhandi | 202 | 202 | 278:26 | 3217:14 | 2136:21 | 2376:41 | 4513:02 | 1193.5181 | 4791:28 | 23:43 | 96.897 | 96.7055 | 1327.5694 | 157:44 | 96.7713 | 96.4087
23 | Mudhol | 190 | 190 | 215:43 | 2015:27 | 1868:27 | 3548:24 | 5416:51 | 1245.2424 | 5632:34 | 29:39 | 96.0403 | 95.8826 | 1329.2194 | 167:54 | 96.4186 | 96.1771
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of October-2020 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the month of October-2020 |  |  |  | Reliability for cumulative period from April-20 to October-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 364:25 | 1693:45 | 1100:15 | 1823:11 | 2923:26 | 19754:27 | 3287:51 | 73:04 | 91.2681 | 90.1797 | 21448:12 | 476:38 | 91.4527 | 90.7199
2 | Dharwad Rural | 81 | 81 | 337:00 | 1495:18 | 1435:03 | 2664:18 | 4099:21 | 1416.6521 | 4436:21 | 54:46 | 93.1977 | 92.6385 | 1478.9562 | 438:13 | 91.8273 | 91.4679
3 | Gadag | 92 | 92 | 104:55 | 1974:30 | 2254:23 | 2864:05 | 5118:28 | 1606.959 | 5223:23 | 56:47 | 92.5221 | 92.3688 | 1689.2299 | 440:40 | 91.8379 | 91.42
4 | Ron | 53 | 53 | 219:50 | 1819:36 | 1104:45 | 1359:30 | 2464:15 | 19203:51 | 2684:05 | 50:39 | 93.7506 | 93.1931 | 20600:42 | 388:42 | 92.9452 | 92.432
5 | Haveri | 195 | 195 | 1729:35 | 11009:17 | 2664:00 | 11377:47 | 14041:47 | 4253.6674 | 15771:22 | 80:53 | 90.3214 | 89.1292 | 4712.3875 | 579:59 | 89.8067 | 88.7074
6 | Ranebennur | 181 | 181 | 935:20 | 6907:31 | 3990:31 | 6526:50 | 10517:21 | 3255.7333 | 11452:41 | 63:16 | 92.1899 | 91.4954 | 3543.5465 | 469:52 | 91.5946 | 90.8516
7 | Sirsi | 53 | 53 | 478:30 | 3881:38 | 719:53 | 1428:07 | 2148:00 | 21210:12 | 2626:30 | 49:33 | 94.5526 | 93.3392 | 1045.4931 | 473:26 | 92.2081 | 90.7821
8 | Dandeli | 21 | 21 | 161:31 | 995:44 | 217:31 | 408:49 | 626:20 | 6531:17 | 787:51 | 37:31 | 95.9912 | 94.9574 | 7527:01 | 358:26 | 93.9444 | 93.0212
9 | Karwar | 32 | 32 | 314:41 | 2448:53 | 319:20 | 306:29 | 625:49 | 7548:32 | 940:30 | 29:23 | 97.3714 | 96.0496 | 9997:25 | 312:25 | 95.4071 | 93.9171
10 | Honnavar | 39 | 39 | 391:13 | 3004:54 | 380:13 | 361:44 | 741:57 | 9319:37 | 1133:10 | 29:03 | 97.443 | 96.0947 | 12324:31 | 316:01 | 95.3473 | 93.8471
11 | Belagavi | 131 | 131 | 376:45 | 3657:12 | 2765:51 | 2121:14 | 4887:05 | 1750.5118 | 5263:50 | 40:11 | 94.9858 | 94.5992 | 1902.8949 | 348:37 | 93.7558 | 93.2122
12 | Bailhongal | 191 | 191 | 2061:25 | 7454:17 | 2455:27 | 5845:47 | 8301:14 | 2599.3 | 10362:39 | 54:15 | 94.1583 | 92.7077 | 2909.8951 | 365:38 | 93.6407 | 92.8808
13 | Ramdurg | 75 | 75 | 941:03 | 3054:12 | 1169:10 | 2726:09 | 3895:19 | 1226.5083 | 4836:22 | 64:29 | 93.0191 | 91.3327 | 1353.7667 | 433:12 | 92.3582 | 91.5653
14 | Ghataprabha | 157 | 157 | 581:37 | 3221:22 | 1223:20 | 3387:34 | 4610:54 | 1196.1528 | 5192:31 | 33:04 | 96.0526 | 95.5547 | 1330.3764 | 203:22 | 96.4398 | 96.0403
15 | Raibag | 166 | 166 | 878:42 | 3945:40 | 4896:52 | 2527:38 | 7424:30 | 1969.4681 | 8303:12 | 50:01 | 93.9885 | 93.277 | 2133.8708 | 308:31 | 94.456 | 93.9932
16 | Athani | 183 | 183 | 502:50 | 5653:40 | 2094:33 | 2536:59 | 4631:32 | 1476.3125 | 5134:22 | 28:03 | 96.5983 | 96.2289 | 1711.8819 | 224:31 | 96.2302 | 95.6287
17 | Chikkodi | 184 | 184 | 363:00 | 2006:06 | 1453:39 | 2601:29 | 4055:08 | 1033.2111 | 4418:08 | 24:01 | 97.0378 | 96.7726 | 1116.7986 | 145:40 | 97.376 | 97.1638
18 | Vijayapur | 152 | 152 | 762:12 | 3063:33 | 1948:05 | 6450:58 | 8399:03 | 2075.3799 | 9161:15 | 60:16 | 92.573 | 91.899 | 2203.0278 | 347:51 | 93.6197 | 93.2273
19 | Indi | 249 | 249 | 1277:27 | 9202:04 | 3743:47 | 8745:00 | 12488:47 | 3267.0396 | 13766:14 | 55:17 | 93.2586 | 92.5691 | 3650.459 | 351:51 | 93.8689 | 93.1493
20 | B.Bagewadi | 130 | 130 | 608:39 | 4045:59 | 1689:52 | 5881:08 | 7571:00 | 1937.4438 | 8179:39 | 62:55 | 92.1722 | 91.543 | 2106.0264 | 388:48 | 93.0358 | 92.4298
21 | Bagalkot | 181 | 181 | 352:20 | 5063:57 | 2894:19 | 6610:17 | 9504:36 | 2773.5792 | 9856:56 | 54:27 | 92.942 | 92.6804 | 2984.5771 | 395:45 | 92.8394 | 92.2947
22 | Jamkhandi | 202 | 202 | 544:37 | 3761:51 | 2051:41 | 2653:17 | 4704:58 | 1389.5583 | 5249:35 | 25:59 | 96.8694 | 96.507 | 1546.3021 | 183:43 | 96.7855 | 96.4229
23 | Mudhol | 192 | 192 | 2129:13 | 4144:40 | 1916:01 | 3740:55 | 5656:56 | 1480.9479 | 7786:09 | 40:33 | 96.0399 | 94.5493 | 1653.6424 | 206:42 | 96.3957 | 95.9754
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of November-2020 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the month of November-2020 |  |  |  | Reliability for cumulative period from April-20 to November-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 195:25 | 1889:10 | 702:08 | 724:15 | 1426:23 | 21180:50 | 1621:48 | 36:02 | 95.5976 | 94.9944 | 23070:00 | 512:40 | 91.9623 | 91.2454
2 | Dharwad Rural | 81 | 81 | 141:35 | 1636:53 | 1586:28 | 1351:13 | 2937:41 | 1539.0556 | 3079:16 | 38:01 | 94.9628 | 94.7201 | 1607.259 | 476:13 | 92.2128 | 91.8677
3 | Gadag | 92 | 92 | 147:00 | 2121:30 | 1618:06 | 1199:15 | 2817:21 | 1724.3486 | 2964:21 | 32:13 | 95.7468 | 95.5248 | 1812.7444 | 472:53 | 92.3185 | 91.9247
4 | Ron | 53 | 53 | 200:05 | 2019:41 | 762:20 | 704:10 | 1466:30 | 20670:21 | 1666:35 | 31:27 | 96.157 | 95.6326 | 22267:17 | 420:08 | 93.3401 | 92.8255
5 | Haveri | 195 | 195 | 1263:40 | 12272:57 | 3237:39 | 3430:03 | 6667:42 | 4531.4883 | 7931:22 | 40:40 | 95.2509 | 94.3509 | 5042.8612 | 620:40 | 90.4761 | 89.4013
6 | Ranebennur | 182 | 182 | 768:53 | 7676:24 | 3647:13 | 2513:32 | 6160:45 | 3512.4312 | 6929:38 | 38:04 | 95.2986 | 94.7118 | 3832.2812 | 505:21 | 92.0905 | 91.3703
7 | Sirsi | 53 | 53 | 186:03 | 4067:41 | 554:16 | 882:41 | 1436:57 | 22647:09 | 1623:00 | 30:37 | 96.2344 | 95.7469 | 1113.1181 | 504:03 | 92.7031 | 91.3925
8 | Dandeli | 21 | 21 | 58:04 | 1053:48 | 208:31 | 179:30 | 388:01 | 6919:18 | 446:05 | 21:15 | 97.4338 | 97.0497 | 7973:06 | 379:40 | 94.3735 | 93.5165
9 | Karwar | 32 | 32 | 581:37 | 3030:30 | 285:06 | 309:33 | 594:39 | 8143:11 | 1176:16 | 36:45 | 97.4191 | 94.8947 | 11173:41 | 349:11 | 95.6545 | 94.0373
10 | Honnavar | 39 | 39 | 340:09 | 3345:03 | 399:02 | 288:50 | 687:52 | 10007:29 | 1028:01 | 26:22 | 97.5503 | 96.339 | 13352:32 | 342:22 | 95.6181 | 94.1535
11 | Belagavi | 133 | 133 | 210:16 | 3867:28 | 2409:31 | 1243:13 | 3652:44 | 1902.709 | 3863:00 | 29:03 | 96.1855 | 95.966 | 2063.8532 | 372:25 | 94.1369 | 93.6403
12 | Bailhongal | 191 | 191 | 383:18 | 7837:35 | 2203:55 | 2804:39 | 5008:34 | 2807.9903 | 5391:52 | 28:14 | 96.3579 | 96.0792 | 3134.5562 | 393:52 | 93.9748 | 93.2741
13 | Ramdurg | 75 | 75 | 251:40 | 3305:52 | 1450:20 | 702:30 | 2152:50 | 1316.2097 | 2404:30 | 32:04 | 96.0133 | 95.5472 | 1453.9542 | 465:16 | 92.8076 | 92.0549
14 | Ghataprabha | 156 | 156 | 284:53 | 3506:15 | 1312:06 | 1003:10 | 2315:16 | 1292.6222 | 2600:09 | 16:40 | 97.9387 | 97.6851 | 1438.716 | 221:20 | 96.6041 | 96.2203
15 | Raibag | 168 | 168 | 304:11 | 4249:51 | 4625:20 | 1019:00 | 5644:20 | 2204.6486 | 5948:31 | 35:24 | 95.3337 | 95.0822 | 2381.7257 | 340:15 | 94.6218 | 94.1898
16 | Athani | 183 | 183 | 582:07 | 6235:47 | 2448:53 | 1461:03 | 3909:56 | 1639.2264 | 4492:03 | 24:33 | 97.0325 | 96.5907 | 1899.0507 | 249:03 | 96.3289 | 95.747
17 | Chikkodi | 185 | 185 | 131:25 | 2137:31 | 1282:07 | 946:44 | 2228:51 | 1126.0799 | 2360:16 | 12:45 | 98.3267 | 98.228 | 1215.1431 | 157:38 | 97.5054 | 97.3081
18 | Vijayapur | 152 | 152 | 87:10 | 3150:43 | 1540:24 | 2736:01 | 4276:25 | 2253.5639 | 4363:35 | 28:42 | 96.0925 | 96.0128 | 2384.8438 | 376:33 | 93.9237 | 93.5698
19 | Indi | 249 | 249 | 520:36 | 9722:40 | 2424:27 | 2941:32 | 5365:59 | 3490.6222 | 5886:35 | 23:38 | 97.0069 | 96.7165 | 3895.7333 | 375:30 | 94.2547 | 93.5879
20 | B.Bagewadi | 130 | 130 | 234:20 | 4280:19 | 1251:27 | 1827:48 | 3079:15 | 2065.7458 | 3313:35 | 25:29 | 96.7102 | 96.4598 | 2244.0924 | 414:18 | 93.4876 | 92.9253
21 | Bagalkot | 181 | 181 | 428:09 | 5492:06 | 2798:06 | 3398:38 | 6196:44 | 3031.7764 | 6624:53 | 36:36 | 95.245 | 94.9164 | 3260.6139 | 432:21 | 93.1352 | 92.617
22 | Jamkhandi | 205 | 205 | 212:58 | 3974:49 | 1613:30 | 1004:04 | 2617:34 | 1498.6236 | 2830:32 | 13:48 | 98.2266 | 98.0823 | 1664.241 | 194:50 | 97.004 | 96.6728
23 | Mudhol | 192 | 192 | 162:45 | 4307:25 | 1622:03 | 1311:00 | 2933:03 | 1603.1583 | 3095:48 | 16:07 | 97.8783 | 97.7606 | 1782.634 | 222:50 | 96.578 | 96.1949
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of December-2020 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the month of December-2020 |  |  |  | Reliability for cumulative period from April-20 to December-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 89:05 | 1978:15 | 492:13 | 456:13 | 948:26 | 22129:16 | 1037:31 | 23:03 | 97.1672 | 96.9011 | 1004.4799 | 535:43 | 92.5491 | 91.883
2 | Dharwad Rural | 82 | 82 | 209:00 | 1845:53 | 1587:03 | 861:21 | 2448:24 | 1641.0722 | 2657:24 | 32:24 | 95.9868 | 95.6442 | 1717.984 | 502:49 | 92.7225 | 92.3814
3 | Gadag | 93 | 93 | 37:32 | 2159:02 | 2341:32 | 1857:58 | 4199:30 | 1899.3278 | 4237:02 | 45:34 | 93.9307 | 93.8764 | 1989.2875 | 513:22 | 92.5735 | 92.2217
4 | Ron | 53 | 53 | 80:00 | 2099:41 | 524:10 | 246:35 | 770:45 | 21441:06 | 850:45 | 16:03 | 98.0454 | 97.8425 | 23118:02 | 436:11 | 93.8705 | 93.3911
5 | Haveri | 196 | 196 | 498:31 | 12771:28 | 2775:49 | 2073:04 | 4848:53 | 4733.5251 | 5347:24 | 27:17 | 96.6748 | 96.333 | 5265.6696 | 644:47 | 91.2179 | 90.2307
6 | Ranebennur | 182 | 182 | 672:50 | 8349:14 | 3406:03 | 2244:51 | 5650:54 | 3747.8854 | 6323:44 | 34:45 | 95.8268 | 95.3299 | 4095.7701 | 540:06 | 92.5117 | 91.8166
7 | Sirsi | 53 | 53 | 131:13 | 4198:54 | 465:20 | 672:45 | 1138:05 | 23785:14 | 1269:18 | 23:57 | 97.1138 | 96.781 | 1166.0056 | 528:00 | 93.2003 | 92
8 | Dandeli | 21 | 21 | 33:10 | 1086:58 | 163:08 | 233:44 | 396:52 | 7316:10 | 430:02 | 20:29 | 97.4599 | 97.2476 | 8403:08 | 400:09 | 94.7214 | 93.9371
9 | Karwar | 32 | 32 | 265:41 | 3296:11 | 283:09 | 259:24 | 542:33 | 8685:44 | 808:14 | 25:15 | 97.7211 | 96.6052 | 11981:55 | 374:26 | 95.8874 | 94.3267
10 | Honnavar | 39 | 39 | 238:06 | 3583:09 | 354:47 | 270:00 | 624:47 | 10632:16 | 862:53 | 22:08 | 97.8468 | 97.0262 | 14215:25 | 364:30 | 95.8694 | 94.4773
11 | Belagavi | 135 | 135 | 182:14 | 4049:42 | 2496:05 | 1058:44 | 3554:49 | 2050.8264 | 3737:03 | 27:41 | 96.4608 | 96.2793 | 2219.5637 | 394:35 | 94.4759 | 94.0214
12 | Bailhongal | 190 | 190 | 474:17 | 8311:52 | 1611:39 | 1252:17 | 2863:56 | 2927.3208 | 3338:13 | 17:34 | 97.974 | 97.6385 | 3273.6486 | 413:31 | 94.3975 | 93.7346
13 | Ramdurg | 75 | 75 | 75:30 | 3381:22 | 1476:03 | 366:50 | 1842:53 | 1392.9965 | 1918:23 | 25:35 | 96.6973 | 96.562 | 1533.8868 | 490:51 | 93.2461 | 92.563
14 | Ghataprabha | 156 | 156 | 296:34 | 3802:49 | 889:55 | 651:25 | 1541:20 | 1356.8444 | 1837:54 | 11:47 | 98.672 | 98.4165 | 1515.2951 | 233:07 | 96.8372 | 96.4678
15 | Raibag | 168 | 168 | 163:50 | 4413:41 | 3657:31 | 488:12 | 4145:43 | 2377.3868 | 4309:33 | 25:39 | 96.6832 | 96.5521 | 2561.2903 | 365:54 | 94.8541 | 94.4561
16 | Athani | 185 | 185 | 556:46 | 6792:33 | 2519:11 | 523:11 | 3042:22 | 1765.9917 | 3599:08 | 19:27 | 97.7896 | 97.3851 | 2049.0146 | 265:49 | 96.5288 | 95.9725
17 | Chikkodi | 185 | 185 | 263:35 | 2401:06 | 908:17 | 528:17 | 1436:34 | 1185.9368 | 1700:09 | 9:11 | 98.9563 | 98.7648 | 1285.9826 | 166:50 | 97.6689 | 97.4723
18 | Vijayapur | 153 | 153 | 457:01 | 3607:44 | 1020:59 | 799:34 | 1820:33 | 2329.4201 | 2277:34 | 14:53 | 98.4007 | 97.9992 | 2479.7424 | 388:59 | 94.4636 | 94.1064
19 | Indi | 250 | 250 | 363:37 | 10086:17 | 1972:16 | 1659:55 | 3632:11 | 3641.9632 | 3995:48 | 15:59 | 98.0472 | 97.8517 | 4062.225 | 389:58 | 94.7026 | 94.0913
20 | B.Bagewadi | 134 | 134 | 292:45 | 4573:04 | 1176:08 | 921:39 | 2097:47 | 2153.1535 | 2390:32 | 17:50 | 97.8958 | 97.6022 | 2343.6979 | 419:46 | 94.157 | 93.6399
21 | Bagalkot | 181 | 181 | 454:12 | 5946:18 | 2201:05 | 1564:55 | 3766:00 | 3188.6931 | 4220:12 | 23:19 | 97.2034 | 96.8661 | 3436.4556 | 455:40 | 93.5938 | 93.096
22 | Jamkhandi | 205 | 205 | 197:25 | 4172:14 | 1327:27 | 642:58 | 1970:25 | 1580.7243 | 2167:50 | 10:34 | 98.7081 | 98.5787 | 1754.5674 | 205:25 | 97.1961 | 96.8877
23 | Mudhol | 192 | 192 | 140:35 | 4448:00 | 1323:18 | 646:08 | 1969:26 | 1685.2181 | 2110:01 | 10:59 | 98.6213 | 98.5229 | 1870.5514 | 233:49 | 96.8083 | 96.4573
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of January-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the month of January-21 |  |  |  | Reliability for cumulative period from April-20 to January-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 284:25 | 2262:40 | 938:53 | 535:57 | 1474:50 | 23604:06 | 1759:15 | 39:06 | 95.5949 | 94.7454 | 1077.7819 | 574:49 | 92.8576 | 92.173
2 | Dharwad Rural | 82 | 82 | 191:48 | 2037:41 | 1767:44 | 1933:59 | 3701:43 | 1795.3104 | 3893:31 | 47:29 | 93.9324 | 93.618 | 1880.2139 | 550:18 | 92.8451 | 92.5067
3 | Gadag | 93 | 93 | 83:55 | 2242:57 | 1223:37 | 1603:29 | 2827:06 | 2017.1236 | 2911:01 | 31:18 | 95.9141 | 95.7928 | 2110.5799 | 544:40 | 92.9119 | 92.5835
4 | Ron | 53 | 53 | 99:10 | 2198:51 | 439:40 | 505:45 | 945:25 | 22386:31 | 1044:35 | 19:43 | 97.6024 | 97.3509 | 1006.7757 | 455:54 | 94.2485 | 93.7922
5 | Haveri | 196 | 196 | 986:20 | 13757:48 | 2938:15 | 4161:16 | 7099:31 | 5029.3383 | 8085:51 | 41:15 | 95.1314 | 94.4551 | 5602.58 | 686:02 | 91.6144 | 90.6586
6 | Ranebennur | 182 | 182 | 754:20 | 9103:34 | 3174:02 | 3499:19 | 6673:21 | 4025.9417 | 7427:41 | 40:49 | 95.0717 | 94.5146 | 4405.2569 | 580:55 | 92.7711 | 92.09
7 | Sirsi | 53 | 53 | 103:46 | 4302:40 | 429:43 | 1258:15 | 1687:58 | 1061.3833 | 1791:44 | 33:48 | 95.7193 | 95.4561 | 1240.6611 | 561:49 | 93.4555 | 92.3501
8 | Dandeli | 21 | 21 | 84:31 | 1171:29 | 270:16 | 231:02 | 501:18 | 7817:28 | 585:49 | 27:54 | 96.7915 | 96.2505 | 8988:57 | 428:03 | 94.9311 | 94.1715
9 | Karwar | 33 | 33 | 150:22 | 3446:33 | 358:46 | 359:58 | 718:44 | 9404:28 | 869:06 | 26:20 | 97.0726 | 96.4602 | 12851:01 | 389:25 | 96.1195 | 94.6974
10 | Honnavar | 40 | 40 | 375:00 | 3958:09 | 333:28 | 376:54 | 710:22 | 11342:38 | 1085:22 | 27:08 | 97.613 | 96.3529 | 15300:47 | 382:31 | 96.1388 | 94.7914
11 | Belagavi | 135 | 135 | 416:11 | 4465:53 | 2198:13 | 1214:32 | 3412:45 | 2193.0243 | 3828:56 | 28:22 | 96.6022 | 96.1878 | 2379.1025 | 422:57 | 94.6913 | 94.2409
12 | Bailhongal | 190 | 190 | 891:29 | 9203:21 | 1931:57 | 2937:42 | 4869:39 | 3130.2229 | 5761:08 | 30:19 | 96.5551 | 95.9245 | 3513.6958 | 443:50 | 94.6161 | 93.9565
13 | Ramdurg | 76 | 76 | 299:56 | 3681:18 | 1278:47 | 1298:32 | 2577:19 | 1500.3847 | 2877:15 | 37:52 | 95.4419 | 94.9115 | 1653.7722 | 522:15 | 93.5484 | 92.8888
14 | Ghataprabha | 157 | 157 | 58:25 | 3861:14 | 983:54 | 943:03 | 1926:57 | 1437.134 | 1985:22 | 12:39 | 98.3503 | 98.3003 | 1598.0187 | 244:17 | 97.0086 | 96.6737
15 | Raibag | 169 | 169 | 254:11 | 4667:52 | 3575:43 | 922:33 | 4498:16 | 2564.8146 | 4752:27 | 28:07 | 96.4225 | 96.2203 | 2759.309 | 391:51 | 95.0404 | 94.6643
16 | Athani | 185 | 185 | 325:11 | 7117:44 | 2591:08 | 506:17 | 3097:25 | 1895.0507 | 3422:36 | 18:30 | 97.7496 | 97.5134 | 2191.6229 | 284:19 | 96.6524 | 96.1286
17 | Chikkodi | 186 | 186 | 165:45 | 2566:51 | 1230:25 | 1187:24 | 2417:49 | 1286.6792 | 2583:34 | 13:53 | 98.2528 | 98.133 | 1393.6312 | 179:49 | 97.7393 | 97.5514
18 | Vijayapur | 153 | 153 | 289:03 | 3896:47 | 1128:03 | 1317:13 | 2445:16 | 2431.3062 | 2734:19 | 17:52 | 97.8519 | 97.5979 | 2593.6722 | 406:51 | 94.8069 | 94.4601
19 | Indi | 248 | 248 | 303:37 | 10389:54 | 2092:18 | 1416:48 | 3509:06 | 3788.1757 | 3812:43 | 15:22 | 98.0982 | 97.9336 | 4221.0882 | 408:30 | 95.0082 | 94.4377
20 | B.Bagewadi | 135 | 135 | 112:56 | 4686:00 | 1137:48 | 1022:35 | 2160:23 | 2243.1694 | 2273:19 | 16:50 | 97.8491 | 97.7366 | 2438.4194 | 433:30 | 94.5699 | 94.0973
21 | Bagalkot | 180 | 180 | 362:51 | 6309:09 | 2103:04 | 1980:00 | 4083:04 | 3358.8208 | 4445:55 | 24:42 | 96.9511 | 96.6802 | 3621.7021 | 482:54 | 93.9019 | 93.4247
22 | Jamkhandi | 205 | 205 | 605:47 | 4778:01 | 1320:12 | 865:22 | 2185:34 | 1671.7896 | 2791:21 | 13:37 | 98.567 | 98.1698 | 1870.8736 | 219:02 | 97.3349 | 97.0176
23 | Mudhol | 192 | 192 | 233:35 | 4681:35 | 1329:39 | 1124:27 | 2454:06 | 1787.4722 | 2687:41 | 14:00 | 98.282 | 98.1185 | 1982.5382 | 247:49 | 96.9576 | 96.6256
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of FEBRUARY-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the month of February-21 |  |  |  | Reliability for cumulative period from April-20 to February-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 285:55 | 2548:35 | 577:26 | 746:57 | 1324:23 | 1038.6868 | 1610:18 | 35:47 | 95.6204 | 94.6749 | 1144.8778 | 610:36 | 93.0892 | 92.3827
2 | Dharwad Rural | 82 | 82 | 146:04 | 2183:45 | 1569:00 | 1181:10 | 2750:10 | 1909.9007 | 2896:14 | 35:19 | 95.0091 | 94.7441 | 2000.8903 | 585:38 | 93.0265 | 92.6943
3 | Gadag | 93 | 93 | 149:15 | 2392:12 | 1040:21 | 884:55 | 1925:16 | 2097.3431 | 2074:31 | 22:18 | 96.9194 | 96.6806 | 2197.0181 | 566:58 | 93.2479 | 92.927
4 | Ron | 53 | 53 | 130:25 | 2329:16 | 553:40 | 335:45 | 889:25 | 23275:56 | 1019:50 | 19:15 | 97.5028 | 97.1366 | 1049.2687 | 475:08 | 94.5214 | 94.0726
5 | Haveri | 196 | 196 | 1581:47 | 15339:35 | 2752:32 | 3411:52 | 6164:24 | 5286.1883 | 7746:11 | 39:31 | 95.3198 | 94.1188 | 5925.3376 | 725:33 | 91.925 | 90.9487
6 | Ranebennur | 182 | 182 | 726:42 | 9830:16 | 2922:49 | 3128:28 | 6051:17 | 4278.0785 | 6777:59 | 37:14 | 95.0523 | 94.4581 | 4687.6729 | 618:09 | 92.9623 | 92.2885
7 | Sirsi | 53 | 53 | 358:31 | 4661:11 | 439:11 | 1099:19 | 1538:30 | 1125.4875 | 1897:01 | 35:48 | 95.6803 | 94.6737 | 1319.7035 | 597:36 | 93.642 | 92.5449
8 | Dandeli | 21 | 21 | 47:18 | 1218:47 | 332:00 | 212:17 | 544:17 | 8361:45 | 591:35 | 28:10 | 96.1431 | 95.8079 | 9580:32 | 456:13 | 95.0327 | 94.3087
9 | Karwar | 33 | 33 | 205:48 | 3652:21 | 255:49 | 288:18 | 544:07 | 9948:35 | 749:55 | 22:43 | 97.5464 | 96.6183 | 13600:56 | 412:09 | 96.2391 | 94.8584
10 | Honnavar | 40 | 40 | 220:52 | 4179:01 | 326:36 | 245:05 | 571:41 | 11914:19 | 792:33 | 19:49 | 97.8732 | 97.0515 | 16093:20 | 402:20 | 96.2842 | 94.9809
11 | Belagavi | 135 | 135 | 342:59 | 4808:52 | 2722:44 | 970:57 | 3693:41 | 2346.9278 | 4036:40 | 29:54 | 95.9285 | 95.5504 | 2547.297 | 452:51 | 94.795 | 94.3506
12 | Bailhongal | 190 | 190 | 913:31 | 10116:52 | 2340:31 | 1562:22 | 3902:53 | 3292.8431 | 4816:24 | 25:21 | 96.9432 | 96.2278 | 3714.3792 | 469:11 | 94.8112 | 94.1469
13 | Ramdurg | 76 | 76 | 194:18 | 3875:36 | 1015:20 | 899:24 | 1914:44 | 1580.1653 | 2109:02 | 27:45 | 96.2509 | 95.8705 | 1741.6486 | 550:00 | 93.775 | 93.1388
14 | Ghataprabha | 158 | 158 | 269:15 | 4130:29 | 1078:10 | 809:16 | 1887:26 | 1515.7771 | 2156:41 | 13:39 | 98.2224 | 97.9688 | 1687.8806 | 256:23 | 97.1277 | 96.8016
15 | Raibag | 169 | 169 | 571:33 | 5239:25 | 3654:55 | 671:04 | 4325:59 | 2745.0639 | 4897:32 | 28:59 | 96.1908 | 95.6876 | 2963.3729 | 420:50 | 95.1368 | 94.7501
16 | Athani | 185 | 185 | 381:05 | 7498:49 | 2353:34 | 584:27 | 2938:01 | 2017.4681 | 3319:06 | 17:56 | 97.6367 | 97.3302 | 2329.9188 | 302:16 | 96.735 | 96.2293
17 | Chikkodi | 186 | 186 | 183:30 | 2750:21 | 1366:29 | 602:21 | 1968:50 | 1368.7139 | 2152:20 | 11:34 | 98.4248 | 98.278 | 1483.3118 | 191:24 | 97.7968 | 97.6123
18 | Vijayapur | 153 | 153 | 470:31 | 4367:18 | 1235:58 | 670:20 | 1906:18 | 2510.7354 | 2376:49 | 15:32 | 98.1459 | 97.6883 | 2692.7063 | 422:23 | 95.0868 | 94.7307
19 | Indi | 249 | 249 | 375:22 | 10765:16 | 2115:25 | 1386:34 | 3501:59 | 3934.0917 | 3877:21 | 15:34 | 97.9071 | 97.6828 | 4382.6444 | 422:25 | 95.2696 | 94.7302
20 | B.Bagewadi | 135 | 135 | 453:43 | 5139:43 | 1597:55 | 924:40 | 2522:35 | 2348.2771 | 2976:18 | 22:03 | 97.2194 | 96.7192 | 2562.4319 | 455:33 | 94.792 | 94.3171
21 | Bagalkot | 181 | 181 | 411:51 | 6721:00 | 2150:35 | 1353:26 | 3504:01 | 3504.8215 | 3915:52 | 21:38 | 97.1192 | 96.7806 | 3784.8632 | 501:52 | 94.2025 | 93.7393
22 | Jamkhandi | 206 | 206 | 154:28 | 4932:29 | 1230:24 | 767:07 | 1997:31 | 1755.0194 | 2151:59 | 10:27 | 98.557 | 98.4455 | 1960.5396 | 228:25 | 97.4492 | 97.1505
23 | Mudhol | 192 | 192 | 184:37 | 4866:12 | 1263:06 | 599:59 | 1863:05 | 1865.1007 | 2047:42 | 10:40 | 98.556 | 98.4129 | 2067.859 | 258:29 | 97.0916 | 96.7754
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of MARCH-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 20-21 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the month of March-21 |  |  |  | Reliability for cumulative period from April-20 to March-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 20-21 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 288:50 | 2837:25 | 727:03 | 558:57 | 1286:00 | 1092.2701 | 1574:50 | 35:00 | 96.1589 | 95.2962 | 1210.4958 | 645:36 | 93.35 | 92.6302
2 | Dharwad Rural | 82 | 82 | 347:05 | 2530:50 | 1604:51 | 951:13 | 2556:04 | 2016.4035 | 2903:09 | 35:24 | 95.8103 | 95.2414 | 2121.8549 | 621:02 | 93.2629 | 92.9106
3 | Gadag | 94 | 94 | 163:15 | 2555:27 | 1030:59 | 853:44 | 1884:43 | 2175.8729 | 2047:58 | 21:47 | 97.3051 | 97.0717 | 2282.35 | 582:44 | 93.6582 | 93.3479
4 | Ron | 53 | 53 | 316:45 | 2646:01 | 681:56 | 1017:46 | 1699:42 | 1040.6514 | 2016:27 | 38:03 | 95.6895 | 94.8863 | 1133.2875 | 513:11 | 94.6206 | 94.1417
5 | Haveri | 197 | 197 | 1726:45 | 17066:20 | 2954:34 | 2763:02 | 5717:36 | 5524.4216 | 7444:21 | 37:47 | 96.099 | 94.9209 | 6235.5189 | 759:39 | 92.3171 | 91.3281
6 | Ranebennur | 182 | 182 | 1101:38 | 10931:54 | 2813:39 | 2593:21 | 5407:00 | 4503.3701 | 6508:38 | 35:46 | 96.0069 | 95.1933 | 4958.866 | 653:55 | 93.2209 | 92.5352
7 | Sirsi | 54 | 54 | 336:03 | 4997:14 | 635:33 | 1077:41 | 1713:14 | 1196.8722 | 2049:17 | 37:57 | 95.7357 | 94.8992 | 1405.0903 | 624:29 | 93.9276 | 92.8712
8 | Dandeli | 22 | 22 | 46:22 | 1265:09 | 365:48 | 274:28 | 640:16 | 9002:01 | 686:38 | 31:13 | 96.0883 | 95.805 | 10267:10 | 466:41 | 95.329 | 94.6725
9 | Karwar | 33 | 33 | 577:44 | 4230:05 | 329:21 | 195:43 | 525:04 | 10473:39 | 1102:48 | 33:25 | 97.8614 | 95.5083 | 14703:44 | 445:34 | 96.3769 | 94.9136
10 | Honnavar | 40 | 40 | 485:13 | 4664:14 | 466:01 | 216:04 | 682:05 | 12596:24 | 1167:18 | 29:11 | 97.7081 | 96.0776 | 17260:38 | 431:31 | 96.4051 | 95.074
11 | Belagavi | 135 | 135 | 355:48 | 5164:40 | 3028:54 | 1032:58 | 4061:52 | 2516.1722 | 4417:40 | 32:43 | 95.9559 | 95.6017 | 2731.3664 | 485:35 | 94.8936 | 94.4569
12 | Bailhongal | 191 | 191 | 1804:51 | 11921:43 | 4131:49 | 1518:46 | 5650:35 | 3528.284 | 7455:26 | 39:02 | 96.0236 | 94.7535 | 4025.0222 | 505:46 | 94.939 | 94.2265
13 | Ramdurg | 76 | 76 | 319:05 | 4194:41 | 1270:35 | 835:45 | 2106:20 | 1667.9292 | 2425:25 | 31:55 | 96.2749 | 95.7106 | 1842.7076 | 581:54 | 93.9873 | 93.3572
14 | Ghataprabha | 159 | 159 | 178:05 | 4308:34 | 1429:26 | 638:35 | 2068:01 | 1601.9444 | 2246:06 | 14:08 | 98.2518 | 98.1013 | 1781.4681 | 268:54 | 97.2397 | 96.9304
15 | Raibag | 169 | 169 | 447:50 | 5687:15 | 4926:49 | 890:37 | 5817:26 | 2987.4569 | 6265:16 | 37:04 | 95.3733 | 95.0171 | 3224.4257 | 457:54 | 95.1569 | 94.7728
16 | Athani | 197 | 197 | 750:04 | 8248:53 | 2130:01 | 589:12 | 2719:13 | 2130.7688 | 3469:17 | 17:37 | 98.1447 | 97.633 | 2474.4722 | 301:28 | 97.0367 | 96.5587
17 | Chikkodi | 186 | 186 | 428:20 | 3178:41 | 1738:00 | 1201:07 | 2939:07 | 1491.1771 | 3367:27 | 18:06 | 97.8761 | 97.5666 | 1623.6222 | 209:30 | 97.8035 | 97.6085
18 | Vijayapur | 158 | 158 | 1226:24 | 5593:42 | 1365:03 | 1103:50 | 2468:53 | 2613.6056 | 3695:17 | 23:23 | 97.8998 | 96.8565 | 2846.6764 | 432:24 | 95.468 | 95.0639
19 | Indi | 249 | 249 | 1473:24 | 12238:40 | 2617:06 | 1409:47 | 4026:53 | 4101.8785 | 5500:17 | 22:05 | 97.8263 | 97.031 | 4611.8229 | 444:31 | 95.4867 | 94.9257
20 | B.Bagewadi | 138 | 138 | 1732:14 | 6871:57 | 1552:37 | 1020:27 | 2573:04 | 2455.4882 | 4305:18 | 31:12 | 97.4939 | 95.8067 | 2741.8194 | 476:50 | 95.1251 | 94.5566
21 | Bagalkot | 181 | 181 | 851:59 | 7572:59 | 2507:53 | 1469:28 | 3977:21 | 3670.5444 | 4829:20 | 26:41 | 97.0465 | 96.4138 | 3986.0854 | 528:33 | 94.444 | 93.9664
22 | Jamkhandi | 206 | 206 | 217:51 | 5150:20 | 1973:27 | 689:23 | 2662:50 | 1865.9708 | 2880:41 | 13:59 | 98.2626 | 98.1204 | 2080.5681 | 242:24 | 97.5183 | 97.2329
23 | Mudhol | 192 | 192 | 216:26 | 5082:38 | 1892:38 | 985:06 | 2877:44 | 1985.0062 | 3094:10 | 16:07 | 97.9855 | 97.8339 | 2196.7826 | 274:36 | 97.1675 | 96.8653
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]