## DHQ
Annex-1 | [13 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of April-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2021 |  |  |  | Reliability for cumulative period from Apr-21 to Apr-21
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 2:37 | 2:37 | 518:43 | 328:30 | 847:13 | 847:13 | 849:50 | 26:33 | 96.3228 | 96.3115 | 849:50 | 26:33 | 96.3228 | 96.3115
2 | Gadag | 16 | 16 | 27:11 | 27:11 | 94:39 | 71:11 | 165:50 | 165:50 | 193:01 | 12:04 | 98.5605 | 98.3245 | 193:01 | 12:04 | 98.5605 | 98.3245
3 | Haveri | 7 | 7 | 31:00 | 31:00 | 23:35 | 30:25 | 54:00 | 54:00 | 85:00 | 12:09 | 98.9286 | 98.3135 | 85:00 | 12:09 | 98.9286 | 98.3135
4 | Karwar | 10 | 10 | 96:28 | 96:28 | 70:30 | 61:58 | 132:28 | 132:28 | 228:56 | 22:54 | 98.1602 | 96.8204 | 228:56 | 22:54 | 98.1602 | 96.8204
5 | Belagavi | 75 | 75 | 66:42 | 66:42 | 456:46 | 144:09 | 600:55 | 600:55 | 667:37 | 8:54 | 98.8872 | 98.7637 | 667:37 | 8:54 | 98.8872 | 98.7637
6 | Vijayapur | 37 | 37 | 59:01 | 59:01 | 202:03 | 255:31 | 457:34 | 457:34 | 516:35 | 13:58 | 98.2824 | 98.0609 | 516:35 | 13:58 | 98.2824 | 98.0609
7 | Bagalkot | 11 | 11 | 51:28 | 51:28 | 61:03 | 63:37 | 124:40 | 124:40 | 176:08 | 16:01 | 98.4259 | 97.7761 | 176:08 | 16:01 | 98.4259 | 97.7761
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of May-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2021 |  |  |  | Reliability for cumulative period from Apr-21 to May-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 0:00 | 2:37 | 529:31 | 291:43 | 821:14 | 1668:27 | 821:14 | 25:40 | 96.5506 | 96.5506 | 1671:04 | 52:13 | 96.4386 | 96.433
2 | Gadag | 16 | 16 | 0:00 | 27:11 | 81:31 | 93:30 | 175:01 | 340:51 | 175:01 | 10:56 | 98.5298 | 98.5298 | 368:02 | 23:00 | 98.5449 | 98.4288
3 | Haveri | 7 | 7 | 0:00 | 31:00 | 67:30 | 83:05 | 150:35 | 204:35 | 150:35 | 21:31 | 97.1086 | 97.1086 | 235:35 | 33:39 | 98.0037 | 97.7012
4 | Karwar | 10 | 10 | 192:00 | 288:28 | 186:50 | 170:03 | 356:53 | 489:21 | 548:53 | 54:53 | 95.2032 | 92.6225 | 777:49 | 77:47 | 96.6574 | 94.687
5 | Belagavi | 75 | 75 | 142:26 | 209:08 | 389:36 | 153:04 | 542:40 | 1143:35 | 685:06 | 9:08 | 99.0275 | 98.7722 | 1352:43 | 18:02 | 98.9585 | 98.768
6 | Vijayapur | 37 | 37 | 19:36 | 78:37 | 178:41 | 319:55 | 498:36 | 956:10 | 518:12 | 14:00 | 98.1888 | 98.1176 | 1034:47 | 27:58 | 98.2348 | 98.0897
7 | Bagalkot | 11 | 11 | 0:40 | 52:08 | 54:22 | 58:02 | 112:24 | 237:04 | 113:04 | 10:17 | 98.6266 | 98.6184 | 289:12 | 26:17 | 98.5279 | 98.2042
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of June-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2021 |  |  |  | Reliability for cumulative period from Apr-21 to June-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 14:30 | 17:07 | 542:48 | 301:13 | 844:01 | 2512:28 | 858:31 | 26:50 | 96.3367 | 96.2738 | 2529:35 | 79:03 | 96.405 | 96.3805
2 | Gadag | 16 | 16 | 7:00 | 34:11 | 80:26 | 96:55 | 177:21 | 518:12 | 184:21 | 11:31 | 98.4605 | 98.3997 | 552:23 | 34:31 | 98.5171 | 98.4192
3 | Haveri | 7 | 7 | 0:00 | 31:00 | 78:40 | 67:25 | 146:05 | 350:40 | 146:05 | 20:52 | 97.1015 | 97.1015 | 381:40 | 54:31 | 97.7063 | 97.5035
4 | Karwar | 10 | 10 | 73:44 | 362:12 | 145:33 | 155:14 | 300:47 | 790:08 | 374:31 | 37:27 | 95.8225 | 94.7984 | 1152:20 | 115:14 | 96.3822 | 94.7237
5 | Belagavi | 76 | 76 | 112:56 | 322:04 | 669:26 | 116:43 | 786:09 | 1929:44 | 899:05 | 11:50 | 98.5633 | 98.3569 | 2251:48 | 29:38 | 98.8374 | 98.6434
6 | Vijayapur | 37 | 37 | 12:09 | 90:46 | 213:49 | 192:50 | 406:39 | 1362:49 | 418:48 | 11:19 | 98.4735 | 98.4279 | 1453:35 | 39:17 | 98.3135 | 98.2012
7 | Bagalkot | 11 | 11 | 4:00 | 56:08 | 105:03 | 69:45 | 174:48 | 411:52 | 178:48 | 16:15 | 97.7929 | 97.7424 | 468:00 | 42:33 | 98.2856 | 98.0519
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of July-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2021 |  |  |  | Reliability for cumulative period from Apr-21 to July-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 10:25 | 27:32 | 582:33 | 366:57 | 949:30 | 3461:58 | 959:55 | 30:00 | 96.0118 | 95.9681 | 3489:30 | 109:03 | 96.3051 | 96.2757
2 | Gadag | 16 | 16 | 25:33 | 59:44 | 89:18 | 45:24 | 134:42 | 652:54 | 160:15 | 10:01 | 98.8684 | 98.6538 | 712:38 | 44:32 | 98.6063 | 98.4788
3 | Haveri | 7 | 7 | 0:00 | 31:00 | 41:45 | 22:20 | 64:05 | 414:45 | 64:05 | 9:09 | 98.7695 | 98.7695 | 445:45 | 63:41 | 97.9764 | 97.8252
4 | Karwar | 10 | 10 | 85:08 | 447:20 | 42:49 | 66:06 | 108:55 | 899:03 | 194:03 | 19:24 | 98.5361 | 97.3918 | 1346:23 | 134:38 | 96.9295 | 95.4017
5 | Belagavi | 76 | 76 | 215:04 | 537:08 | 307:53 | 143:10 | 451:03 | 2380:47 | 666:07 | 8:46 | 99.2023 | 98.8219 | 2917:55 | 38:24 | 98.9301 | 98.6887
6 | Vijayapur | 37 | 37 | 24:40 | 115:26 | 304:30 | 156:30 | 461:00 | 1823:49 | 485:40 | 13:08 | 98.3253 | 98.2357 | 1939:15 | 52:25 | 98.3165 | 98.21
7 | Bagalkot | 11 | 11 | 20:30 | 76:38 | 83:37 | 46:02 | 129:39 | 541:31 | 150:09 | 13:39 | 98.4158 | 98.1653 | 618:09 | 56:12 | 98.3187 | 98.0808
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of August-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of August-2021 |  |  |  | Reliability for cumulative period from Apr-21 to August-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 9:15 | 36:47 | 441:57 | 130:42 | 572:39 | 4034:37 | 581:54 | 18:11 | 97.5947 | 97.5559 | 4071:24 | 127:14 | 96.5664 | 96.5351
2 | Gadag | 16 | 16 | 0:00 | 59:44 | 74:42 | 29:29 | 104:11 | 757:05 | 104:11 | 6:31 | 99.1248 | 99.1248 | 816:49 | 51:03 | 98.7114 | 98.6097
3 | Haveri | 7 | 7 | 45:10 | 76:10 | 27:00 | 15:50 | 42:50 | 457:35 | 88:00 | 12:34 | 99.1775 | 98.3103 | 533:45 | 76:15 | 98.2198 | 97.9235
4 | Karwar | 10 | 10 | 26:42 | 474:02 | 72:09 | 61:52 | 134:01 | 1033:04 | 160:43 | 16:04 | 98.1987 | 97.8398 | 1507:06 | 150:43 | 97.1866 | 95.8957
5 | Belagavi | 78 | 78 | 10:42 | 547:50 | 255:21 | 122:38 | 377:59 | 2758:46 | 388:41 | 4:59 | 99.3487 | 99.3302 | 3306:36 | 42:24 | 99.0368 | 98.8455
6 | Vijayapur | 37 | 37 | 0:25 | 115:51 | 249:14 | 200:28 | 449:42 | 2273:31 | 450:07 | 12:10 | 98.3664 | 98.3649 | 2389:22 | 64:35 | 98.3266 | 98.2414
7 | Bagalkot | 11 | 11 | 0:00 | 76:38 | 67:05 | 35:49 | 102:54 | 644:25 | 102:54 | 9:21 | 98.7427 | 98.7427 | 721:03 | 65:33 | 98.4046 | 98.2149
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]

## URBAN
Annex-II | [13 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of April-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2021 |  |  |  | Reliability for cumulative period from Apr-21 to Apr-21
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 77 | 77 | 9:10 | 9:10 | 313:25 | 525:48 | 839:13 | 839:13 | 848:23 | 11:01 | 98.4863 | 98.4697 | 848:23 | 11:01 | 98.4863 | 98.4697
2 | Dharwad(R) | 19 | 19 | 9:45 | 9:45 | 259:38 | 242:11 | 501:49 | 501:49 | 511:34 | 26:55 | 96.3317 | 96.2605 | 511:34 | 26:55 | 96.3317 | 96.2605
3 | Kundagol | 1 | 1 | 46:10 | 46:10 | 6:15 | 12:45 | 19:00 | 19:00 | 65:10 | 65:10 | 97.3611 | 90.9491 | 65:10 | 65:10 | 97.3611 | 90.9491
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 5:16 | 7:36 | 12:52 | 12:52 | 12:52 | 12:52 | 98.213 | 98.213 | 12:52 | 12:52 | 98.213 | 98.213
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 13:18 | 4:27 | 17:45 | 17:45 | 17:45 | 17:45 | 97.5347 | 97.5347 | 17:45 | 17:45 | 97.5347 | 97.5347
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 73:35 | 53:10 | 126:45 | 126:45 | 126:45 | 63:22 | 91.1979 | 91.1979 | 126:45 | 63:22 | 91.1979 | 91.1979
7 | Alnavar | 1 | 1 | 6:10 | 6:10 | 10:55 | 6:05 | 17:00 | 17:00 | 23:10 | 23:10 | 97.6389 | 96.7824 | 23:10 | 23:10 | 97.6389 | 96.7824
8 | Naragund | 2 | 2 | 9:20 | 9:20 | 32:50 | 25:45 | 58:35 | 58:35 | 67:55 | 33:58 | 95.9317 | 95.2836 | 67:55 | 33:58 | 95.9317 | 95.2836
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 22:00 | 31:35 | 53:35 | 53:35 | 53:35 | 13:24 | 98.1395 | 98.1395 | 53:35 | 13:24 | 98.1395 | 98.1395
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 44:47 | 49:57 | 94:44 | 94:44 | 94:44 | 23:41 | 96.7106 | 96.7106 | 94:44 | 23:41 | 96.7106 | 96.7106
11 | Naregal | 1 | 1 | 0:00 | 0:00 | 9:05 | 10:15 | 19:20 | 19:20 | 19:20 | 19:20 | 97.3148 | 97.3148 | 19:20 | 19:20 | 97.3148 | 97.3148
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 34:10 | 21:20 | 55:30 | 55:30 | 55:30 | 27:45 | 96.1458 | 96.1458 | 55:30 | 27:45 | 96.1458 | 96.1458
13 | Ron | 3 | 3 | 0:00 | 0:00 | 34:55 | 31:35 | 66:30 | 66:30 | 66:30 | 22:10 | 96.9213 | 96.9213 | 66:30 | 22:10 | 96.9213 | 96.9213
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 11:15 | 15:55 | 27:10 | 27:10 | 27:10 | 9:03 | 98.7423 | 98.7423 | 27:10 | 9:03 | 98.7423 | 98.7423
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 19:35 | 27:28 | 47:03 | 47:03 | 47:03 | 47:03 | 93.4653 | 93.4653 | 47:03 | 47:03 | 93.4653 | 93.4653
16 | G.C.T.M | 1 | 1 | 9:10 | 9:10 | 7:40 | 4:00 | 11:40 | 11:40 | 20:50 | 20:50 | 98.3796 | 97.1065 | 20:50 | 20:50 | 98.3796 | 97.1065
17 | F.C.S.M | 2 | 2 | 9:00 | 9:00 | 5:35 | 4:50 | 10:25 | 10:25 | 19:25 | 9:42 | 99.2766 | 98.6516 | 19:25 | 9:42 | 99.2766 | 98.6516
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 9:46 | 2:25 | 12:11 | 12:11 | 12:11 | 12:11 | 98.3079 | 98.3079 | 12:11 | 12:11 | 98.3079 | 98.3079
19 | Hole-Alur | 1 | 1 | 20:40 | 20:40 | 20:15 | 5:15 | 25:30 | 25:30 | 46:10 | 46:10 | 96.4583 | 93.588 | 46:10 | 46:10 | 96.4583 | 93.588
20 | Savanur | 2 | 2 | 2:30 | 2:30 | 16:45 | 15:55 | 32:40 | 32:40 | 35:10 | 17:35 | 97.7315 | 97.5579 | 35:10 | 17:35 | 97.7315 | 97.5579
21 | Shiggaon | 2 | 2 | 13:35 | 13:35 | 75:50 | 26:20 | 102:10 | 102:10 | 115:45 | 57:52 | 92.9051 | 91.9618 | 115:45 | 57:52 | 92.9051 | 91.9618
22 | Bankapur | 1 | 1 | 7:15 | 7:15 | 11:10 | 7:25 | 18:35 | 18:35 | 25:50 | 25:50 | 97.419 | 96.412 | 25:50 | 25:50 | 97.419 | 96.412
23 | Hangal | 2 | 2 | 32:40 | 32:40 | 34:30 | 22:00 | 56:30 | 56:30 | 89:10 | 44:35 | 96.0764 | 93.8079 | 89:10 | 44:35 | 96.0764 | 93.8079
24 | Ranebennur | 16 | 16 | 40:55 | 40:55 | 76:16 | 38:57 | 115:13 | 115:13 | 156:08 | 9:45 | 98.9999 | 98.6447 | 156:08 | 9:45 | 98.9999 | 98.6447
25 | Halageri | 2 | 2 | 54:20 | 54:20 | 26:50 | 2:50 | 29:40 | 29:40 | 84:00 | 42:00 | 97.9398 | 94.1667 | 84:00 | 42:00 | 97.9398 | 94.1667
26 | Tuminakatti | 2 | 2 | 2:00 | 2:00 | 33:00 | 5:05 | 38:05 | 38:05 | 40:05 | 20:02 | 97.3553 | 97.2164 | 40:05 | 20:02 | 97.3553 | 97.2164
27 | Kahanderayanahalli | 1 | 1 | 1:00 | 1:00 | 26:40 | 50:10 | 76:50 | 76:50 | 77:50 | 77:50 | 89.3287 | 89.1898 | 77:50 | 77:50 | 89.3287 | 89.1898
28 | Rattihalli | 1 | 1 | 2:40 | 2:40 | 16:10 | 9:15 | 25:25 | 25:25 | 28:05 | 28:05 | 96.4699 | 96.0995 | 28:05 | 28:05 | 96.4699 | 96.0995
29 | Hirekerur | 2 | 2 | 30:20 | 30:20 | 35:50 | 14:50 | 50:40 | 50:40 | 81:00 | 40:30 | 96.4815 | 94.375 | 81:00 | 40:30 | 96.4815 | 94.375
30 | Byadagi | 8 | 8 | 30:10 | 30:10 | 153:45 | 120:00 | 273:45 | 273:45 | 303:55 | 37:59 | 95.2474 | 94.7237 | 303:55 | 37:59 | 95.2474 | 94.7237
31 | Sirsi | 5 | 5 | 4:35 | 4:35 | 28:11 | 35:14 | 63:25 | 63:25 | 68:00 | 13:36 | 98.2384 | 98.1111 | 68:00 | 13:36 | 98.2384 | 98.1111
32 | Yellapur | 3 | 3 | 12:03 | 12:03 | 15:00 | 9:50 | 24:50 | 24:50 | 36:53 | 12:18 | 98.8503 | 98.2924 | 36:53 | 12:18 | 98.8503 | 98.2924
33 | Mundagod | 3 | 3 | 0:00 | 0:00 | 49:30 | 46:00 | 95:30 | 95:30 | 95:30 | 31:50 | 95.5787 | 95.5787 | 95:30 | 31:50 | 95.5787 | 95.5787
34 | Siddapur | 2 | 2 | 4:10 | 4:10 | 4:15 | 20:30 | 24:45 | 24:45 | 28:55 | 14:28 | 98.2812 | 97.9919 | 28:55 | 14:28 | 98.2812 | 97.9919
35 | Dandeli | 8 | 8 | 38:40 | 38:40 | 33:30 | 68:48 | 102:18 | 102:18 | 140:58 | 17:37 | 98.224 | 97.5527 | 140:58 | 17:37 | 98.224 | 97.5527
36 | Haliyal | 3 | 3 | 0:19 | 0:19 | 38:20 | 26:04 | 64:24 | 64:24 | 64:43 | 21:34 | 97.0185 | 97.0039 | 64:43 | 21:34 | 97.0185 | 97.0039
37 | Ankola | 3 | 3 | 16:23 | 16:23 | 14:49 | 5:40 | 20:29 | 20:29 | 36:52 | 12:17 | 99.0517 | 98.2932 | 36:52 | 12:17 | 99.0517 | 98.2932
38 | Kumta | 3 | 3 | 3:30 | 3:30 | 16:03 | 9:21 | 25:24 | 25:24 | 28:54 | 9:38 | 98.8241 | 98.662 | 28:54 | 9:38 | 98.8241 | 98.662
39 | Gokarna | 1 | 1 | 4:57 | 4:57 | 1:25 | 1:25 | 2:50 | 2:50 | 7:47 | 7:47 | 99.6065 | 98.919 | 7:47 | 7:47 | 99.6065 | 98.919
40 | Kasarkod | 1 | 1 | 38:40 | 38:40 | 6:55 | 7:45 | 14:40 | 14:40 | 53:20 | 53:20 | 97.963 | 92.5926 | 53:20 | 53:20 | 97.963 | 92.5926
41 | Honnavar | 3 | 3 | 13:15 | 13:15 | 10:03 | 13:17 | 23:20 | 23:20 | 36:35 | 12:12 | 98.9198 | 98.3063 | 36:35 | 12:12 | 98.9198 | 98.3063
42 | Murdeshwar | 4 | 4 | 20:36 | 20:36 | 46:32 | 38:23 | 84:55 | 84:55 | 105:31 | 26:23 | 97.0515 | 96.3362 | 105:31 | 26:23 | 97.0515 | 96.3362
43 | Bhatkal | 3 | 3 | 10:03 | 10:03 | 16:59 | 11:20 | 28:19 | 28:19 | 38:22 | 12:47 | 98.689 | 98.2238 | 38:22 | 12:47 | 98.689 | 98.2238
44 | Khanapur | 2 | 2 | 6:50 | 6:50 | 7:45 | 21:25 | 29:10 | 29:10 | 36:00 | 18:00 | 97.9745 | 97.5 | 36:00 | 18:00 | 97.9745 | 97.5
45 | Bailhongal | 3 | 3 | 46:25 | 46:25 | 106:15 | 62:40 | 168:55 | 168:55 | 215:20 | 71:47 | 92.1798 | 90.0309 | 215:20 | 71:47 | 92.1798 | 90.0309
46 | Soundatti | 3 | 3 | 1:00 | 1:00 | 58:40 | 30:09 | 88:49 | 88:49 | 89:49 | 29:56 | 95.8881 | 95.8418 | 89:49 | 29:56 | 95.8881 | 95.8418
47 | Ramdurg | 2 | 2 | 6:30 | 6:30 | 19:35 | 5:55 | 25:30 | 25:30 | 32:00 | 16:00 | 98.2292 | 97.7778 | 32:00 | 16:00 | 98.2292 | 97.7778
48 | Gokak | 11 | 11 | 10:27 | 10:27 | 32:18 | 22:35 | 54:53 | 54:53 | 65:20 | 5:56 | 99.307 | 99.1751 | 65:20 | 5:56 | 99.307 | 99.1751
49 | Mudalagi | 2 | 2 | 2:20 | 2:20 | 16:05 | 6:00 | 22:05 | 22:05 | 24:25 | 12:12 | 98.4664 | 98.3044 | 24:25 | 12:12 | 98.4664 | 98.3044
50 | Konnur | 1 | 1 | 0:15 | 0:15 | 42:40 | 8:30 | 51:10 | 51:10 | 51:25 | 51:25 | 92.8935 | 92.8588 | 51:25 | 51:25 | 92.8935 | 92.8588
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 19:35 | 9:00 | 28:35 | 28:35 | 28:35 | 28:35 | 96.0301 | 96.0301 | 28:35 | 28:35 | 96.0301 | 96.0301
52 | Kudachi | 1 | 1 | 0:00 | 0:00 | 61:30 | 8:35 | 70:05 | 70:05 | 70:05 | 70:05 | 90.2662 | 90.2662 | 70:05 | 70:05 | 90.2662 | 90.2662
53 | Athani | 6 | 6 | 42:58 | 42:58 | 59:02 | 94:37 | 153:39 | 153:39 | 196:37 | 32:46 | 96.4433 | 95.4487 | 196:37 | 32:46 | 96.4433 | 95.4487
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 8:15 | 8:35 | 16:50 | 16:50 | 16:50 | 8:25 | 98.831 | 98.831 | 16:50 | 8:25 | 98.831 | 98.831
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 76:50 | 47:20 | 124:10 | 124:10 | 124:10 | 24:50 | 96.5509 | 96.5509 | 124:10 | 24:50 | 96.5509 | 96.5509
56 | Sadalaga | 1 | 1 | 0:00 | 0:00 | 11:00 | 4:00 | 15:00 | 15:00 | 15:00 | 15:00 | 97.9167 | 97.9167 | 15:00 | 15:00 | 97.9167 | 97.9167
57 | Muddebihal | 2 | 2 | 6:00 | 6:00 | 58:55 | 26:00 | 84:55 | 84:55 | 90:55 | 45:28 | 94.103 | 93.6863 | 90:55 | 45:28 | 94.103 | 93.6863
58 | Talikoti | 1 | 1 | 8:00 | 8:00 | 8:30 | 6:25 | 14:55 | 14:55 | 22:55 | 22:55 | 97.9282 | 96.8171 | 22:55 | 22:55 | 97.9282 | 96.8171
59 | B.Bagewadi | 1 | 1 | 3:27 | 3:27 | 2:40 | 3:40 | 6:20 | 6:20 | 9:47 | 9:47 | 99.1204 | 98.6412 | 9:47 | 9:47 | 99.1204 | 98.6412
60 | Indi | 3 | 3 | 5:33 | 5:33 | 14:38 | 14:31 | 29:09 | 29:09 | 34:42 | 11:34 | 98.6505 | 98.3935 | 34:42 | 11:34 | 98.6505 | 98.3935
61 | Sindagi | 2 | 2 | 8:40 | 8:40 | 26:45 | 9:30 | 36:15 | 36:15 | 44:55 | 22:28 | 97.4826 | 96.8808 | 44:55 | 22:28 | 97.4826 | 96.8808
62 | Guledgudda | 1 | 1 | 4:54 | 4:54 | 44:39 | 5:45 | 50:24 | 50:24 | 55:18 | 55:18 | 93 | 92.3194 | 55:18 | 55:18 | 93 | 92.3194
63 | Ilkal | 8 | 8 | 47:35 | 47:35 | 186:12 | 154:59 | 341:11 | 341:11 | 388:46 | 48:36 | 94.0767 | 93.2506 | 388:46 | 48:36 | 94.0767 | 93.2506
64 | Kerur | 2 | 2 | 10:25 | 10:25 | 11:10 | 17:17 | 28:27 | 28:27 | 38:52 | 19:26 | 98.0243 | 97.3009 | 38:52 | 19:26 | 98.0243 | 97.3009
65 | Hungund | 4 | 4 | 24:52 | 24:52 | 32:49 | 50:07 | 82:56 | 82:56 | 107:48 | 26:57 | 97.1204 | 96.2569 | 107:48 | 26:57 | 97.1204 | 96.2569
66 | Gaddankeri | 3 | 3 | 15:18 | 15:18 | 41:50 | 36:57 | 78:47 | 78:47 | 94:05 | 31:22 | 96.3526 | 95.6443 | 94:05 | 31:22 | 96.3526 | 95.6443
67 | Rampur | 1 | 1 | 5:33 | 5:33 | 21:12 | 1:15 | 22:27 | 22:27 | 28:00 | 28:00 | 96.8819 | 96.1111 | 28:00 | 28:00 | 96.8819 | 96.1111
68 | Kaladagi | 2 | 2 | 4:42 | 4:42 | 19:21 | 20:15 | 39:36 | 39:36 | 44:18 | 22:09 | 97.25 | 96.9236 | 44:18 | 22:09 | 97.25 | 96.9236
69 | Achanur | 1 | 1 | 3:03 | 3:03 | 11:33 | 7:21 | 18:54 | 18:54 | 21:57 | 21:57 | 97.375 | 96.9514 | 21:57 | 21:57 | 97.375 | 96.9514
70 | Shirur | 1 | 1 | 8:15 | 8:15 | 2:27 | 5:48 | 8:15 | 8:15 | 16:30 | 16:30 | 98.8542 | 97.7083 | 16:30 | 16:30 | 98.8542 | 97.7083
71 | Badami | 1 | 1 | 6:12 | 6:12 | 11:54 | 11:19 | 23:13 | 23:13 | 29:25 | 29:25 | 96.7755 | 95.9144 | 29:25 | 29:25 | 96.7755 | 95.9144
72 | Kulageri | 1 | 1 | 4:56 | 4:56 | 5:35 | 0:15 | 5:50 | 5:50 | 10:46 | 10:46 | 99.1898 | 98.5046 | 10:46 | 10:46 | 99.1898 | 98.5046
73 | Jamkhandi | 6 | 6 | 7:30 | 7:30 | 90:50 | 15:15 | 106:05 | 106:05 | 113:35 | 18:56 | 97.5444 | 97.3708 | 113:35 | 18:56 | 97.5444 | 97.3708
74 | Mahalingapur | 3 | 3 | 1:00 | 1:00 | 49:52 | 27:09 | 77:01 | 77:01 | 78:01 | 26:00 | 96.4344 | 96.3881 | 78:01 | 26:00 | 96.4344 | 96.3881
75 | Rabakavi | 2 | 2 | 7:45 | 7:45 | 16:50 | 4:00 | 20:50 | 20:50 | 28:35 | 14:17 | 98.5532 | 98.015 | 28:35 | 14:17 | 98.5532 | 98.015
76 | Banahatti | 2 | 2 | 0:30 | 0:30 | 13:50 | 0:35 | 14:25 | 14:25 | 14:55 | 7:28 | 98.9988 | 98.9641 | 14:55 | 7:28 | 98.9988 | 98.9641
77 | Terdal | 2 | 2 | 0:00 | 0:00 | 21:00 | 2:40 | 23:40 | 23:40 | 23:40 | 11:50 | 98.3565 | 98.3565 | 23:40 | 11:50 | 98.3565 | 98.3565
78 | Mudhol | 4 | 4 | 4:26 | 4:26 | 29:58 | 14:53 | 44:51 | 44:51 | 49:17 | 12:19 | 98.4427 | 98.2888 | 49:17 | 12:19 | 98.4427 | 98.2888
79 | Bilagi | 1 | 1 | 6:50 | 6:50 | 8:50 | 2:50 | 11:40 | 11:40 | 18:30 | 18:30 | 98.3796 | 97.4306 | 18:30 | 18:30 | 98.3796 | 97.4306
80 | Lokapur | 2 | 2 | 6:20 | 6:20 | 52:15 | 22:00 | 74:15 | 74:15 | 80:35 | 40:18 | 94.8438 | 94.4039 | 80:35 | 40:18 | 94.8438 | 94.4039
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of May-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2021 |  |  |  | Reliability for cumulative period from Apr-21 to May-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 77 | 77 | 10:50 | 20:00 | 297:47 | 278:16 | 576:03 | 1415:16 | 586:53 | 7:37 | 98.9945 | 98.9756 | 1435:16 | 18:38 | 98.7445 | 98.7268
2 | Dharwad(R) | 19 | 19 | 130:45 | 140:30 | 261:21 | 254:04 | 515:25 | 1017:14 | 646:10 | 34:01 | 96.3539 | 95.4289 | 1157:44 | 60:56 | 96.343 | 95.8379
3 | Kundagol | 1 | 1 | 28:50 | 75:00 | 2:45 | 15:20 | 18:05 | 37:05 | 46:55 | 46:55 | 97.5694 | 93.694 | 112:05 | 112:05 | 97.467 | 92.344
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 5:07 | 8:43 | 13:50 | 26:42 | 13:50 | 13:50 | 98.1407 | 98.1407 | 26:42 | 26:42 | 98.1762 | 98.1762
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 7:10 | 14:49 | 21:59 | 39:44 | 21:59 | 21:59 | 97.0453 | 97.0453 | 39:44 | 39:44 | 97.286 | 97.286
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 15:00 | 31:30 | 46:30 | 173:15 | 46:30 | 23:15 | 96.875 | 96.875 | 173:15 | 86:38 | 94.083 | 94.083
7 | Alnavar | 1 | 1 | 0:00 | 6:10 | 4:25 | 10:50 | 15:15 | 32:15 | 15:15 | 15:15 | 97.9503 | 97.9503 | 38:25 | 38:25 | 97.7971 | 97.3759
8 | Naragund | 2 | 2 | 5:40 | 15:00 | 26:00 | 34:00 | 60:00 | 118:35 | 65:40 | 32:50 | 95.9677 | 95.5869 | 133:35 | 66:48 | 95.95 | 95.4377
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 35:50 | 48:30 | 84:20 | 137:55 | 84:20 | 21:05 | 97.1662 | 97.1662 | 137:55 | 34:29 | 97.6449 | 97.6449
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 52:32 | 61:20 | 113:52 | 208:36 | 113:52 | 28:28 | 96.1738 | 96.1738 | 208:36 | 52:09 | 96.4378 | 96.4378
11 | Naregal | 1 | 1 | 0:00 | 0:00 | 7:50 | 8:50 | 16:40 | 36:00 | 16:40 | 16:40 | 97.7599 | 97.7599 | 36:00 | 36:00 | 97.541 | 97.541
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 23:30 | 31:50 | 55:20 | 110:50 | 55:20 | 27:40 | 96.2814 | 96.2814 | 110:50 | 55:25 | 96.2147 | 96.2147
13 | Ron | 3 | 3 | 0:00 | 0:00 | 26:45 | 107:31 | 134:16 | 200:46 | 134:16 | 44:45 | 93.9845 | 93.9845 | 200:46 | 66:55 | 95.4288 | 95.4288
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 11:15 | 15:55 | 27:10 | 54:20 | 27:10 | 9:03 | 98.7829 | 98.7829 | 54:20 | 18:07 | 98.7629 | 98.7629
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 30:35 | 39:28 | 70:03 | 117:06 | 70:03 | 70:03 | 90.5847 | 90.5847 | 117:06 | 117:06 | 92.0014 | 92.0014
16 | G.C.T.M | 1 | 1 | 12:25 | 21:35 | 17:30 | 3:25 | 20:55 | 32:35 | 33:20 | 33:20 | 97.1886 | 95.5197 | 54:10 | 54:10 | 97.7744 | 96.3001
17 | F.C.S.M | 2 | 2 | 23:20 | 32:20 | 30:40 | 4:20 | 35:00 | 45:25 | 58:20 | 29:10 | 97.6478 | 96.0797 | 77:45 | 38:52 | 98.4489 | 97.3446
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 6:43 | 7:14 | 13:57 | 26:08 | 13:57 | 13:57 | 98.125 | 98.125 | 26:08 | 26:08 | 98.2149 | 98.2149
19 | Hole-Alur | 1 | 1 | 5:40 | 26:20 | 8:40 | 2:45 | 11:25 | 36:55 | 17:05 | 17:05 | 98.4655 | 97.7039 | 63:15 | 63:15 | 97.4784 | 95.6796
20 | Savanur | 2 | 2 | 1:40 | 4:10 | 16:35 | 15:25 | 32:00 | 64:40 | 33:40 | 16:50 | 97.8495 | 97.7375 | 68:50 | 34:25 | 97.7914 | 97.6491
21 | Shiggaon | 2 | 2 | 0:45 | 14:20 | 11:20 | 26:05 | 37:25 | 139:35 | 38:10 | 19:05 | 97.4854 | 97.435 | 153:55 | 76:57 | 95.2328 | 94.7433
22 | Bankapur | 1 | 1 | 11:55 | 19:10 | 20:40 | 8:55 | 29:35 | 48:10 | 41:30 | 41:30 | 96.0237 | 94.422 | 67:20 | 67:20 | 96.7099 | 95.4007
23 | Hangal | 2 | 2 | 21:30 | 54:10 | 67:05 | 44:15 | 111:20 | 167:50 | 132:50 | 66:25 | 92.5179 | 91.073 | 222:00 | 111:00 | 94.268 | 92.418
24 | Ranebennur | 16 | 16 | 5:36 | 46:31 | 158:15 | 191:29 | 349:44 | 464:57 | 355:20 | 22:12 | 97.0621 | 97.015 | 511:28 | 31:58 | 98.0151 | 97.8165
25 | Halageri | 2 | 2 | 56:50 | 111:10 | 42:15 | 165:15 | 207:30 | 237:10 | 264:20 | 132:10 | 86.0551 | 82.2357 | 348:20 | 174:10 | 91.9 | 88.1034
26 | Tuminakatti | 2 | 2 | 0:10 | 2:10 | 27:50 | 13:30 | 41:20 | 79:25 | 41:30 | 20:45 | 97.2222 | 97.211 | 81:35 | 40:48 | 97.2877 | 97.2137
27 | Kahanderayanahalli | 1 | 1 | 1:42 | 2:42 | 19:40 | 85:55 | 105:35 | 182:25 | 107:17 | 107:17 | 85.8087 | 85.5802 | 185:07 | 185:07 | 87.5398 | 87.3554
28 | Rattihalli | 1 | 1 | 0:20 | 3:00 | 10:25 | 14:35 | 25:00 | 50:25 | 25:20 | 25:20 | 96.6398 | 96.595 | 53:25 | 53:25 | 96.5562 | 96.3513
29 | Hirekerur | 2 | 2 | 5:15 | 35:35 | 16:00 | 24:20 | 40:20 | 91:00 | 45:35 | 22:47 | 97.2894 | 96.9366 | 126:35 | 63:18 | 96.8921 | 95.6768
30 | Byadagi | 8 | 8 | 51:40 | 81:50 | 161:50 | 416:30 | 578:20 | 852:05 | 630:00 | 78:45 | 90.2834 | 89.4153 | 933:55 | 116:44 | 92.7247 | 92.026
31 | Sirsi | 5 | 5 | 5:15 | 9:50 | 16:36 | 37:34 | 54:10 | 117:35 | 59:25 | 11:53 | 98.5439 | 98.4028 | 127:25 | 25:29 | 98.3937 | 98.2593
32 | Yellapur | 3 | 3 | 79:15 | 91:18 | 19:25 | 15:25 | 34:50 | 59:40 | 114:05 | 38:02 | 98.4394 | 94.8887 | 150:58 | 50:19 | 98.6415 | 96.5627
33 | Mundagod | 3 | 3 | 4:15 | 4:15 | 31:20 | 47:20 | 78:40 | 174:10 | 82:55 | 27:38 | 96.4755 | 96.2851 | 178:25 | 59:28 | 96.0345 | 95.9377
34 | Siddapur | 2 | 2 | 0:10 | 4:20 | 10:05 | 13:10 | 23:15 | 48:00 | 23:25 | 11:42 | 98.4375 | 98.4263 | 52:20 | 26:10 | 98.3607 | 98.2127
35 | Dandeli | 8 | 8 | 14:24 | 53:04 | 120:18 | 97:28 | 217:46 | 320:04 | 232:10 | 29:01 | 96.3413 | 96.0994 | 373:08 | 46:38 | 97.2672 | 96.8141
36 | Haliyal | 3 | 3 | 1:33 | 1:52 | 20:23 | 31:17 | 51:40 | 116:04 | 53:13 | 17:44 | 97.6852 | 97.6157 | 117:56 | 39:19 | 97.3573 | 97.3148
37 | Ankola | 3 | 3 | 41:25 | 57:48 | 17:40 | 17:40 | 35:20 | 55:49 | 76:45 | 25:35 | 98.417 | 96.5614 | 113:37 | 37:52 | 98.7291 | 97.4131
38 | Kumta | 3 | 3 | 2:36 | 6:06 | 20:00 | 32:01 | 52:01 | 77:25 | 54:37 | 18:12 | 97.6695 | 97.553 | 83:31 | 27:50 | 98.2373 | 98.0984
39 | Gokarna | 1 | 1 | 14:04 | 19:01 | 10:35 | 1:45 | 12:20 | 15:10 | 26:24 | 26:24 | 98.3423 | 96.4516 | 34:11 | 34:11 | 98.964 | 97.6651
40 | Kasarkod | 1 | 1 | 26:21 | 65:01 | 16:20 | 13:15 | 29:35 | 44:15 | 55:56 | 55:56 | 96.0237 | 92.4821 | 109:16 | 109:16 | 96.9775 | 92.5364
41 | Honnavar | 3 | 3 | 12:30 | 25:45 | 29:27 | 55:14 | 84:41 | 108:01 | 97:11 | 32:24 | 96.2059 | 95.6459 | 133:46 | 44:35 | 97.5406 | 96.9543
42 | Murdeshwar | 4 | 4 | 32:04 | 52:40 | 127:11 | 130:05 | 257:16 | 342:11 | 289:20 | 72:20 | 91.3553 | 90.2778 | 394:51 | 98:43 | 94.1567 | 93.2573
43 | Bhatkal | 3 | 3 | 81:09 | 91:12 | 29:15 | 43:02 | 72:17 | 100:36 | 153:26 | 51:09 | 96.7615 | 93.1257 | 191:48 | 63:56 | 97.7095 | 95.633
44 | Khanapur | 2 | 2 | 8:30 | 15:20 | 22:45 | 26:15 | 49:00 | 78:10 | 57:30 | 28:45 | 96.707 | 96.1358 | 93:30 | 46:45 | 97.3304 | 96.8067
45 | Bailhongal | 3 | 3 | 1:30 | 47:55 | 58:50 | 86:40 | 145:30 | 314:25 | 147:00 | 49:00 | 93.4812 | 93.414 | 362:20 | 120:47 | 92.8412 | 91.7502
46 | Soundatti | 3 | 3 | 12:00 | 13:00 | 53:51 | 37:23 | 91:14 | 180:03 | 103:14 | 34:25 | 95.9125 | 95.3749 | 193:03 | 64:21 | 95.9005 | 95.6045
47 | Ramdurg | 2 | 2 | 0:40 | 7:10 | 23:22 | 18:58 | 42:20 | 67:50 | 43:00 | 21:30 | 97.155 | 97.1102 | 75:00 | 37:30 | 97.6833 | 97.4385
48 | Gokak | 10 | 10 | 3:47 | 14:14 | 24:24 | 17:51 | 42:15 | 97:08 | 46:02 | 4:36 | 99.4321 | 99.3813 | 111:22 | 11:08 | 99.3365 | 99.2393
49 | Mudalagi | 2 | 2 | 2:00 | 4:20 | 13:00 | 15:05 | 28:05 | 50:10 | 30:05 | 15:02 | 98.1127 | 97.9783 | 54:30 | 27:15 | 98.2867 | 98.1387
50 | Konnur | 1 | 1 | 0:00 | 0:15 | 21:25 | 6:35 | 28:00 | 79:10 | 28:00 | 28:00 | 96.2366 | 96.2366 | 79:25 | 79:25 | 94.5924 | 94.5754
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 22:00 | 23:50 | 45:50 | 74:25 | 45:50 | 45:50 | 93.8396 | 93.8396 | 74:25 | 74:25 | 94.9169 | 94.9169
52 | Kudachi | 1 | 1 | 0:00 | 0:00 | 25:00 | 5:00 | 30:00 | 100:05 | 30:00 | 30:00 | 95.9677 | 95.9677 | 100:05 | 100:05 | 93.1637 | 93.1637
53 | Athani | 5 | 5 | 34:12 | 77:10 | 58:36 | 103:31 | 162:07 | 315:46 | 196:19 | 39:16 | 95.642 | 94.7227 | 392:56 | 78:35 | 95.6862 | 94.6321
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 18:35 | 35:25 | 54:00 | 70:50 | 54:00 | 27:00 | 96.371 | 96.371 | 70:50 | 35:25 | 97.5808 | 97.5808
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 52:30 | 32:25 | 84:55 | 209:05 | 84:55 | 16:59 | 97.7173 | 97.7173 | 209:05 | 41:49 | 97.1437 | 97.1437
56 | Sadalaga | 1 | 1 | 0:00 | 0:00 | 7:45 | 13:15 | 21:00 | 36:00 | 21:00 | 21:00 | 97.1774 | 97.1774 | 36:00 | 36:00 | 97.541 | 97.541
57 | Muddebihal | 2 | 2 | 2:10 | 8:10 | 37:25 | 34:55 | 72:20 | 157:15 | 74:30 | 37:15 | 95.1389 | 94.9933 | 165:25 | 82:42 | 94.6294 | 94.3505
58 | Talikoti | 1 | 1 | 3:35 | 11:35 | 12:55 | 8:25 | 21:20 | 36:15 | 24:55 | 24:55 | 97.1326 | 96.651 | 47:50 | 47:50 | 97.5239 | 96.7327
59 | B.Bagewadi | 1 | 1 | 2:10 | 5:37 | 10:02 | 9:40 | 19:42 | 26:02 | 21:52 | 21:52 | 97.3522 | 97.0609 | 31:39 | 31:39 | 98.2218 | 97.8381
60 | Indi | 3 | 3 | 0:00 | 5:33 | 4:20 | 17:30 | 21:50 | 50:59 | 21:50 | 7:17 | 99.0218 | 99.0218 | 56:32 | 18:51 | 98.8392 | 98.7128
61 | Sindagi | 2 | 2 | 27:00 | 35:40 | 22:55 | 12:45 | 35:40 | 71:55 | 62:40 | 31:20 | 97.603 | 95.7885 | 107:35 | 53:48 | 97.5438 | 96.3257
62 | Guledgudda | 1 | 1 | 0:00 | 4:54 | 5:08 | 11:53 | 17:01 | 67:25 | 17:01 | 17:01 | 97.7128 | 97.7128 | 72:19 | 72:19 | 95.395 | 95.0603
63 | Ilkal | 8 | 8 | 56:24 | 103:59 | 126:18 | 282:29 | 408:47 | 749:58 | 465:11 | 58:09 | 93.132 | 92.1844 | 853:57 | 106:45 | 93.5966 | 92.7088
64 | Kerur | 2 | 2 | 0:05 | 10:30 | 14:36 | 22:25 | 37:01 | 65:28 | 37:06 | 18:33 | 97.5123 | 97.5067 | 75:58 | 37:59 | 97.7641 | 97.4055
65 | Hungund | 4 | 4 | 22:16 | 47:08 | 50:16 | 95:53 | 146:09 | 229:05 | 168:25 | 42:06 | 95.089 | 94.3408 | 276:13 | 69:03 | 96.0881 | 95.2832
66 | Gaddankeri | 3 | 3 | 3:02 | 18:20 | 33:17 | 21:27 | 54:44 | 133:31 | 57:46 | 19:15 | 97.5478 | 97.4119 | 151:51 | 50:37 | 96.96 | 96.5426
67 | Rampur | 1 | 1 | 0:15 | 5:48 | 7:27 | 5:51 | 13:18 | 35:45 | 13:33 | 13:33 | 98.2124 | 98.1788 | 41:33 | 41:33 | 97.5581 | 97.1619
68 | Kaladagi | 2 | 2 | 0:00 | 4:42 | 15:54 | 27:51 | 43:45 | 83:21 | 43:45 | 21:52 | 97.0598 | 97.0598 | 88:03 | 44:02 | 97.1533 | 96.9928
69 | Achanur | 1 | 1 | 0:09 | 3:12 | 24:09 | 9:42 | 33:51 | 52:45 | 34:00 | 34:00 | 95.4503 | 95.4301 | 55:57 | 55:57 | 96.3969 | 96.1783
70 | Shirur | 1 | 1 | 5:33 | 13:48 | 6:30 | 37:54 | 44:24 | 52:39 | 49:57 | 49:57 | 94.0323 | 93.2863 | 66:27 | 66:27 | 96.4037 | 95.4611
71 | Badami | 1 | 1 | 0:15 | 6:27 | 5:07 | 19:46 | 24:53 | 48:06 | 25:08 | 25:08 | 96.6555 | 96.6219 | 54:33 | 54:33 | 96.7145 | 96.2739
72 | Kulageri | 1 | 1 | 2:00 | 6:56 | 4:15 | 3:50 | 8:05 | 13:55 | 10:05 | 10:05 | 98.9135 | 98.6447 | 20:51 | 20:51 | 99.0494 | 98.5758
73 | Jamkhandi | 6 | 6 | 0:00 | 7:30 | 52:25 | 29:25 | 81:50 | 187:55 | 81:50 | 13:38 | 98.1668 | 98.1668 | 195:25 | 32:34 | 97.8607 | 97.7753
74 | Mahalingapur | 3 | 3 | 0:00 | 1:00 | 52:07 | 15:40 | 67:47 | 144:48 | 67:47 | 22:36 | 96.9631 | 96.9631 | 145:48 | 48:36 | 96.7031 | 96.6803
75 | Rabakavi | 2 | 2 | 1:00 | 8:45 | 14:40 | 6:45 | 21:25 | 42:15 | 22:25 | 11:12 | 98.5607 | 98.4935 | 51:00 | 25:30 | 98.557 | 98.2582
76 | Banahatti | 2 | 2 | 0:00 | 0:30 | 27:25 | 4:25 | 31:50 | 46:15 | 31:50 | 15:55 | 97.8607 | 97.8607 | 46:45 | 23:22 | 98.4204 | 98.4033
77 | Terdal | 2 | 2 | 0:00 | 0:00 | 28:50 | 6:45 | 35:35 | 59:15 | 35:35 | 17:48 | 97.6086 | 97.6086 | 59:15 | 29:38 | 97.9764 | 97.9764
78 | Mudhol | 4 | 4 | 1:35 | 6:01 | 54:56 | 34:41 | 89:37 | 134:28 | 91:12 | 22:48 | 96.9887 | 96.9355 | 140:29 | 35:07 | 97.7038 | 97.601
79 | Bilagi | 1 | 1 | 4:58 | 11:48 | 8:10 | 5:10 | 13:20 | 25:00 | 18:18 | 18:18 | 98.2079 | 97.5403 | 36:48 | 36:48 | 98.2923 | 97.4863
80 | Lokapur | 2 | 2 | 0:00 | 6:20 | 39:40 | 23:05 | 62:45 | 137:00 | 62:45 | 31:22 | 95.7829 | 95.7829 | 143:20 | 71:40 | 95.321 | 95.1047
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of June-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2021 |  |  |  | Reliability for cumulative period from Apr-21 to June-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 77 | 77 | 1:15 | 21:15 | 259:44 | 297:50 | 557:34 | 1972:50 | 558:49 | 7:15 | 98.9943 | 98.992 | 1994:05 | 25:54 | 98.8269 | 98.8142
2 | Dharwad(R) | 19 | 19 | 2:15 | 142:45 | 256:59 | 181:43 | 438:42 | 1455:56 | 440:57 | 23:12 | 96.7931 | 96.7767 | 1598:41 | 84:08 | 96.4914 | 96.1474
3 | Kundagol | 1 | 1 | 6:40 | 81:40 | 7:45 | 10:40 | 18:25 | 55:30 | 25:05 | 25:05 | 97.4421 | 96.5162 | 137:10 | 137:10 | 97.4588 | 93.7195
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 3:23 | 5:42 | 9:05 | 35:47 | 9:05 | 9:05 | 98.7384 | 98.7384 | 35:47 | 35:47 | 98.3616 | 98.3616
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 6:45 | 7:10 | 13:55 | 53:39 | 13:55 | 13:55 | 98.0671 | 98.0671 | 53:39 | 53:39 | 97.5435 | 97.5435
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 10:05 | 127:20 | 137:25 | 310:40 | 137:25 | 68:42 | 90.4572 | 90.4572 | 310:40 | 155:20 | 92.8877 | 92.8877
7 | Alnavar | 1 | 1 | 0:00 | 6:10 | 12:10 | 17:45 | 29:55 | 62:10 | 29:55 | 29:55 | 95.8449 | 95.8449 | 68:20 | 68:20 | 97.1535 | 96.8712
8 | Naragund | 2 | 2 | 4:20 | 19:20 | 20:00 | 27:05 | 47:05 | 165:40 | 51:25 | 25:42 | 96.7303 | 96.4294 | 185:00 | 92:30 | 96.2073 | 95.7647
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 43:15 | 53:35 | 96:50 | 234:45 | 96:50 | 24:12 | 96.6377 | 96.6377 | 234:45 | 58:41 | 97.3128 | 97.3128
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 54:36 | 47:17 | 101:53 | 310:29 | 101:53 | 25:28 | 96.4624 | 96.4624 | 310:29 | 77:37 | 96.4459 | 96.4459
11 | Naregal | 1 | 1 | 5:05 | 5:05 | 9:15 | 2:55 | 12:10 | 48:10 | 17:15 | 17:15 | 98.3102 | 97.6042 | 53:15 | 53:15 | 97.7946 | 97.5618
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 26:25 | 17:00 | 43:25 | 154:15 | 43:25 | 21:42 | 96.985 | 96.985 | 154:15 | 77:08 | 96.4686 | 96.4686
13 | Ron | 3 | 3 | 14:15 | 14:15 | 28:10 | 31:15 | 59:25 | 260:11 | 73:40 | 24:33 | 97.2492 | 96.5895 | 274:26 | 91:29 | 96.0289 | 95.8115
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 13:45 | 15:45 | 29:30 | 83:50 | 29:30 | 9:50 | 98.6343 | 98.6343 | 83:50 | 27:57 | 98.7205 | 98.7205
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 21:35 | 18:53 | 40:28 | 157:34 | 40:28 | 40:28 | 94.3796 | 94.3796 | 157:34 | 157:34 | 92.7854 | 92.7854
16 | G.C.T.M | 1 | 1 | 4:10 | 25:45 | 13:20 | 4:10 | 17:30 | 50:05 | 21:40 | 21:40 | 97.5694 | 96.9907 | 75:50 | 75:50 | 97.7068 | 96.5278
17 | F.C.S.M | 2 | 2 | 10:45 | 43:05 | 10:45 | 3:20 | 14:05 | 59:30 | 24:50 | 12:25 | 99.022 | 98.2755 | 102:35 | 51:18 | 98.6378 | 97.6515
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 6:31 | 3:08 | 9:39 | 35:47 | 9:39 | 9:39 | 98.6597 | 98.6597 | 35:47 | 35:47 | 98.3616 | 98.3616
19 | Hole-Alur | 1 | 1 | 13:20 | 39:40 | 7:40 | 3:05 | 10:45 | 47:40 | 24:05 | 24:05 | 98.5069 | 96.6551 | 87:20 | 87:20 | 97.8175 | 96.0012
20 | Savanur | 3 | 3 | 0:00 | 4:10 | 13:10 | 40:50 | 54:00 | 118:40 | 54:00 | 18:00 | 97.5 | 97.5 | 122:50 | 40:57 | 98.1888 | 98.1253
21 | Shiggaon | 2 | 2 | 0:00 | 14:20 | 27:15 | 46:45 | 74:00 | 213:35 | 74:00 | 37:00 | 94.8611 | 94.8611 | 227:55 | 113:57 | 95.1103 | 94.7821
22 | Bankapur | 1 | 1 | 2:00 | 21:10 | 19:20 | 13:50 | 33:10 | 81:20 | 35:10 | 35:10 | 95.3935 | 95.1157 | 102:30 | 102:30 | 96.2759 | 95.3068
23 | Hangal | 2 | 2 | 0:30 | 54:40 | 23:05 | 45:25 | 68:30 | 236:20 | 69:00 | 34:30 | 95.2431 | 95.2083 | 291:00 | 145:30 | 94.5894 | 93.3379
24 | Ranebennur | 16 | 16 | 8:25 | 54:56 | 105:44 | 105:52 | 211:36 | 676:33 | 220:01 | 13:45 | 98.1632 | 98.0901 | 731:29 | 45:43 | 98.0639 | 97.9067
25 | Halageri | 2 | 2 | 7:55 | 119:05 | 37:20 | 2:10 | 39:30 | 276:40 | 47:25 | 23:42 | 97.2569 | 96.7072 | 395:45 | 197:52 | 93.6661 | 90.9398
26 | Tuminakatti | 2 | 2 | 0:10 | 2:20 | 18:00 | 3:45 | 21:45 | 101:10 | 21:55 | 10:58 | 98.4896 | 98.478 | 103:30 | 51:45 | 97.6839 | 97.6305
27 | Kahanderayanahalli | 1 | 1 | 0:10 | 2:52 | 13:55 | 39:05 | 53:00 | 235:25 | 53:10 | 53:10 | 92.6389 | 92.6157 | 238:17 | 238:17 | 89.2208 | 89.0896
28 | Rattihalli | 1 | 1 | 0:10 | 3:10 | 21:00 | 3:15 | 24:15 | 74:40 | 24:25 | 24:25 | 96.6319 | 96.6088 | 77:50 | 77:50 | 96.5812 | 96.4362
29 | Hirekerur | 2 | 2 | 1:55 | 37:30 | 21:55 | 15:45 | 37:40 | 128:40 | 39:35 | 19:48 | 97.3843 | 97.2512 | 166:10 | 83:05 | 97.0543 | 96.1958
30 | Byadagi | 8 | 8 | 18:10 | 100:00 | 106:00 | 57:45 | 163:45 | 1015:50 | 181:55 | 22:44 | 97.1571 | 96.8417 | 1115:50 | 139:29 | 94.1859 | 93.6136
31 | Sirsi | 5 | 5 | 9:10 | 19:00 | 15:17 | 43:28 | 58:45 | 176:20 | 67:55 | 13:35 | 98.3681 | 98.1134 | 195:20 | 39:04 | 98.3852 | 98.2112
32 | Yellapur | 3 | 3 | 34:45 | 126:03 | 2:25 | 18:20 | 20:45 | 80:25 | 55:30 | 18:30 | 99.0394 | 97.4306 | 206:28 | 68:49 | 98.7726 | 96.8488
33 | Mundagod | 3 | 3 | 1:03 | 5:18 | 23:23 | 43:20 | 66:43 | 240:53 | 67:46 | 22:35 | 96.9113 | 96.8627 | 246:11 | 82:04 | 96.3235 | 96.2426
34 | Siddapur | 2 | 2 | 8:00 | 12:20 | 11:05 | 27:10 | 38:15 | 86:15 | 46:15 | 23:08 | 97.3438 | 96.7882 | 98:35 | 49:17 | 98.0254 | 97.7431
35 | Dandeli | 8 | 8 | 6:20 | 59:24 | 35:33 | 104:20 | 139:53 | 459:57 | 146:13 | 18:17 | 97.5715 | 97.4615 | 519:21 | 64:55 | 97.3675 | 97.0275
36 | Haliyal | 3 | 3 | 4:24 | 6:16 | 12:10 | 20:15 | 32:25 | 148:29 | 36:49 | 12:16 | 98.4992 | 98.2955 | 154:45 | 51:35 | 97.7338 | 97.6381
37 | Ankola | 3 | 3 | 38:22 | 96:10 | 16:03 | 17:36 | 33:39 | 89:28 | 72:01 | 24:00 | 98.4421 | 96.6659 | 185:38 | 61:53 | 98.6345 | 97.1668
38 | Kumta | 3 | 3 | 3:33 | 9:39 | 15:51 | 23:46 | 39:37 | 117:02 | 43:10 | 14:23 | 98.1659 | 98.0015 | 126:41 | 42:14 | 98.2138 | 98.0665
39 | Gokarna | 1 | 1 | 21:45 | 40:46 | 20:00 | 3:55 | 23:55 | 39:05 | 45:40 | 45:40 | 96.6782 | 93.6574 | 79:51 | 79:51 | 98.2105 | 96.3439
40 | Kasarkod | 1 | 1 | 33:56 | 98:57 | 26:57 | 12:03 | 39:00 | 83:15 | 72:56 | 72:56 | 94.5833 | 89.8704 | 182:12 | 182:12 | 96.1882 | 91.6575
41 | Honnavar | 3 | 3 | 3:33 | 29:18 | 47:55 | 22:41 | 70:36 | 178:37 | 74:09 | 24:43 | 96.7315 | 96.5671 | 207:55 | 69:18 | 97.2739 | 96.8267
42 | Murdeshwar | 4 | 4 | 4:48 | 57:28 | 54:51 | 21:29 | 76:20 | 418:31 | 81:08 | 20:17 | 97.3495 | 97.1829 | 475:59 | 119:00 | 95.2093 | 94.5515
43 | Bhatkal | 3 | 3 | 24:45 | 115:57 | 31:15 | 18:01 | 49:16 | 149:52 | 74:01 | 24:40 | 97.7191 | 96.5733 | 265:49 | 88:36 | 97.7127 | 95.943
44 | Khanapur | 2 | 2 | 10:10 | 25:30 | 30:30 | 14:50 | 45:20 | 123:30 | 55:30 | 27:45 | 96.8519 | 96.1458 | 149:00 | 74:30 | 97.1726 | 96.5888
45 | Bailhongal | 3 | 3 | 0:00 | 47:55 | 56:40 | 85:45 | 142:25 | 456:50 | 142:25 | 47:28 | 93.4066 | 93.4066 | 504:45 | 168:15 | 93.0276 | 92.2962
46 | Soundatti | 3 | 3 | 5:05 | 18:05 | 63:35 | 25:03 | 88:38 | 268:41 | 93:43 | 31:14 | 95.8966 | 95.6613 | 286:46 | 95:35 | 95.8992 | 95.6232
47 | Ramdurg | 2 | 2 | 6:50 | 14:00 | 26:20 | 21:55 | 48:15 | 116:05 | 55:05 | 27:32 | 96.6493 | 96.1748 | 130:05 | 65:02 | 97.3424 | 97.0219
48 | Gokak | 10 | 10 | 4:51 | 19:05 | 14:57 | 26:09 | 41:06 | 138:14 | 45:57 | 4:36 | 99.4292 | 99.3618 | 157:19 | 15:44 | 99.3671 | 99.2797
49 | Mudalagi | 2 | 2 | 1:10 | 5:30 | 29:10 | 16:25 | 45:35 | 95:45 | 46:45 | 23:23 | 96.8345 | 96.7535 | 101:15 | 50:38 | 97.8079 | 97.682
50 | Konnur | 1 | 1 | 0:00 | 0:15 | 17:50 | 2:30 | 20:20 | 99:30 | 20:20 | 20:20 | 97.1759 | 97.1759 | 99:45 | 99:45 | 95.4441 | 95.4327
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 14:35 | 10:10 | 24:45 | 99:10 | 24:45 | 24:45 | 96.5625 | 96.5625 | 99:10 | 99:10 | 95.4594 | 95.4594
52 | Kudachi | 1 | 1 | 1:10 | 1:10 | 31:05 | 0:00 | 31:05 | 131:10 | 32:15 | 32:15 | 95.6829 | 95.5208 | 132:20 | 132:20 | 93.9942 | 93.9408
53 | Athani | 6 | 6 | 17:42 | 94:52 | 54:45 | 66:37 | 121:22 | 437:08 | 139:04 | 23:11 | 97.1906 | 96.7809 | 532:00 | 88:40 | 96.6641 | 95.9402
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 10:30 | 11:35 | 22:05 | 92:55 | 22:05 | 11:02 | 98.4664 | 98.4664 | 92:55 | 46:28 | 97.8728 | 97.8728
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 65:10 | 56:25 | 121:35 | 330:40 | 121:35 | 24:19 | 96.6227 | 96.6227 | 330:40 | 66:08 | 96.9719 | 96.9719
56 | Sadalaga | 1 | 1 | 0:10 | 0:10 | 9:10 | 10:05 | 19:15 | 55:15 | 19:25 | 19:25 | 97.3264 | 97.3032 | 55:25 | 55:25 | 97.4702 | 97.4626
57 | Muddebihal | 2 | 2 | 39:40 | 47:50 | 64:20 | 37:20 | 101:40 | 258:55 | 141:20 | 70:40 | 92.9398 | 90.1852 | 306:45 | 153:22 | 94.0724 | 92.9773
58 | Talikoti | 1 | 1 | 2:30 | 14:05 | 11:00 | 8:00 | 19:00 | 55:15 | 21:30 | 21:30 | 97.3611 | 97.0139 | 69:20 | 69:20 | 97.4702 | 96.8254
59 | B.Bagewadi | 1 | 1 | 2:20 | 7:57 | 4:00 | 3:45 | 7:45 | 33:47 | 10:05 | 10:05 | 98.9236 | 98.5995 | 41:44 | 41:44 | 98.4531 | 98.0891
60 | Indi | 3 | 3 | 0:00 | 5:33 | 5:43 | 9:27 | 15:10 | 66:09 | 15:10 | 5:03 | 99.2978 | 99.2978 | 71:42 | 23:54 | 98.9904 | 98.9057
61 | Sindagi | 2 | 2 | 4:20 | 40:00 | 19:10 | 17:30 | 36:40 | 108:35 | 41:00 | 20:30 | 97.4537 | 97.1528 | 148:35 | 74:18 | 97.5141 | 96.5984
62 | Guledgudda | 1 | 1 | 0:00 | 4:54 | 17:04 | 6:48 | 23:52 | 91:17 | 23:52 | 23:52 | 96.6852 | 96.6852 | 96:11 | 96:11 | 95.8204 | 95.596
63 | Ilkal | 8 | 8 | 40:03 | 144:02 | 162:00 | 222:00 | 384:00 | 1133:58 | 424:03 | 53:00 | 93.3333 | 92.638 | 1278:00 | 159:45 | 93.5098 | 92.6854
64 | Kerur | 2 | 2 | 1:55 | 12:25 | 18:25 | 14:57 | 33:22 | 98:50 | 35:17 | 17:39 | 97.6829 | 97.5498 | 111:15 | 55:38 | 97.7373 | 97.4531
65 | Hungund | 4 | 4 | 24:52 | 72:00 | 32:49 | 50:07 | 82:56 | 312:01 | 107:48 | 26:57 | 97.1204 | 96.2569 | 384:01 | 96:00 | 96.4284 | 95.6042
66 | Gaddankeri | 3 | 3 | 6:50 | 25:10 | 72:21 | 28:37 | 100:58 | 234:29 | 107:48 | 35:56 | 95.3256 | 95.0093 | 259:39 | 86:33 | 96.4212 | 96.0371
67 | Rampur | 1 | 1 | 0:12 | 6:00 | 16:18 | 3:18 | 19:36 | 55:21 | 19:48 | 19:48 | 97.2778 | 97.25 | 61:21 | 61:21 | 97.4657 | 97.1909
68 | Kaladagi | 2 | 2 | 1:00 | 5:42 | 40:24 | 27:48 | 68:12 | 151:33 | 69:12 | 34:36 | 95.2639 | 95.1944 | 157:15 | 78:38 | 96.5304 | 96.4
69 | Achanur | 1 | 1 | 0:12 | 3:24 | 28:03 | 24:42 | 52:45 | 105:30 | 52:57 | 52:57 | 92.6736 | 92.6458 | 108:54 | 108:54 | 95.1694 | 95.0137
70 | Shirur | 1 | 1 | 9:26 | 23:14 | 7:21 | 42:07 | 49:28 | 102:07 | 58:54 | 58:54 | 93.1296 | 91.8194 | 125:21 | 125:21 | 95.3243 | 94.2605
71 | Badami | 1 | 1 | 5:58 | 12:25 | 17:25 | 20:35 | 38:00 | 86:06 | 43:58 | 43:58 | 94.7222 | 93.8935 | 98:31 | 98:31 | 96.0577 | 95.4892
72 | Kulageri | 1 | 1 | 1:55 | 8:51 | 5:15 | 6:05 | 11:20 | 25:15 | 13:15 | 13:15 | 98.4259 | 98.1597 | 34:06 | 34:06 | 98.8439 | 98.4386
73 | Jamkhandi | 6 | 6 | 42:00 | 49:30 | 59:35 | 30:10 | 89:45 | 277:40 | 131:45 | 21:57 | 97.9225 | 96.9502 | 327:10 | 54:32 | 97.8811 | 97.5033
74 | Mahalingapur | 3 | 3 | 1:38 | 2:38 | 30:27 | 10:39 | 41:06 | 185:54 | 42:44 | 14:15 | 98.0972 | 98.0216 | 188:32 | 62:51 | 97.1627 | 97.1225
75 | Rabakavi | 2 | 2 | 5:20 | 14:05 | 11:25 | 5:00 | 16:25 | 58:40 | 21:45 | 10:52 | 98.86 | 98.4896 | 72:45 | 36:22 | 98.6569 | 98.3345
76 | Banahatti | 2 | 2 | 5:40 | 6:10 | 19:20 | 5:40 | 25:00 | 71:15 | 30:40 | 15:20 | 98.2639 | 97.8704 | 77:25 | 38:42 | 98.3688 | 98.2276
77 | Terdal | 2 | 2 | 1:10 | 1:10 | 28:00 | 7:45 | 35:45 | 95:00 | 36:55 | 18:28 | 97.5174 | 97.4363 | 96:10 | 48:05 | 97.8251 | 97.7984
78 | Mudhol | 4 | 4 | 11:06 | 17:07 | 30:34 | 12:37 | 43:11 | 177:39 | 54:17 | 13:34 | 98.5006 | 98.1152 | 194:46 | 48:42 | 97.9665 | 97.7705
79 | Bilagi | 1 | 1 | 1:25 | 13:13 | 9:50 | 6:00 | 15:50 | 40:50 | 17:15 | 17:15 | 97.8009 | 97.6042 | 54:03 | 54:03 | 98.1303 | 97.5252
80 | Lokapur | 2 | 2 | 0:00 | 6:20 | 51:25 | 30:30 | 81:55 | 218:55 | 81:55 | 40:58 | 94.3113 | 94.3113 | 225:15 | 112:38 | 94.9882 | 94.8432
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of July-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2021 |  |  |  | Reliability for cumulative period from Apr-21 to July-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 78 | 78 | 10:07 | 31:22 | 232:18 | 257:09 | 489:27 | 2462:17 | 499:34 | 6:24 | 99.1566 | 99.1392 | 2493:39 | 31:58 | 98.9219 | 98.9081
2 | Dharwad(R) | 19 | 19 | 8:50 | 151:35 | 208:46 | 472:34 | 681:20 | 2137:16 | 690:10 | 36:19 | 95.1802 | 95.1177 | 2288:51 | 120:28 | 96.1582 | 95.8857
3 | Kundagol | 1 | 1 | 12:05 | 93:45 | 1:05 | 2:15 | 3:20 | 58:50 | 15:25 | 15:25 | 99.552 | 97.9279 | 152:35 | 152:35 | 97.9907 | 94.7888
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 4:52 | 12:52 | 17:44 | 53:31 | 17:44 | 17:44 | 97.6165 | 97.6165 | 53:31 | 53:31 | 98.1722 | 98.1722
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 5:50 | 3:45 | 9:35 | 63:14 | 9:35 | 9:35 | 98.7119 | 98.7119 | 63:14 | 63:14 | 97.8404 | 97.8404
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 7:40 | 18:05 | 25:45 | 336:25 | 25:45 | 12:52 | 98.2695 | 98.2695 | 336:25 | 168:12 | 94.2552 | 94.2552
7 | Alnavar | 1 | 1 | 0:00 | 6:10 | 10:25 | 14:40 | 25:05 | 87:15 | 25:05 | 25:05 | 96.6286 | 96.6286 | 93:25 | 93:25 | 97.0202 | 96.8095
8 | Naragund | 2 | 2 | 16:20 | 35:40 | 21:55 | 25:10 | 47:05 | 212:45 | 63:25 | 31:42 | 96.8358 | 95.7381 | 248:25 | 124:12 | 96.367 | 95.7579
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 23:10 | 32:15 | 55:25 | 290:10 | 55:25 | 13:51 | 98.1379 | 98.1379 | 290:10 | 72:32 | 97.5225 | 97.5225
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 56:13 | 25:58 | 82:11 | 392:40 | 82:11 | 20:33 | 97.2385 | 97.2385 | 392:40 | 98:10 | 96.6473 | 96.6473
11 | Naregal | 1 | 1 | 5:50 | 10:55 | 1:35 | 1:55 | 3:30 | 51:40 | 9:20 | 9:20 | 99.5296 | 98.7455 | 62:35 | 62:35 | 98.2354 | 97.8626
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 27:30 | 10:00 | 37:30 | 191:45 | 37:30 | 18:45 | 97.4798 | 97.4798 | 191:45 | 95:52 | 96.7256 | 96.7256
13 | Ron | 3 | 3 | 0:00 | 14:15 | 22:55 | 27:26 | 50:21 | 310:32 | 50:21 | 16:47 | 97.7442 | 97.7442 | 324:47 | 108:16 | 96.4648 | 96.3026
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 31:45 | 21:50 | 53:35 | 137:25 | 53:35 | 17:52 | 97.5993 | 97.5993 | 137:25 | 45:48 | 98.4356 | 98.4356
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 14:41 | 0:25 | 15:06 | 172:40 | 15:06 | 15:06 | 97.9704 | 97.9704 | 172:40 | 172:40 | 94.1029 | 94.1029
16 | G.C.T.M | 1 | 1 | 4:40 | 30:25 | 10:05 | 5:00 | 15:05 | 65:10 | 19:45 | 19:45 | 97.9727 | 97.3454 | 95:35 | 95:35 | 97.7744 | 96.7355
17 | F.C.S.M | 2 | 2 | 9:20 | 52:25 | 14:55 | 2:55 | 17:50 | 77:20 | 27:10 | 13:35 | 98.8015 | 98.1743 | 129:45 | 64:52 | 98.6794 | 97.7843
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 7:25 | 1:31 | 8:56 | 44:43 | 8:56 | 8:56 | 98.7993 | 98.7993 | 44:43 | 44:43 | 98.4728 | 98.4728
19 | Hole-Alur | 1 | 1 | 17:20 | 57:00 | 5:45 | 0:45 | 6:30 | 54:10 | 23:50 | 23:50 | 99.1263 | 96.7966 | 111:10 | 111:10 | 98.15 | 96.2033
20 | Savanur | 3 | 3 | 0:00 | 4:10 | 129:00 | 26:25 | 155:25 | 274:05 | 155:25 | 51:48 | 93.0369 | 93.0369 | 278:15 | 92:45 | 96.8797 | 96.8323
21 | Shiggaon | 2 | 2 | 0:00 | 14:20 | 18:00 | 60:15 | 78:15 | 291:50 | 78:15 | 39:08 | 94.7413 | 94.7413 | 306:10 | 153:05 | 95.0165 | 94.7717
22 | Bankapur | 1 | 1 | 11:20 | 32:30 | 17:40 | 9:40 | 27:20 | 108:40 | 38:40 | 38:40 | 96.3262 | 94.8029 | 141:10 | 141:10 | 96.2887 | 95.1787
23 | Hangal | 2 | 2 | 0:50 | 55:30 | 27:10 | 17:30 | 44:40 | 281:00 | 45:30 | 22:45 | 96.9982 | 96.9422 | 336:30 | 168:15 | 95.2015 | 94.2538
24 | Ranebennur | 16 | 16 | 1:30 | 56:26 | 98:49 | 53:01 | 151:50 | 828:23 | 153:20 | 9:35 | 98.7245 | 98.7119 | 884:49 | 55:18 | 98.2318 | 98.1113
25 | Halageri | 2 | 2 | 36:00 | 155:05 | 49:40 | 6:50 | 56:30 | 333:10 | 92:30 | 46:15 | 96.203 | 93.7836 | 488:15 | 244:08 | 94.3107 | 91.6624
26 | Tuminakatti | 2 | 2 | 0:00 | 2:20 | 17:55 | 1:55 | 19:50 | 121:00 | 19:50 | 9:55 | 98.6671 | 98.6671 | 123:20 | 61:40 | 97.9337 | 97.8939
27 | Kahanderayanahalli | 1 | 1 | 0:55 | 3:47 | 10:00 | 58:35 | 68:35 | 304:00 | 69:30 | 69:30 | 90.7818 | 90.6586 | 307:47 | 307:47 | 89.6175 | 89.4883
28 | Rattihalli | 1 | 1 | 0:00 | 3:10 | 23:55 | 7:00 | 30:55 | 105:35 | 30:55 | 30:55 | 95.8445 | 95.8445 | 108:45 | 108:45 | 96.394 | 96.2859
29 | Hirekerur | 2 | 2 | 0:45 | 38:15 | 43:00 | 67:10 | 110:10 | 238:50 | 110:55 | 55:28 | 92.5963 | 92.5459 | 277:05 | 138:32 | 95.9216 | 95.2684
30 | Byadagi | 8 | 8 | 19:15 | 119:15 | 74:50 | 100:10 | 175:00 | 1190:50 | 194:15 | 24:17 | 97.0598 | 96.7364 | 1310:05 | 163:46 | 94.9162 | 94.4071
31 | Sirsi | 5 | 5 | 36:55 | 55:55 | 22:09 | 18:04 | 40:13 | 216:33 | 77:08 | 15:26 | 98.9189 | 97.9265 | 272:28 | 54:30 | 98.5208 | 98.1389
32 | Yellapur | 3 | 3 | 18:30 | 144:33 | 4:35 | 13:35 | 18:10 | 98:35 | 36:40 | 12:13 | 99.1861 | 98.3572 | 243:08 | 81:03 | 98.8777 | 97.2321
33 | Mundagod | 3 | 3 | 1:30 | 6:48 | 24:00 | 48:00 | 72:00 | 312:53 | 73:30 | 24:30 | 96.7742 | 96.707 | 319:41 | 106:34 | 96.438 | 96.3606
34 | Siddapur | 2 | 2 | 29:46 | 42:06 | 15:55 | 37:40 | 53:35 | 139:50 | 83:21 | 41:40 | 96.399 | 94.3985 | 181:56 | 90:58 | 97.6121 | 96.8932
35 | Dandeli | 8 | 8 | 10:32 | 69:56 | 106:22 | 144:48 | 251:10 | 711:07 | 261:42 | 32:43 | 95.7801 | 95.6032 | 781:03 | 97:38 | 96.9642 | 96.6656
36 | Haliyal | 3 | 3 | 2:58 | 9:14 | 34:37 | 25:03 | 59:40 | 208:09 | 62:38 | 20:53 | 97.3268 | 97.1938 | 217:23 | 72:28 | 97.6304 | 97.5252
37 | Ankola | 3 | 3 | 23:32 | 119:42 | 23:41 | 26:56 | 50:37 | 140:05 | 74:09 | 24:43 | 97.7322 | 96.6779 | 259:47 | 86:36 | 98.4052 | 97.0425
38 | Kumta | 3 | 3 | 0:09 | 9:48 | 21:13 | 17:34 | 38:47 | 155:49 | 38:56 | 12:59 | 98.2624 | 98.2557 | 165:37 | 55:12 | 98.2261 | 98.1146
39 | Gokarna | 1 | 1 | 15:40 | 56:26 | 4:40 | 2:30 | 7:10 | 46:15 | 22:50 | 22:50 | 99.0367 | 96.931 | 102:41 | 102:41 | 98.4204 | 96.4931
40 | Kasarkod | 1 | 1 | 47:32 | 146:29 | 3:37 | 3:35 | 7:12 | 90:27 | 54:44 | 54:44 | 99.0323 | 92.6434 | 236:56 | 236:56 | 96.9109 | 91.908
41 | Honnavar | 3 | 3 | 0:09 | 29:27 | 30:23 | 92:48 | 123:11 | 301:48 | 123:20 | 41:07 | 94.481 | 94.4743 | 331:15 | 110:25 | 96.5642 | 96.2289
42 | Murdeshwar | 4 | 4 | 5:56 | 63:24 | 25:48 | 28:58 | 54:46 | 473:17 | 60:42 | 15:10 | 98.1597 | 97.9603 | 536:41 | 134:10 | 95.959 | 95.4177
43 | Bhatkal | 3 | 3 | 21:02 | 136:59 | 24:08 | 11:35 | 35:43 | 185:35 | 56:45 | 18:55 | 98.3998 | 97.4574 | 322:34 | 107:31 | 97.8873 | 96.3278
44 | Khanapur | 2 | 2 | 11:30 | 37:00 | 56:15 | 7:45 | 64:00 | 187:30 | 75:30 | 37:45 | 95.6989 | 94.9261 | 224:30 | 112:15 | 96.7982 | 96.1663
45 | Bailhongal | 3 | 3 | 8:36 | 56:31 | 91:40 | 42:35 | 134:15 | 591:05 | 142:51 | 47:37 | 93.9852 | 93.5999 | 647:36 | 215:52 | 93.2709 | 92.6275
46 | Soundatti | 3 | 3 | 2:23 | 20:28 | 23:22 | 15:05 | 38:27 | 307:08 | 40:50 | 13:37 | 98.2773 | 98.1705 | 327:36 | 109:12 | 96.5035 | 96.2705
47 | Ramdurg | 2 | 2 | 1:58 | 15:58 | 26:18 | 7:28 | 33:46 | 149:51 | 35:44 | 17:52 | 97.7307 | 97.5986 | 165:49 | 82:54 | 97.4411 | 97.1684
48 | Gokak | 10 | 10 | 10:53 | 29:58 | 30:26 | 102:23 | 132:49 | 271:03 | 143:42 | 14:22 | 98.2148 | 98.0685 | 301:01 | 30:06 | 99.0743 | 98.9719
49 | Mudalagi | 2 | 2 | 2:15 | 7:45 | 29:40 | 22:00 | 51:40 | 147:25 | 53:55 | 26:58 | 96.5278 | 96.3766 | 155:10 | 77:35 | 97.4826 | 97.3503
50 | Konnur | 1 | 1 | 0:40 | 0:55 | 17:05 | 2:50 | 19:55 | 119:25 | 20:35 | 20:35 | 97.323 | 97.2334 | 120:20 | 120:20 | 95.9216 | 95.8903
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 19:00 | 15:41 | 34:41 | 133:51 | 34:41 | 34:41 | 95.3383 | 95.3383 | 133:51 | 133:51 | 95.4286 | 95.4286
52 | Kudachi | 1 | 1 | 1:00 | 2:10 | 38:00 | 11:00 | 49:00 | 180:10 | 50:00 | 50:00 | 93.414 | 93.2796 | 182:20 | 182:20 | 93.8468 | 93.7728
53 | Athani | 6 | 6 | 47:18 | 142:10 | 30:39 | 57:21 | 88:00 | 525:08 | 135:18 | 22:33 | 98.0287 | 96.9691 | 667:18 | 111:13 | 97.0109 | 96.2016
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 6:40 | 10:35 | 17:15 | 110:10 | 17:15 | 8:38 | 98.8407 | 98.8407 | 110:10 | 55:05 | 98.1187 | 98.1187
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 65:00 | 46:18 | 111:18 | 441:58 | 111:18 | 22:16 | 97.0081 | 97.0081 | 441:58 | 88:24 | 96.9811 | 96.9811
56 | Sadalaga | 1 | 1 | 0:00 | 0:10 | 29:40 | 12:00 | 41:40 | 96:55 | 41:40 | 41:40 | 94.3996 | 94.3996 | 97:05 | 97:05 | 96.69 | 96.6843
57 | Muddebihal | 2 | 2 | 16:30 | 64:20 | 45:55 | 16:35 | 62:30 | 321:25 | 79:00 | 39:30 | 95.7997 | 94.6909 | 385:45 | 192:52 | 94.5113 | 93.4127
58 | Talikoti | 1 | 1 | 2:45 | 16:50 | 7:05 | 7:15 | 14:20 | 69:35 | 17:05 | 17:05 | 98.0735 | 97.7039 | 86:25 | 86:25 | 97.6235 | 97.0486
59 | B.Bagewadi | 1 | 1 | 6:13 | 14:10 | 1:30 | 0:00 | 1:30 | 35:17 | 7:43 | 7:43 | 99.7984 | 98.9628 | 49:27 | 49:27 | 98.795 | 98.3111
60 | Indi | 3 | 3 | 2:50 | 8:23 | 7:30 | 7:20 | 14:50 | 80:59 | 17:40 | 5:53 | 99.3354 | 99.2085 | 89:22 | 29:47 | 99.0781 | 98.9826
61 | Sindagi | 2 | 2 | 19:00 | 59:00 | 32:25 | 9:20 | 41:45 | 150:20 | 60:45 | 30:22 | 97.1942 | 95.9173 | 209:20 | 104:40 | 97.4328 | 96.4253
62 | Guledgudda | 1 | 1 | 2:41 | 7:35 | 12:14 | 5:15 | 17:29 | 108:46 | 20:10 | 20:10 | 97.6501 | 97.2894 | 116:21 | 116:21 | 96.2853 | 96.0263
63 | Ilkal | 8 | 8 | 21:45 | 165:47 | 134:36 | 126:19 | 260:55 | 1394:53 | 282:40 | 35:20 | 95.6163 | 95.2509 | 1560:40 | 195:05 | 94.0451 | 93.3373
64 | Kerur | 2 | 2 | 6:05 | 18:30 | 7:53 | 2:34 | 10:27 | 109:17 | 16:32 | 8:16 | 99.2977 | 98.8889 | 127:47 | 63:54 | 98.1338 | 97.8179
65 | Hungund | 4 | 4 | 8:12 | 80:12 | 65:13 | 39:35 | 104:48 | 416:49 | 113:00 | 28:15 | 96.4785 | 96.203 | 497:01 | 124:15 | 96.4411 | 95.7563
66 | Gaddankeri | 3 | 3 | 10:42 | 35:52 | 44:38 | 20:40 | 65:18 | 299:47 | 76:00 | 25:20 | 97.0744 | 96.595 | 335:39 | 111:53 | 96.5872 | 96.1788
67 | Rampur | 1 | 1 | 4:09 | 10:09 | 15:06 | 2:39 | 17:45 | 73:06 | 21:54 | 21:54 | 97.6142 | 97.0565 | 83:15 | 83:15 | 97.5034 | 97.1568
68 | Kaladagi | 2 | 2 | 6:45 | 12:27 | 20:42 | 8:51 | 29:33 | 181:06 | 36:18 | 18:09 | 98.0141 | 97.5605 | 193:33 | 96:46 | 96.9074 | 96.6948
69 | Achanur | 1 | 1 | 5:06 | 8:30 | 30:12 | 38:30 | 68:42 | 174:12 | 73:48 | 73:48 | 90.7661 | 90.0806 | 182:42 | 182:42 | 94.0505 | 93.7602
70 | Shirur | 1 | 1 | 11:27 | 34:41 | 0:00 | 21:06 | 21:06 | 123:13 | 32:33 | 32:33 | 97.164 | 95.625 | 157:54 | 157:54 | 95.7918 | 94.6072
71 | Badami | 1 | 1 | 3:30 | 15:55 | 14:43 | 5:11 | 19:54 | 106:00 | 23:24 | 23:24 | 97.3253 | 96.8548 | 121:55 | 121:55 | 96.3798 | 95.8362
72 | Kulageri | 1 | 1 | 1:50 | 10:41 | 4:20 | 2:55 | 7:15 | 32:30 | 9:05 | 9:05 | 99.0255 | 98.7791 | 43:11 | 43:11 | 98.89 | 98.5252
73 | Jamkhandi | 7 | 7 | 32:45 | 82:15 | 102:05 | 37:00 | 139:05 | 416:45 | 171:50 | 24:33 | 97.3294 | 96.7006 | 499:00 | 71:17 | 97.9667 | 97.5654
74 | Mahalingapur | 3 | 3 | 2:56 | 5:34 | 36:21 | 14:29 | 50:50 | 236:44 | 53:46 | 17:55 | 97.7225 | 97.5911 | 242:18 | 80:46 | 97.3049 | 97.2416
75 | Rabakavi | 2 | 2 | 2:40 | 16:45 | 9:45 | 7:15 | 17:00 | 75:40 | 19:40 | 9:50 | 98.8575 | 98.6783 | 92:25 | 46:12 | 98.7079 | 98.4218
76 | Banahatti | 2 | 2 | 4:10 | 10:20 | 30:30 | 2:20 | 32:50 | 104:05 | 37:00 | 18:30 | 97.7935 | 97.5134 | 114:25 | 57:13 | 98.2226 | 98.0462
77 | Terdal | 2 | 2 | 0:00 | 1:10 | 32:55 | 7:35 | 40:30 | 135:30 | 40:30 | 20:15 | 97.2782 | 97.2782 | 136:40 | 68:20 | 97.6861 | 97.6662
78 | Mudhol | 4 | 4 | 4:38 | 21:45 | 62:45 | 32:41 | 95:26 | 273:05 | 100:04 | 25:01 | 96.7932 | 96.6375 | 294:50 | 73:42 | 97.6683 | 97.4826
79 | Bilagi | 1 | 1 | 5:10 | 18:23 | 11:40 | 4:00 | 15:40 | 56:30 | 20:50 | 20:50 | 97.8943 | 97.1998 | 74:53 | 74:53 | 98.0704 | 97.4425
80 | Lokapur | 2 | 2 | 3:25 | 9:45 | 50:25 | 17:10 | 67:35 | 286:30 | 71:00 | 35:30 | 95.4581 | 95.2285 | 296:15 | 148:08 | 95.1076 | 94.9411
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of August-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of August-2021 |  |  |  | Reliability for cumulative period from Apr-21 to August-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 78 | 78 | 58:23 | 89:45 | 217:10 | 238:36 | 455:46 | 2918:03 | 514:09 | 6:35 | 99.2146 | 99.114 | 3007:48 | 38:34 | 98.9812 | 98.9498
2 | Dharwad(R) | 19 | 19 | 34:00 | 185:35 | 218:21 | 94:11 | 312:32 | 2449:48 | 346:32 | 18:14 | 97.7891 | 97.5486 | 2635:23 | 138:42 | 96.4886 | 96.2226
3 | Kundagol | 1 | 1 | 5:15 | 99:00 | 5:30 | 19:40 | 25:10 | 84:00 | 30:25 | 30:25 | 96.6174 | 95.9117 | 183:00 | 183:00 | 97.7124 | 95.0163
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 7:41 | 3:49 | 11:30 | 65:01 | 11:30 | 11:30 | 98.4543 | 98.4543 | 65:01 | 65:01 | 98.2294 | 98.2294
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 13:00 | 4:10 | 17:10 | 80:24 | 17:10 | 17:10 | 97.6927 | 97.6927 | 80:24 | 80:24 | 97.8105 | 97.8105
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 10:55 | 9:15 | 20:10 | 356:35 | 20:10 | 10:05 | 98.6447 | 98.6447 | 356:35 | 178:18 | 95.1446 | 95.1446
7 | Alnavar | 1 | 1 | 0:00 | 6:10 | 21:20 | 9:00 | 30:20 | 117:35 | 30:20 | 30:20 | 95.9229 | 95.9229 | 123:45 | 123:45 | 96.7978 | 96.6299
8 | Naragund | 2 | 2 | 2:40 | 38:20 | 10:35 | 7:45 | 18:20 | 231:05 | 21:00 | 10:30 | 98.7679 | 98.5887 | 269:25 | 134:42 | 96.8534 | 96.3315
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 16:20 | 28:10 | 44:30 | 334:40 | 44:30 | 11:08 | 98.5047 | 98.5047 | 334:40 | 83:40 | 97.7215 | 97.7215
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 40:54 | 19:39 | 60:33 | 453:13 | 60:33 | 15:08 | 97.9654 | 97.9654 | 453:13 | 113:18 | 96.9144 | 96.9144
11 | Naregal | 1 | 1 | 0:00 | 10:55 | 0:35 | 1:00 | 1:35 | 53:15 | 1:35 | 1:35 | 99.7872 | 99.7872 | 64:10 | 64:10 | 98.5498 | 98.2525
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 12:35 | 4:21 | 16:56 | 208:41 | 16:56 | 8:28 | 98.862 | 98.862 | 208:41 | 104:20 | 97.1585 | 97.1585
13 | Ron | 3 | 3 | 0:00 | 14:15 | 29:20 | 7:00 | 36:20 | 346:52 | 36:20 | 12:07 | 98.3722 | 98.3722 | 361:07 | 120:22 | 96.8512 | 96.7219
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 28:05 | 36:45 | 64:50 | 202:15 | 64:50 | 21:37 | 97.0953 | 97.0953 | 202:15 | 67:25 | 98.164 | 98.164
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 13:52 | 4:32 | 18:24 | 191:04 | 18:24 | 18:24 | 97.5269 | 97.5269 | 191:04 | 191:04 | 94.7967 | 94.7967
16 | G.C.T.M | 1 | 1 | 4:40 | 35:05 | 8:40 | 2:55 | 11:35 | 76:45 | 16:15 | 16:15 | 98.4431 | 97.8159 | 111:50 | 111:50 | 97.9099 | 96.9544
17 | F.C.S.M | 2 | 2 | 8:50 | 61:15 | 6:20 | 3:40 | 10:00 | 87:20 | 18:50 | 9:25 | 99.328 | 98.7343 | 148:35 | 74:18 | 98.8108 | 97.9768
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 2:55 | 4:07 | 7:02 | 51:45 | 7:02 | 7:02 | 99.0547 | 99.0547 | 51:45 | 51:45 | 98.5907 | 98.5907
19 | Hole-Alur | 1 | 1 | 4:55 | 61:55 | 5:55 | 0:20 | 6:15 | 60:25 | 11:10 | 11:10 | 99.1599 | 98.4991 | 122:20 | 122:20 | 98.3547 | 96.6685
20 | Savanur | 3 | 3 | 3:10 | 7:20 | 11:25 | 5:25 | 16:50 | 290:55 | 20:00 | 6:40 | 99.2458 | 99.1039 | 298:15 | 99:25 | 97.3591 | 97.2926
21 | Shiggaon | 2 | 2 | 3:20 | 17:40 | 17:10 | 26:50 | 44:00 | 335:50 | 47:20 | 23:40 | 97.043 | 96.819 | 353:30 | 176:45 | 95.4271 | 95.1865
22 | Bankapur | 1 | 1 | 10:10 | 42:40 | 17:55 | 3:45 | 21:40 | 130:20 | 31:50 | 31:50 | 97.0878 | 95.7213 | 173:00 | 173:00 | 96.4506 | 95.2887
23 | Hangal | 2 | 2 | 0:35 | 56:05 | 15:30 | 19:35 | 35:05 | 316:05 | 35:40 | 17:50 | 97.6422 | 97.603 | 372:10 | 186:05 | 95.696 | 94.9324
24 | Ranebennur | 16 | 16 | 19:50 | 76:16 | 127:51 | 43:32 | 171:23 | 999:46 | 191:13 | 11:57 | 98.5603 | 98.3937 | 1076:02 | 67:15 | 98.2983 | 98.1685
25 | Halageri | 2 | 2 | 13:10 | 168:15 | 32:15 | 0:40 | 32:55 | 366:05 | 46:05 | 23:02 | 97.7879 | 96.903 | 534:20 | 267:10 | 95.0152 | 92.7242
26 | Tuminakatti | 2 | 2 | 1:45 | 4:05 | 8:20 | 0:55 | 9:15 | 130:15 | 11:00 | 5:30 | 99.3784 | 99.2608 | 134:20 | 67:10 | 98.2264 | 98.1708
27 | Kahanderayanahalli | 1 | 1 | 1:40 | 5:27 | 8:30 | 1:15 | 9:45 | 313:45 | 11:25 | 11:25 | 98.6895 | 98.4655 | 319:12 | 319:12 | 91.4556 | 91.3072
28 | Rattihalli | 1 | 1 | 0:40 | 3:50 | 14:30 | 4:00 | 18:30 | 124:05 | 19:10 | 19:10 | 97.5134 | 97.4238 | 127:55 | 127:55 | 96.6208 | 96.5164
29 | Hirekerur | 2 | 2 | 5:30 | 43:45 | 31:00 | 5:50 | 36:50 | 275:40 | 42:20 | 21:10 | 97.5246 | 97.155 | 319:25 | 159:42 | 96.2464 | 95.6506
30 | Byadagi | 8 | 8 | 20:30 | 139:45 | 39:40 | 24:30 | 64:10 | 1255:00 | 84:40 | 10:35 | 98.9219 | 98.5775 | 1394:45 | 174:21 | 95.7278 | 95.2521
31 | Sirsi | 5 | 5 | 3:45 | 59:40 | 49:22 | 9:37 | 58:59 | 275:32 | 62:44 | 12:33 | 98.4144 | 98.3136 | 335:12 | 67:02 | 98.4993 | 98.1743
32 | Yellapur | 3 | 3 | 23:40 | 168:13 | 13:30 | 3:10 | 16:40 | 115:15 | 40:20 | 13:27 | 99.2533 | 98.193 | 283:28 | 94:29 | 98.9538 | 97.4268
33 | Mundagod | 3 | 3 | 10:30 | 17:18 | 68:18 | 9:50 | 78:08 | 391:01 | 88:38 | 29:33 | 96.4994 | 96.029 | 408:19 | 136:06 | 96.4505 | 96.2934
34 | Siddapur | 2 | 2 | 0:10 | 42:16 | 5:55 | 7:55 | 13:50 | 153:40 | 14:00 | 7:00 | 99.0703 | 99.0591 | 195:56 | 97:58 | 97.9076 | 97.3321
35 | Dandeli | 8 | 8 | 12:52 | 82:48 | 63:44 | 52:57 | 116:41 | 827:48 | 129:33 | 16:12 | 98.0396 | 97.8234 | 910:36 | 113:50 | 97.1821 | 96.9002
36 | Haliyal | 3 | 3 | 4:15 | 13:29 | 25:35 | 18:06 | 43:41 | 251:50 | 47:56 | 15:59 | 98.0429 | 97.8524 | 265:19 | 88:26 | 97.7139 | 97.5915
37 | Ankola | 3 | 3 | 14:55 | 134:37 | 30:48 | 38:12 | 69:00 | 209:05 | 83:55 | 27:58 | 96.9086 | 96.2403 | 343:42 | 114:34 | 98.102 | 96.88
38 | Kumta | 3 | 3 | 3:45 | 13:33 | 12:04 | 12:48 | 24:52 | 180:41 | 28:37 | 9:32 | 98.8859 | 98.7179 | 194:14 | 64:45 | 98.3598 | 98.2368
39 | Gokarna | 1 | 1 | 4:36 | 61:02 | 5:00 | 3:15 | 8:15 | 54:30 | 12:51 | 12:51 | 98.8911 | 98.2728 | 115:32 | 115:32 | 98.5158 | 96.8537
40 | Kasarkod | 1 | 1 | 13:57 | 160:26 | 6:13 | 9:57 | 16:10 | 106:37 | 30:07 | 30:07 | 97.8271 | 95.9521 | 267:03 | 267:03 | 97.0965 | 92.7274
41 | Honnavar | 3 | 3 | 3:51 | 33:18 | 18:09 | 10:52 | 29:01 | 330:49 | 32:52 | 10:57 | 98.7 | 98.5275 | 364:07 | 121:22 | 96.9969 | 96.6947
42 | Murdeshwar | 4 | 4 | 5:52 | 69:16 | 37:31 | 19:15 | 56:46 | 530:03 | 62:38 | 15:39 | 98.0925 | 97.8954 | 599:19 | 149:50 | 96.3913 | 95.9197
43 | Bhatkal | 3 | 3 | 25:48 | 162:47 | 25:16 | 4:57 | 30:13 | 215:48 | 56:01 | 18:40 | 98.6462 | 97.4903 | 378:35 | 126:12 | 98.041 | 96.5633
44 | Khanapur | 2 | 2 | 1:30 | 38:30 | 10:35 | 4:45 | 15:20 | 202:50 | 16:50 | 8:25 | 98.9695 | 98.8687 | 241:20 | 120:40 | 97.2381 | 96.7139
45 | Bailhongal | 3 | 3 | 0:00 | 56:31 | 98:16 | 40:30 | 138:46 | 729:51 | 138:46 | 46:15 | 93.7829 | 93.7829 | 786:22 | 262:07 | 93.3746 | 92.8616
46 | Soundatti | 3 | 3 | 0:00 | 20:28 | 39:34 | 6:16 | 45:50 | 352:58 | 45:50 | 15:17 | 97.9465 | 97.9465 | 373:26 | 124:29 | 96.7959 | 96.6101
47 | Ramdurg | 2 | 2 | 18:20 | 34:18 | 9:53 | 6:55 | 16:48 | 166:39 | 35:08 | 17:34 | 98.871 | 97.6389 | 200:57 | 100:28 | 97.7308 | 97.2638
48 | Gokak | 10 | 10 | 8:11 | 38:09 | 58:11 | 16:36 | 74:47 | 345:50 | 82:58 | 8:18 | 98.9948 | 98.8849 | 383:59 | 38:24 | 99.0582 | 98.9543
49 | Mudalagi | 2 | 2 | 12:10 | 19:55 | 25:45 | 7:20 | 33:05 | 180:30 | 45:15 | 22:38 | 97.7767 | 96.959 | 200:25 | 100:12 | 97.5422 | 97.271
50 | Konnur | 1 | 1 | 0:00 | 0:55 | 9:00 | 1:10 | 10:10 | 129:35 | 10:10 | 10:10 | 98.6335 | 98.6335 | 130:30 | 130:30 | 96.471 | 96.4461
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 19:30 | 17:58 | 37:28 | 171:19 | 37:28 | 37:28 | 94.9642 | 94.9642 | 171:19 | 171:19 | 95.3345 | 95.3345
52 | Kudachi | 1 | 1 | 0:05 | 2:15 | 47:50 | 6:10 | 54:00 | 234:10 | 54:05 | 54:05 | 92.7419 | 92.7307 | 236:25 | 236:25 | 93.6229 | 93.5616
53 | Athani | 7 | 7 | 9:22 | 151:32 | 42:05 | 36:14 | 78:19 | 603:27 | 87:41 | 12:32 | 98.4962 | 98.3164 | 754:59 | 107:51 | 97.6523 | 97.0628
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 6:10 | 6:35 | 12:45 | 122:55 | 12:45 | 6:22 | 99.1431 | 99.1431 | 122:55 | 61:28 | 98.3263 | 98.3263
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 29:35 | 17:00 | 46:35 | 488:33 | 46:35 | 9:19 | 98.7478 | 98.7478 | 488:33 | 97:43 | 97.3391 | 97.3391
56 | Sadalaga | 1 | 1 | 6:25 | 6:35 | 22:20 | 5:10 | 27:30 | 124:25 | 33:55 | 33:55 | 96.3038 | 95.4413 | 131:00 | 131:00 | 96.6117 | 96.4325
57 | Muddebihal | 2 | 2 | 2:10 | 66:30 | 31:25 | 9:00 | 40:25 | 361:50 | 42:35 | 21:18 | 97.2838 | 97.1382 | 428:20 | 214:10 | 95.0731 | 94.1676
58 | Talikoti | 1 | 1 | 2:05 | 18:55 | 11:30 | 7:00 | 18:30 | 88:05 | 20:35 | 20:35 | 97.5134 | 97.2334 | 107:00 | 107:00 | 97.6012 | 97.0861
59 | B.Bagewadi | 1 | 1 | 2:15 | 16:25 | 6:12 | 5:42 | 11:54 | 47:11 | 14:09 | 14:09 | 98.4005 | 98.0981 | 63:36 | 63:36 | 98.7151 | 98.268
60 | Indi | 3 | 3 | 0:00 | 8:23 | 33:19 | 3:31 | 36:50 | 117:49 | 36:50 | 12:17 | 98.3498 | 98.3498 | 126:12 | 42:04 | 98.9305 | 98.8544
61 | Sindagi | 2 | 2 | 1:20 | 60:20 | 34:35 | 4:30 | 39:05 | 189:25 | 40:25 | 20:12 | 97.3734 | 97.2838 | 249:45 | 124:52 | 97.4208 | 96.5993
62 | Guledgudda | 1 | 1 | 0:00 | 7:35 | 12:05 | 8:25 | 20:30 | 129:16 | 20:30 | 20:30 | 97.2446 | 97.2446 | 136:51 | 136:51 | 96.4797 | 96.2731
63 | Ilkal | 8 | 8 | 3:40 | 169:27 | 76:39 | 77:33 | 154:12 | 1549:05 | 157:52 | 19:44 | 97.4093 | 97.3477 | 1718:32 | 214:49 | 94.7267 | 94.1499
64 | Kerur | 2 | 2 | 7:25 | 25:55 | 9:13 | 9:28 | 18:41 | 127:58 | 26:06 | 13:03 | 98.7444 | 98.246 | 153:53 | 76:57 | 98.2575 | 97.9046
65 | Hungund | 4 | 4 | 0:00 | 80:12 | 67:47 | 35:18 | 103:05 | 519:54 | 103:05 | 25:46 | 96.5362 | 96.5362 | 600:06 | 150:02 | 96.4604 | 95.9144
66 | Gaddankeri | 3 | 3 | 3:00 | 38:52 | 35:30 | 31:36 | 67:06 | 366:53 | 70:06 | 23:22 | 96.9937 | 96.8593 | 405:45 | 135:15 | 96.6695 | 96.3167
67 | Rampur | 1 | 1 | 2:32 | 12:41 | 8:27 | 5:45 | 14:12 | 87:18 | 16:44 | 16:44 | 98.0914 | 97.7509 | 99:59 | 99:59 | 97.6225 | 97.2771
68 | Kaladagi | 2 | 2 | 10:54 | 23:21 | 5:51 | 25:03 | 30:54 | 212:00 | 41:48 | 20:54 | 97.9234 | 97.1909 | 235:21 | 117:40 | 97.1133 | 96.7953
69 | Achanur | 1 | 1 | 1:12 | 9:42 | 18:21 | 36:52 | 55:13 | 229:25 | 56:25 | 56:25 | 92.5784 | 92.4171 | 239:07 | 239:07 | 93.7523 | 93.4881
70 | Shirur | 1 | 1 | 3:24 | 38:05 | 0:27 | 21:45 | 22:12 | 145:25 | 25:36 | 25:36 | 97.0161 | 96.5591 | 183:30 | 183:30 | 96.0399 | 95.0027
71 | Badami | 1 | 1 | 0:33 | 16:28 | 14:05 | 8:22 | 22:27 | 128:27 | 23:00 | 23:00 | 96.9825 | 96.9086 | 144:55 | 144:55 | 96.5019 | 96.0535
72 | Kulageri | 1 | 1 | 1:28 | 12:09 | 3:30 | 0:55 | 4:25 | 36:55 | 5:53 | 5:53 | 99.4064 | 99.2092 | 49:04 | 49:04 | 98.9946 | 98.6638
73 | Jamkhandi | 7 | 7 | 5:15 | 87:30 | 42:15 | 12:00 | 54:15 | 471:00 | 59:30 | 8:30 | 98.9583 | 98.8575 | 558:30 | 79:47 | 98.1676 | 97.8272
74 | Mahalingapur | 3 | 3 | 0:00 | 5:34 | 36:54 | 8:02 | 44:56 | 281:40 | 44:56 | 14:59 | 97.9869 | 97.9869 | 287:14 | 95:45 | 97.4431 | 97.3926
75 | Rabakavi | 2 | 2 | 4:20 | 21:05 | 23:45 | 15:10 | 38:55 | 114:35 | 43:15 | 21:38 | 97.3846 | 97.0934 | 135:40 | 67:50 | 98.4398 | 98.1527
76 | Banahatti | 2 | 2 | 0:30 | 10:50 | 17:15 | 3:35 | 20:50 | 124:55 | 21:20 | 10:40 | 98.5999 | 98.5663 | 135:45 | 67:53 | 98.2991 | 98.1516
77 | Terdal | 2 | 2 | 2:35 | 3:45 | 33:10 | 4:35 | 37:45 | 173:15 | 40:20 | 20:10 | 97.463 | 97.2894 | 177:00 | 88:30 | 97.6409 | 97.5899
78 | Mudhol | 4 | 4 | 7:35 | 29:20 | 41:49 | 15:44 | 57:33 | 330:38 | 65:08 | 16:17 | 98.0662 | 97.8114 | 359:58 | 90:00 | 97.749 | 97.5492
79 | Bilagi | 1 | 1 | 0:15 | 18:38 | 22:03 | 4:55 | 26:58 | 83:28 | 27:13 | 27:13 | 96.3754 | 96.3418 | 102:06 | 102:06 | 97.7269 | 97.2195
80 | Lokapur | 2 | 2 | 0:45 | 10:30 | 33:00 | 4:45 | 37:45 | 324:15 | 38:30 | 19:15 | 97.463 | 97.4126 | 334:45 | 167:22 | 95.5848 | 95.4419
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]

## RURAL (Incl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2021 |  |  |  | Reliability for cumulative period from Apr-21 to Apr-21
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 585:45 | 585:45 | 5554:28 | 1642:49 | 7197:17 | 7197:17 | 7783:02 | 172:57 | 77.7862 | 75.9783 | 7783:02 | 172:57 | 77.7862 | 75.9783
2 | Dharwad Rural | 82 | 82 | 317:48 | 317:48 | 15560:04 | 3818:42 | 19378:46 | 19378:46 | 19696:34 | 240:12 | 67.1769 | 66.6386 | 19696:34 | 240:12 | 67.1769 | 66.6386
3 | Gadag | 94 | 94 | 64:50 | 64:50 | 18787:09 | 2671:07 | 21458:16 | 21458:16 | 21523:06 | 228:58 | 68.2945 | 68.1987 | 21523:06 | 228:58 | 68.2945 | 68.1987
4 | Ron | 53 | 53 | 326:45 | 326:45 | 12741:16 | 1064:51 | 13806:07 | 13806:07 | 14132:52 | 266:39 | 63.8204 | 62.9642 | 14132:52 | 266:39 | 63.8204 | 62.9642
5 | Haveri | 197 | 197 | 2306:56 | 2306:56 | 2377.6236 | 8476:46 | 2730.8222 | 2730.8222 | 2826.9444 | 344:24 | 53.7932 | 52.1668 | 2826.9444 | 344:24 | 53.7932 | 52.1668
6 | Ranebennur | 182 | 182 | 1162:15 | 1162:15 | 2360.775 | 6907:59 | 2648.6076 | 2648.6076 | 2697.0347 | 355:39 | 51.4907 | 50.6038 | 2697.0347 | 355:39 | 51.4907 | 50.6038
7 | Sirsi | 53 | 53 | 368:08 | 368:08 | 643:19 | 2016:24 | 2659:43 | 2659:43 | 3027:51 | 57:08 | 93.0301 | 92.0654 | 3027:51 | 57:08 | 93.0301 | 92.0654
8 | Dandeli | 22 | 22 | 87:36 | 87:36 | 291:20 | 437:31 | 728:51 | 728:51 | 816:27 | 37:07 | 95.3987 | 94.8456 | 816:27 | 37:07 | 95.3987 | 94.8456
9 | Karwar | 30 | 30 | 437:29 | 437:29 | 352:54 | 1336:01 | 1688:55 | 1688:55 | 2126:24 | 70:53 | 92.1809 | 90.1556 | 2126:24 | 70:53 | 92.1809 | 90.1556
10 | Honnavar | 40 | 40 | 373:59 | 373:59 | 416:55 | 558:15 | 975:10 | 975:10 | 1349:09 | 33:44 | 96.614 | 95.3155 | 1349:09 | 33:44 | 96.614 | 95.3155
11 | Belagavi | 138 | 138 | 379:44 | 379:44 | 1043.2799 | 2574:19 | 1150.5431 | 1150.5431 | 1166.3653 | 202:51 | 72.2091 | 71.8269 | 1166.3653 | 202:51 | 72.2091 | 71.8269
12 | Bailhongal | 191 | 191 | 2479:50 | 2479:50 | 1745.8528 | 3473:45 | 1890.5924 | 1890.5924 | 1993.9187 | 250:33 | 67.0054 | 65.2021 | 1993.9187 | 250:33 | 67.0054 | 65.2021
13 | Ramdurg | 76 | 76 | 682:35 | 682:35 | 23073:23 | 2266:12 | 1055.816 | 1055.816 | 1084.2569 | 342:24 | 53.6923 | 52.4449 | 1084.2569 | 342:24 | 53.6923 | 52.4449
14 | Ghataprabha | 160 | 160 | 248:53 | 248:53 | 1858.7028 | 1742:10 | 1931.2931 | 1931.2931 | 1941.6632 | 291:15 | 59.7647 | 59.5487 | 1941.6632 | 291:15 | 59.7647 | 59.5487
15 | Raibag | 169 | 169 | 548:16 | 548:16 | 2090.8139 | 1392:55 | 2148.8521 | 2148.8521 | 2171.6965 | 308:24 | 57.6163 | 57.1657 | 2171.6965 | 308:24 | 57.6163 | 57.1657
16 | Athani | 192 | 192 | 408:19 | 408:19 | 1745.2937 | 1745:05 | 1818.0056 | 1818.0056 | 1835.0187 | 229:23 | 68.4374 | 68.142 | 1835.0187 | 229:23 | 68.4374 | 68.142
17 | Chikkodi | 189 | 189 | 409:48 | 409:48 | 2203.7743 | 2237:39 | 2297.0097 | 2297.0097 | 2314.0847 | 293:51 | 59.4884 | 59.1872 | 2314.0847 | 293:51 | 59.4884 | 59.1872
18 | Vijayapur | 159 | 159 | 285:24 | 285:24 | 1990.0132 | 2504:08 | 2094.3521 | 2094.3521 | 2106.2438 | 317:55 | 56.0932 | 55.8439 | 2106.2438 | 317:55 | 56.0932 | 55.8439
19 | Indi | 249 | 249 | 1627:38 | 1627:38 | 3035.5813 | 4511:14 | 3223.5493 | 3223.5493 | 3291.3674 | 317:14 | 56.8467 | 55.9389 | 3291.3674 | 317:14 | 56.8467 | 55.9389
20 | B.Bagewadi | 138 | 138 | 696:55 | 696:55 | 1512.1236 | 2122:09 | 1600.5465 | 1600.5465 | 1629.5847 | 283:24 | 61.3395 | 60.6381 | 1629.5847 | 283:24 | 61.3395 | 60.6381
21 | Bagalkot | 185 | 185 | 926:37 | 926:37 | 2085.0819 | 3887:48 | 2247.0736 | 2247.0736 | 2285.6826 | 296:31 | 59.5122 | 58.8165 | 2285.6826 | 296:31 | 59.5122 | 58.8165
22 | Jamkhandi | 207 | 207 | 539:52 | 539:52 | 2697.3861 | 1261:30 | 2749.9486 | 2749.9486 | 2772.4431 | 321:27 | 55.7174 | 55.3552 | 2772.4431 | 321:27 | 55.7174 | 55.3552
23 | Mudhol | 192 | 192 | 599:35 | 599:35 | 2547.4257 | 1858:22 | 2624.8576 | 2624.8576 | 2649.8403 | 331:14 | 54.4296 | 53.9958 | 2649.8403 | 331:14 | 54.4296 | 53.9958
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2021 |  |  |  | Reliability for cumulative period from Apr-21 to May-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 345:25 | 931:10 | 4495:33 | 2416:31 | 6912:04 | 14109:21 | 7257:29 | 161:17 | 79.3546 | 78.3229 | 15040:31 | 334:14 | 78.5833 | 77.1698
2 | Dharwad Rural | 82 | 82 | 332:05 | 649:53 | 14567:51 | 5334:33 | 19902:24 | 1636.7153 | 20234:29 | 246:46 | 67.3774 | 66.8331 | 1663.7937 | 486:58 | 67.2788 | 66.7374
3 | Gadag | 96 | 96 | 209:06 | 273:56 | 17489:40 | 4432:54 | 21922:34 | 1807.5347 | 22131:40 | 230:32 | 69.3064 | 69.0137 | 1818.9486 | 454:44 | 69.1336 | 68.9387
4 | Ron | 54 | 54 | 194:07 | 520:52 | 12999:57 | 1905:37 | 14905:34 | 1196.3201 | 15099:41 | 279:37 | 62.8993 | 62.4162 | 1218.0229 | 541:21 | 63.6818 | 63.023
5 | Haveri | 197 | 197 | 2616:54 | 4923:50 | 2242.8437 | 17554:29 | 2974.2806 | 5705.1028 | 3083.3181 | 375:38 | 51.2972 | 49.5117 | 5910.2625 | 720:02 | 52.5247 | 50.8175
6 | Ranebennur | 182 | 182 | 1564:24 | 2726:39 | 2300.1451 | 12856:57 | 2835.8514 | 5484.459 | 2901.0347 | 382:33 | 49.7368 | 48.5814 | 5598.0694 | 738:12 | 50.5994 | 49.576
7 | Sirsi | 54 | 54 | 823:35 | 1191:43 | 785:34 | 3103:34 | 3889:08 | 6548:51 | 4712:43 | 87:16 | 90.3198 | 88.2698 | 7740:34 | 143:21 | 91.7162 | 90.2088
8 | Dandeli | 22 | 22 | 89:01 | 176:37 | 217:38 | 512:45 | 730:23 | 1459:14 | 819:24 | 37:15 | 95.5377 | 94.9939 | 1635:51 | 74:21 | 95.4693 | 94.921
9 | Karwar | 30 | 30 | 591:52 | 1029:21 | 819:00 | 1479:16 | 2298:16 | 3987:11 | 2890:08 | 96:20 | 89.7031 | 87.0514 | 5016:32 | 167:13 | 90.9217 | 88.578
10 | Honnavar | 40 | 40 | 904:45 | 1278:44 | 753:35 | 1417:50 | 2171:25 | 3146:35 | 3076:10 | 76:54 | 92.7036 | 89.6634 | 4425:19 | 110:38 | 94.6267 | 92.4431
11 | Belagavi | 139 | 139 | 537:31 | 917:15 | 19091:54 | 4483:06 | 23575:00 | 2132.8347 | 1004.6882 | 173:28 | 77.2037 | 76.684 | 2171.0535 | 374:51 | 74.8457 | 74.3949
12 | Bailhongal | 192 | 192 | 1911:22 | 4391:12 | 1722.1674 | 9036:49 | 2098.7014 | 3989.2937 | 2178.3417 | 272:18 | 64.7396 | 63.4015 | 4172.2604 | 521:32 | 65.9384 | 64.3762
13 | Ramdurg | 76 | 76 | 296:09 | 978:44 | 23346:07 | 3163:15 | 1104.5569 | 2160.3729 | 1116.8965 | 352:42 | 53.1173 | 52.5935 | 2201.1535 | 695:06 | 53.4001 | 52.5204
14 | Ghataprabha | 161 | 161 | 234:39 | 483:32 | 1762.6014 | 3548:34 | 1910.4583 | 3841.7514 | 1920.2354 | 286:15 | 61.7219 | 61.526 | 3861.8986 | 575:41 | 60.8823 | 60.6771
15 | Raibag | 176 | 176 | 403:40 | 951:56 | 1833.3431 | 2628:37 | 1942.8687 | 4091.7208 | 1959.6882 | 267:14 | 64.3902 | 64.082 | 4131.3847 | 563:22 | 61.8878 | 61.5184
16 | Athani | 194 | 194 | 1060:50 | 1469:09 | 1646.6417 | 2769:08 | 1762.0222 | 3580.0278 | 1806.2236 | 223:27 | 70.7013 | 69.9664 | 3641.2424 | 450:28 | 69.7479 | 69.2307
17 | Chikkodi | 190 | 190 | 860:20 | 1270:08 | 2109.0063 | 3240:56 | 2244.0451 | 4541.0549 | 2279.8924 | 287:59 | 61.9008 | 61.2922 | 4593.9771 | 580:18 | 60.8192 | 60.3626
18 | Vijayapur | 159 | 159 | 193:43 | 479:07 | 1817.5951 | 4837:01 | 2019.1375 | 4113.4896 | 2027.209 | 306:00 | 59.0356 | 58.8718 | 4133.4528 | 623:55 | 57.5885 | 57.3827
19 | Indi | 254 | 254 | 1265:07 | 2892:45 | 3059.1694 | 6792:26 | 3342.1875 | 6565.7368 | 3394.9007 | 320:47 | 57.5541 | 56.8847 | 6686.2681 | 631:46 | 57.624 | 56.8461
20 | B.Bagewadi | 138 | 138 | 408:09 | 1105:04 | 1519.2889 | 4411:40 | 1703.1083 | 3303.6549 | 1720.1146 | 299:09 | 60.1891 | 59.7916 | 3349.6993 | 582:33 | 60.7549 | 60.2079
21 | Bagalkot | 185 | 185 | 975:40 | 1902:17 | 1884.8472 | 8155:52 | 2224.675 | 4471.7486 | 2265.3278 | 293:53 | 61.2088 | 60.5 | 4551.0104 | 590:24 | 60.3744 | 59.672
22 | Jamkhandi | 207 | 207 | 321:57 | 861:49 | 2552.1354 | 2202:10 | 2643.8924 | 5393.841 | 2657.3069 | 308:06 | 58.7986 | 58.5896 | 5429.75 | 629:32 | 57.2833 | 56.9989
23 | Mudhol | 192 | 192 | 320:55 | 920:30 | 2673.3382 | 2845:01 | 2791.8806 | 5416.7382 | 2805.2521 | 350:39 | 53.0934 | 52.8687 | 5455.0924 | 681:53 | 53.7505 | 53.4231
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2021 |  |  |  | Reliability for cumulative period from Apr-21 to June-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 95:05 | 1026:15 | 4752:01 | 2152:30 | 6904:31 | 21013:52 | 6999:36 | 155:33 | 78.6898 | 78.3963 | 22040:07 | 489:47 | 78.6184 | 77.5742
2 | Dharwad Rural | 81 | 81 | 110:32 | 760:25 | 14638:41 | 3486:55 | 18125:36 | 2391.9486 | 18236:08 | 225:08 | 68.9204 | 68.7309 | 2423.6326 | 718:07 | 67.5492 | 67.1194
3 | Gadag | 98 | 98 | 52:25 | 326:21 | 15756:50 | 3470:18 | 19227:08 | 2608.6653 | 19279:33 | 196:44 | 72.7507 | 72.6764 | 2622.2632 | 642:11 | 70.7483 | 70.5958
4 | Ron | 54 | 54 | 293:05 | 813:57 | 11230:45 | 1140:30 | 12371:15 | 1711.7889 | 12664:20 | 234:31 | 68.1809 | 67.4271 | 1745.7035 | 775:52 | 65.1651 | 64.4749
5 | Haveri | 196 | 196 | 1351:53 | 6275:43 | 2094.0514 | 17410:54 | 2819.5056 | 8524.6083 | 2875.834 | 352:09 | 52.0492 | 51.0913 | 8786.0965 | 1075:51 | 52.2056 | 50.7395
6 | Ranebennur | 182 | 182 | 542:50 | 3269:29 | 2274.1194 | 10194:56 | 2698.9083 | 8183.3674 | 2721.5264 | 358:53 | 50.5694 | 50.1552 | 8319.5958 | 1097:05 | 50.5895 | 49.767
7 | Sirsi | 54 | 54 | 737:16 | 1928:59 | 1026:00 | 3492:24 | 4518:24 | 11067:15 | 5255:40 | 97:20 | 88.3786 | 86.4823 | 12996:14 | 240:40 | 90.6159 | 88.9803
8 | Dandeli | 22 | 22 | 345:38 | 522:15 | 282:41 | 645:37 | 928:18 | 2387:32 | 1273:56 | 57:54 | 94.1395 | 91.9575 | 2909:47 | 132:16 | 95.0309 | 93.944
9 | Karwar | 30 | 30 | 474:58 | 1504:19 | 468:19 | 633:22 | 1101:41 | 5088:52 | 1576:39 | 52:33 | 94.8996 | 92.7007 | 6593:11 | 219:46 | 92.2331 | 89.9371
10 | Honnavar | 40 | 40 | 524:11 | 1802:55 | 817:25 | 1357:17 | 2174:42 | 5321:17 | 2698:53 | 67:28 | 92.449 | 90.6289 | 7124:12 | 178:06 | 93.9088 | 91.845
11 | Belagavi | 139 | 139 | 254:31 | 1171:46 | 14899:51 | 3390:10 | 18290:01 | 2894.9187 | 18544:32 | 133:25 | 81.7246 | 81.4703 | 2943.7424 | 508:16 | 77.1135 | 76.7275
12 | Bailhongal | 192 | 192 | 1335:25 | 5726:37 | 1589.4125 | 7985:52 | 1922.1569 | 5911.4507 | 1977.7993 | 247:13 | 66.6292 | 65.6632 | 6150.0597 | 768:45 | 66.1661 | 64.8005
13 | Ramdurg | 76 | 76 | 359:00 | 1337:44 | 22255:56 | 3460:44 | 1071.5278 | 3231.9007 | 1086.4861 | 343:06 | 53.0032 | 52.3471 | 3287.6396 | 1038:12 | 53.2692 | 52.4633
14 | Ghataprabha | 161 | 161 | 173:24 | 656:56 | 1558.9778 | 2700:41 | 1671.5063 | 5513.2576 | 1678.7313 | 250:15 | 65.3932 | 65.2437 | 5540.6299 | 825:56 | 62.3694 | 62.1826
15 | Raibag | 176 | 176 | 289:54 | 1241:50 | 1599.2944 | 1692:24 | 1669.8111 | 5761.5319 | 1681.8903 | 229:21 | 68.3748 | 68.146 | 5813.275 | 792:43 | 64.0264 | 63.7033
16 | Athani | 194 | 194 | 667:32 | 2136:41 | 1438.5007 | 1890:56 | 1517.2896 | 5097.3174 | 1545.1035 | 191:09 | 73.9297 | 73.4518 | 5186.3458 | 641:37 | 71.1266 | 70.6223
17 | Chikkodi | 190 | 190 | 266:35 | 1536:43 | 1888.2528 | 2326:00 | 1985.1694 | 6526.2243 | 1996.2771 | 252:10 | 65.1725 | 64.9776 | 6590.2542 | 832:27 | 62.2543 | 61.884
18 | Vijayapur | 166 | 166 | 354:16 | 833:23 | 1600.4437 | 6059:39 | 1852.9292 | 5966.4187 | 1867.6903 | 270:02 | 62.7926 | 62.4962 | 6001.1431 | 867:38 | 60.503 | 60.2731
19 | Indi | 254 | 254 | 1118:39 | 4011:24 | 2558.0139 | 9719:14 | 2962.9819 | 9528.7188 | 3009.5924 | 284:22 | 61.1157 | 60.504 | 9695.8604 | 916:09 | 58.7751 | 58.052
20 | B.Bagewadi | 139 | 139 | 1367:18 | 2472:22 | 1387.7729 | 4805:03 | 1587.9833 | 4891.6382 | 1644.9542 | 284:01 | 61.9189 | 60.5527 | 4994.6535 | 862:23 | 61.3279 | 60.5135
21 | Bagalkot | 185 | 185 | 899:28 | 2801:45 | 1626.9167 | 8262:16 | 1971.1778 | 6442.9264 | 2008.6556 | 260:35 | 64.4833 | 63.808 | 6559.666 | 850:59 | 61.729 | 61.0355
22 | Jamkhandi | 207 | 207 | 450:58 | 1312:47 | 2321.2146 | 1826:03 | 2397.3 | 7791.141 | 2416.0903 | 280:08 | 61.3961 | 61.0936 | 7845.8403 | 909:40 | 58.6392 | 58.3488
23 | Mudhol | 192 | 192 | 210:43 | 1131:13 | 2585.6097 | 3526:57 | 2732.566 | 8149.3042 | 2741.3458 | 342:40 | 52.5596 | 52.4072 | 8196.4382 | 1024:33 | 53.3579 | 53.0882
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of July-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2021 |  |  |  | Reliability for cumulative period from Apr-21 to July-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 93:25 | 1119:40 | 4649:28 | 2251:22 | 6900:50 | 1163.1125 | 6994:15 | 155:26 | 79.3882 | 79.1092 | 1209.7653 | 645:12 | 78.814 | 77.9642
2 | Dharwad Rural | 81 | 81 | 95:04 | 855:29 | 15371:04 | 3664:06 | 19035:10 | 3185.0806 | 19130:14 | 236:11 | 68.4137 | 68.256 | 3220.7257 | 954:17 | 67.7689 | 67.4082
3 | Gadag | 98 | 98 | 83:10 | 409:31 | 16048:33 | 3181:16 | 19229:49 | 3409.9076 | 19312:59 | 197:04 | 73.626 | 73.5119 | 3426.9708 | 839:15 | 71.4795 | 71.3368
4 | Ron | 54 | 54 | 259:27 | 1073:24 | 10915:35 | 1173:26 | 12089:01 | 2215.4979 | 12348:28 | 228:41 | 69.9099 | 69.2641 | 2260.2229 | 1004:33 | 66.3707 | 65.6918
5 | Haveri | 198 | 198 | 671:52 | 6947:35 | 2262.9097 | 14591:25 | 2870.8854 | 11395.4937 | 2898.8799 | 351:23 | 53.2277 | 52.7716 | 11684.9764 | 1416:22 | 52.8254 | 51.627
6 | Ranebennur | 182 | 182 | 692:10 | 3961:39 | 2404.4972 | 9817:44 | 2813.5694 | 10996.9368 | 2842.4097 | 374:49 | 50.1317 | 49.6205 | 11162.0056 | 1471:55 | 50.4732 | 49.7298
7 | Sirsi | 54 | 54 | 362:05 | 2291:04 | 577:24 | 2910:38 | 3488:02 | 14555:17 | 3850:07 | 71:18 | 91.3181 | 90.4169 | 16846:21 | 311:58 | 90.7943 | 89.3453
8 | Dandeli | 22 | 22 | 129:20 | 651:35 | 364:49 | 837:17 | 1202:06 | 3589:38 | 1331:26 | 60:31 | 92.6558 | 91.8656 | 4241:13 | 192:47 | 94.4274 | 93.4159
9 | Karwar | 30 | 30 | 244:50 | 1749:09 | 586:47 | 1200:18 | 1787:05 | 6875:57 | 2031:55 | 67:44 | 91.9934 | 90.8964 | 8625:06 | 287:30 | 92.1722 | 90.1809
10 | Honnavar | 40 | 40 | 469:23 | 2272:18 | 528:23 | 873:42 | 1402:05 | 6723:22 | 1871:28 | 46:47 | 95.2887 | 93.7115 | 8995:40 | 224:54 | 94.2594 | 92.3193
11 | Belagavi | 142 | 142 | 780:43 | 1952:29 | 14502:52 | 3047:18 | 17550:10 | 3626.1757 | 18330:53 | 129:05 | 83.3881 | 82.6491 | 3707.5292 | 626:37 | 79.0685 | 78.5989
12 | Bailhongal | 192 | 192 | 1281:34 | 7008:11 | 1600.1437 | 6136:38 | 1855.8368 | 7767.2875 | 1909.2354 | 238:39 | 68.8199 | 67.9228 | 8059.2951 | 1007:25 | 66.8405 | 65.5939
13 | Ramdurg | 76 | 76 | 292:22 | 1630:06 | 23937:30 | 3155:42 | 1128.8833 | 4360.784 | 1141.0653 | 360:20 | 52.0847 | 51.5677 | 4428.7049 | 1398:32 | 52.9682 | 52.2357
14 | Ghataprabha | 162 | 162 | 249:00 | 905:56 | 1613.9292 | 3234:54 | 1748.7167 | 7261.9743 | 1759.0917 | 260:36 | 65.1789 | 64.9723 | 7299.7215 | 1081:26 | 63.2566 | 63.0656
15 | Raibag | 176 | 176 | 702:00 | 1943:50 | 1711.8062 | 2407:49 | 1812.1319 | 7573.6639 | 1841.3819 | 251:06 | 66.7864 | 66.2503 | 7654.6569 | 1043:49 | 64.7277 | 64.3505
16 | Athani | 194 | 194 | 732:04 | 2868:45 | 1578.5889 | 2082:07 | 1665.3438 | 6762.6611 | 1695.8465 | 209:48 | 72.3089 | 71.8017 | 6882.1924 | 851:24 | 71.427 | 70.922
17 | Chikkodi | 190 | 190 | 335:15 | 1871:58 | 1980.2694 | 3039:43 | 2106.9243 | 8633.1486 | 2120.8931 | 267:54 | 64.2288 | 63.9916 | 8711.1472 | 1100:21 | 62.756 | 62.4196
18 | Vijayapur | 166 | 166 | 380:45 | 1214:08 | 1631.1208 | 5489:01 | 1859.8299 | 7826.2486 | 1875.6944 | 271:11 | 63.8587 | 63.5504 | 7876.8375 | 1138:49 | 61.3557 | 61.1059
19 | Indi | 254 | 254 | 1330:55 | 5342:19 | 2718.5597 | 8312:16 | 3064.9042 | 12593.6229 | 3120.359 | 294:50 | 61.0756 | 60.3714 | 12816.2194 | 1210:59 | 59.3597 | 58.6413
20 | B.Bagewadi | 142 | 142 | 681:10 | 3153:32 | 1505.8104 | 4588:20 | 1696.991 | 6588.6292 | 1725.3729 | 291:37 | 61.4495 | 60.8048 | 6720.0264 | 1135:47 | 61.9682 | 61.2097
21 | Bagalkot | 185 | 185 | 800:22 | 3602:07 | 1594.8924 | 6917:28 | 1883.1201 | 8326.0465 | 1916.4688 | 248:37 | 67.1644 | 66.5829 | 8476.1347 | 1099:36 | 63.1101 | 62.4451
22 | Jamkhandi | 208 | 208 | 668:40 | 1981:27 | 2347.759 | 1916:40 | 2427.6201 | 10218.7611 | 2455.4812 | 283:19 | 62.3508 | 61.9187 | 10301.3215 | 1188:37 | 59.7306 | 59.4053
23 | Mudhol | 192 | 192 | 435:57 | 1567:10 | 2692.8653 | 3015:20 | 2818.5042 | 10967.8083 | 2836.6688 | 354:35 | 52.6461 | 52.3409 | 11033.1069 | 1379:08 | 53.177 | 52.8983
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of August-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of August-2021 |  |  |  | Reliability for cumulative period from Apr-21 to August-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 71:35 | 1191:15 | 5195:06 | 1847:37 | 7042:43 | 1456.559 | 7114:18 | 158:06 | 78.9644 | 78.7506 | 1506.1944 | 803:18 | 78.8445 | 78.1235
2 | Dharwad Rural | 81 | 81 | 56:46 | 912:15 | 15664:30 | 1759:04 | 17423:34 | 3911.0625 | 17480:20 | 215:48 | 71.0879 | 70.9937 | 3949.0729 | 1170:06 | 68.4414 | 68.1346
3 | Gadag | 98 | 98 | 46:20 | 455:51 | 19375:33 | 2243:19 | 21618:52 | 4310.6938 | 21665:12 | 221:04 | 70.3494 | 70.2858 | 4329.6875 | 1060:20 | 71.2505 | 71.1239
4 | Ron | 54 | 54 | 61:25 | 1134:49 | 8238:15 | 501:20 | 8739:35 | 2579.6472 | 8801:00 | 162:59 | 78.2468 | 78.0939 | 2626.9313 | 1167:32 | 68.777 | 68.2047
5 | Haveri | 197 | 197 | 800:48 | 7748:23 | 2392.2924 | 8576:39 | 2749.6528 | 14145.1465 | 2783.0194 | 339:03 | 54.9754 | 54.429 | 14467.9958 | 1762:36 | 53.0701 | 51.999
6 | Ranebennur | 182 | 182 | 507:24 | 4469:03 | 2495.6 | 5217:06 | 2712.9792 | 13709.916 | 2734.1208 | 360:33 | 51.9146 | 51.5399 | 13896.1264 | 1832:27 | 50.7652 | 50.0965
7 | Sirsi | 54 | 54 | 271:19 | 2562:23 | 533:51 | 1378:00 | 1911:51 | 16467:08 | 2183:10 | 40:26 | 95.2413 | 94.566 | 19029:31 | 352:24 | 91.6953 | 90.4031
8 | Dandeli | 22 | 22 | 69:56 | 721:31 | 254:16 | 463:36 | 717:52 | 4307:30 | 787:48 | 35:49 | 95.6142 | 95.187 | 5029:01 | 228:36 | 94.6679 | 93.7747
9 | Karwar | 30 | 30 | 265:47 | 2014:56 | 326:02 | 480:36 | 806:38 | 7682:35 | 1072:25 | 35:45 | 96.3861 | 95.1953 | 9697:31 | 323:15 | 93.026 | 91.1969
10 | Honnavar | 40 | 40 | 285:02 | 2557:20 | 569:25 | 526:02 | 1095:27 | 7818:49 | 1380:29 | 34:31 | 96.3191 | 95.3613 | 10376:09 | 259:24 | 94.6767 | 92.9356
11 | Belagavi | 142 | 142 | 391:31 | 2344:00 | 22082:29 | 1673:22 | 23755:51 | 4616.0028 | 1006.1403 | 170:03 | 77.5142 | 77.1436 | 4713.6694 | 796:41 | 78.7536 | 78.304
12 | Bailhongal | 192 | 192 | 965:33 | 7973:44 | 1829.8507 | 3026:37 | 1955.9597 | 9723.2472 | 1996.191 | 249:31 | 67.1378 | 66.4618 | 10055.4861 | 1256:56 | 66.9007 | 65.7697
13 | Ramdurg | 78 | 78 | 386:55 | 2017:01 | 1023.4715 | 2282:11 | 1118.5625 | 5479.3465 | 1134.684 | 349:08 | 53.7402 | 53.0734 | 5563.3889 | 1711:49 | 54.0863 | 53.382
14 | Ghataprabha | 162 | 162 | 182:12 | 1088:08 | 1838.4778 | 1250:35 | 1890.5854 | 9152.5597 | 1898.1771 | 281:13 | 62.3539 | 62.2028 | 9197.8986 | 1362:39 | 63.0737 | 62.8908
15 | Raibag | 176 | 176 | 374:49 | 2318:39 | 1677.8417 | 1179:54 | 1727.0042 | 9300.6681 | 1742.6215 | 237:38 | 68.3467 | 68.0605 | 9397.2785 | 1281:27 | 65.461 | 65.1022
16 | Athani | 197 | 197 | 728:11 | 3596:56 | 1602.6042 | 1419:21 | 1661.7438 | 8424.4049 | 1692.0847 | 206:09 | 72.7895 | 72.2927 | 8574.2771 | 1044:35 | 72.05 | 71.5528
17 | Chikkodi | 190 | 190 | 142:40 | 2014:38 | 1703.4687 | 892:44 | 1740.666 | 10373.8146 | 1746.6104 | 220:37 | 70.4471 | 70.3462 | 10457.7576 | 1320:59 | 64.3144 | 64.0256
18 | Vijayapur | 173 | 173 | 416:33 | 1630:41 | 1920.3292 | 5390:02 | 2144.9139 | 9971.1625 | 2162.2701 | 299:58 | 60.0053 | 59.6817 | 10039.1076 | 1392:43 | 62.3289 | 62.0722
19 | Indi | 254 | 254 | 524:50 | 5867:09 | 2816.7715 | 7258:48 | 3119.2215 | 15712.8444 | 3141.0896 | 296:48 | 60.3858 | 60.1081 | 15957.309 | 1507:47 | 59.5676 | 58.9385
20 | B.Bagewadi | 142 | 142 | 284:18 | 3437:50 | 1533.3076 | 2983:21 | 1657.6139 | 8246.2431 | 1669.4597 | 282:10 | 62.3441 | 62.075 | 8389.4861 | 1417:56 | 62.0444 | 61.385
21 | Bagalkot | 187 | 187 | 462:46 | 4064:53 | 1685.9424 | 4885:10 | 1889.491 | 10215.5375 | 1908.7729 | 244:59 | 67.4057 | 67.0731 | 10384.9076 | 1332:49 | 64.2951 | 63.7031
22 | Jamkhandi | 210 | 210 | 792:19 | 2773:46 | 2329.3014 | 1436:09 | 2389.141 | 12607.9021 | 2422.1542 | 276:49 | 63.3004 | 62.7933 | 12723.4757 | 1454:07 | 60.7597 | 60.4
23 | Mudhol | 192 | 192 | 176:02 | 1743:12 | 2644.666 | 2264:56 | 2739.0382 | 13706.8465 | 2746.3729 | 343:18 | 53.9812 | 53.858 | 13779.4799 | 1722:26 | 53.34 | 53.0927
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]

## RURAL(Excl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of April-2021 |  |  |  | Reliability for cumulative period from Apr-21 to Apr-21
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 584:55 | 584:55 | 956:02 | 1642:49 | 2598:51 | 2598:51 | 3183:46 | 70:45 | 91.9789 | 90.1736 | 3183:46 | 70:45 | 91.9789 | 90.1736
2 | Dharwad Rural | 82 | 82 | 317:48 | 317:48 | 1961:00 | 3818:42 | 5779:42 | 5779:42 | 6097:30 | 74:22 | 90.2105 | 89.6723 | 6097:30 | 74:22 | 90.2105 | 89.6723
3 | Gadag | 94 | 94 | 64:50 | 64:50 | 1351:44 | 2671:07 | 4022:51 | 4022:51 | 4087:41 | 43:29 | 94.0561 | 93.9603 | 4087:41 | 43:29 | 94.0561 | 93.9603
4 | Ron | 53 | 53 | 326:45 | 326:45 | 727:51 | 1064:51 | 1792:42 | 1792:42 | 2119:27 | 39:59 | 95.3021 | 94.4459 | 2119:27 | 39:59 | 95.3021 | 94.4459
5 | Haveri | 197 | 197 | 2306:56 | 2306:56 | 2873:41 | 8476:46 | 11350:27 | 11350:27 | 13657:23 | 69:20 | 91.9977 | 90.3713 | 13657:23 | 69:20 | 91.9977 | 90.3713
6 | Ranebennur | 182 | 182 | 1162:15 | 1162:15 | 4092:13 | 6907:59 | 11000:12 | 11000:12 | 12162:27 | 66:50 | 91.6055 | 90.7185 | 12162:27 | 66:50 | 91.6055 | 90.7185
7 | Sirsi | 53 | 53 | 368:08 | 368:08 | 643:19 | 2016:24 | 2659:43 | 2659:43 | 3027:51 | 57:08 | 93.0301 | 92.0654 | 3027:51 | 57:08 | 93.0301 | 92.0654
8 | Dandeli | 22 | 22 | 87:36 | 87:36 | 291:20 | 437:31 | 728:51 | 728:51 | 816:27 | 37:07 | 95.3987 | 94.8456 | 816:27 | 37:07 | 95.3987 | 94.8456
9 | Karwar | 30 | 30 | 437:29 | 437:29 | 352:54 | 1336:01 | 1688:55 | 1688:55 | 2126:24 | 70:53 | 92.1809 | 90.1556 | 2126:24 | 70:53 | 92.1809 | 90.1556
10 | Honnavar | 40 | 40 | 373:59 | 373:59 | 416:55 | 558:15 | 975:10 | 975:10 | 1349:09 | 33:44 | 96.614 | 95.3155 | 1349:09 | 33:44 | 96.614 | 95.3155
11 | Belagavi | 138 | 138 | 379:44 | 379:44 | 3301:53 | 2574:19 | 5876:12 | 5876:12 | 6255:56 | 45:20 | 94.086 | 93.7038 | 6255:56 | 45:20 | 94.086 | 93.7038
12 | Bailhongal | 191 | 191 | 2479:50 | 2479:50 | 2456:45 | 3473:45 | 5930:30 | 5930:30 | 8410:20 | 44:02 | 95.6875 | 93.8843 | 8410:20 | 44:02 | 95.6875 | 93.8843
13 | Ramdurg | 76 | 76 | 682:35 | 682:35 | 1419:58 | 2266:12 | 3686:10 | 3686:10 | 4368:45 | 57:29 | 93.2636 | 92.0162 | 4368:45 | 57:29 | 93.2636 | 92.0162
14 | Ghataprabha | 160 | 160 | 248:53 | 248:53 | 1406:32 | 1742:10 | 3148:42 | 3148:42 | 3397:35 | 21:14 | 97.2668 | 97.0507 | 3397:35 | 21:14 | 97.2668 | 97.0507
15 | Raibag | 169 | 169 | 548:16 | 548:16 | 4626:08 | 1392:55 | 6019:03 | 6019:03 | 6567:19 | 38:52 | 95.0534 | 94.6028 | 6567:19 | 38:52 | 95.0534 | 94.6028
16 | Athani | 192 | 192 | 408:19 | 408:19 | 3000:23 | 1745:05 | 4745:28 | 4745:28 | 5153:47 | 26:51 | 96.5672 | 96.2719 | 5153:47 | 26:51 | 96.5672 | 96.2719
17 | Chikkodi | 189 | 189 | 409:48 | 409:48 | 1710:27 | 2237:39 | 3948:06 | 3948:06 | 4357:54 | 23:03 | 97.0987 | 96.7975 | 4357:54 | 23:03 | 97.0987 | 96.7975
18 | Vijayapur | 159 | 159 | 285:24 | 285:24 | 1273:54 | 2504:08 | 3778:02 | 3778:02 | 4063:26 | 25:33 | 96.6998 | 96.4505 | 4063:26 | 25:33 | 96.6998 | 96.4505
19 | Indi | 249 | 249 | 1627:38 | 1627:38 | 3647:50 | 4511:14 | 8159:04 | 8159:04 | 9786:42 | 39:18 | 95.449 | 94.5411 | 9786:42 | 39:18 | 95.449 | 94.5411
20 | B.Bagewadi | 138 | 138 | 696:55 | 696:55 | 1732:23 | 2122:09 | 3854:32 | 3854:32 | 4551:27 | 32:59 | 96.1206 | 95.4192 | 4551:27 | 32:59 | 96.1206 | 95.4192
21 | Bagalkot | 185 | 185 | 926:37 | 926:37 | 3165:28 | 3887:48 | 7053:16 | 7053:16 | 7979:53 | 43:08 | 94.7048 | 94.0091 | 7979:53 | 43:08 | 94.7048 | 94.0091
22 | Jamkhandi | 207 | 207 | 539:52 | 539:52 | 2082:33 | 1261:30 | 3344:03 | 3344:03 | 3883:55 | 18:46 | 97.7563 | 97.394 | 3883:55 | 18:46 | 97.7563 | 97.394
23 | Mudhol | 192 | 192 | 599:35 | 599:35 | 1788:03 | 1858:22 | 3646:25 | 3646:25 | 4246:00 | 22:07 | 97.3623 | 96.9285 | 4246:00 | 22:07 | 97.3623 | 96.9285
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of May-2021 |  |  |  | Reliability for cumulative period from Apr-21 to May-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 345:25 | 930:20 | 857:21 | 2416:31 | 3273:52 | 5872:43 | 3619:17 | 80:26 | 90.2214 | 89.1897 | 6803:03 | 151:11 | 91.0857 | 89.6736
2 | Dharwad Rural | 82 | 82 | 332:05 | 649:53 | 2072:33 | 5334:33 | 7407:06 | 13186:48 | 7739:11 | 94:23 | 87.8588 | 87.3145 | 13836:41 | 168:44 | 89.0154 | 88.474
3 | Gadag | 96 | 96 | 209:06 | 273:56 | 1659:27 | 4432:54 | 6092:21 | 10115:12 | 6301:27 | 65:38 | 91.4702 | 91.1774 | 10389:08 | 108:13 | 92.8028 | 92.6079
4 | Ron | 54 | 54 | 194:07 | 520:52 | 1007:12 | 1905:37 | 2912:49 | 4705:31 | 3106:56 | 57:32 | 92.7499 | 92.2667 | 5226:23 | 96:47 | 94.0479 | 93.389
5 | Haveri | 197 | 197 | 2616:54 | 4923:50 | 4744:23 | 17554:29 | 22298:52 | 1402.0549 | 1038.1569 | 126:29 | 84.786 | 83.0005 | 1607.2146 | 195:48 | 88.3327 | 86.6255
6 | Ranebennur | 182 | 182 | 1564:24 | 2726:39 | 5561:13 | 12856:57 | 18418:10 | 1225.7653 | 19982:34 | 109:48 | 86.398 | 85.2427 | 1339.3757 | 176:37 | 88.9591 | 87.9357
7 | Sirsi | 54 | 54 | 823:35 | 1191:43 | 785:34 | 3103:34 | 3889:08 | 6548:51 | 4712:43 | 87:16 | 90.3198 | 88.2698 | 7740:34 | 143:21 | 91.7162 | 90.2088
8 | Dandeli | 22 | 22 | 89:01 | 176:37 | 215:38 | 512:45 | 728:23 | 1457:14 | 817:24 | 37:09 | 95.55 | 95.0061 | 1633:51 | 74:16 | 95.4756 | 94.9272
9 | Karwar | 30 | 30 | 591:52 | 1029:21 | 819:00 | 1479:16 | 2298:16 | 3987:11 | 2890:08 | 96:20 | 89.7031 | 87.0514 | 5016:32 | 167:13 | 90.9217 | 88.578
10 | Honnavar | 40 | 40 | 904:45 | 1278:44 | 753:35 | 1417:50 | 2171:25 | 3146:35 | 3076:10 | 76:54 | 92.7036 | 89.6634 | 4425:19 | 110:38 | 94.6267 | 92.4431
11 | Belagavi | 139 | 139 | 537:31 | 917:15 | 2947:42 | 4483:06 | 7430:48 | 13307:00 | 7968:19 | 57:20 | 92.8147 | 92.2949 | 14224:15 | 102:20 | 93.4608 | 93.0101
12 | Bailhongal | 192 | 192 | 1911:22 | 4391:12 | 2935:07 | 9036:49 | 11971:56 | 17902:26 | 13883:18 | 72:19 | 91.6191 | 90.2811 | 22293:38 | 116:07 | 93.631 | 92.0688
13 | Ramdurg | 76 | 76 | 296:09 | 978:44 | 1660:19 | 3163:15 | 4823:34 | 8509:44 | 5119:43 | 67:22 | 91.4694 | 90.9456 | 9488:28 | 124:51 | 92.3518 | 91.4721
14 | Ghataprabha | 161 | 161 | 234:39 | 483:32 | 1640:33 | 3548:34 | 5189:07 | 8337:49 | 5423:46 | 33:41 | 95.6679 | 95.472 | 8821:21 | 54:47 | 96.4626 | 96.2574
15 | Raibag | 176 | 176 | 403:40 | 951:56 | 5242:50 | 2628:37 | 7871:27 | 13890:30 | 8275:07 | 47:01 | 93.9887 | 93.6804 | 14842:26 | 84:20 | 94.6091 | 94.2396
16 | Athani | 194 | 194 | 1060:50 | 1469:09 | 3284:57 | 2769:08 | 6054:05 | 10799:33 | 7114:55 | 36:40 | 95.8056 | 95.0706 | 12268:42 | 63:14 | 96.1976 | 95.6803
17 | Chikkodi | 190 | 190 | 860:20 | 1270:08 | 2242:22 | 3240:56 | 5483:18 | 9431:24 | 6343:38 | 33:23 | 96.121 | 95.5124 | 10701:32 | 56:19 | 96.6094 | 96.1527
18 | Vijayapur | 159 | 159 | 193:43 | 479:07 | 1843:46 | 4837:01 | 6680:47 | 10458:49 | 6874:30 | 43:14 | 94.3525 | 94.1887 | 10937:56 | 68:48 | 95.5069 | 95.3011
19 | Indi | 254 | 254 | 1265:07 | 2892:45 | 3532:05 | 6792:26 | 10324:31 | 18483:35 | 11589:38 | 45:38 | 94.5366 | 93.8671 | 21376:20 | 84:10 | 95.0294 | 94.2514
20 | B.Bagewadi | 138 | 138 | 408:09 | 1105:04 | 2471:21 | 4411:40 | 6883:01 | 10737:33 | 7291:10 | 52:50 | 93.2961 | 92.8986 | 11842:37 | 85:49 | 94.6852 | 94.1382
21 | Bagalkot | 185 | 185 | 975:40 | 1902:17 | 4408:55 | 8155:52 | 12564:47 | 19618:03 | 13540:27 | 73:11 | 90.8713 | 90.1624 | 21520:20 | 116:20 | 92.7566 | 92.0542
22 | Jamkhandi | 207 | 207 | 321:57 | 861:49 | 2086:05 | 2202:10 | 4288:15 | 7632:18 | 4610:12 | 22:16 | 97.2156 | 97.0065 | 8494:07 | 41:02 | 97.4815 | 97.1971
23 | Mudhol | 192 | 192 | 320:55 | 920:30 | 2027:13 | 2845:01 | 4872:14 | 8518:39 | 5193:09 | 27:03 | 96.5892 | 96.3646 | 9439:09 | 49:10 | 96.9694 | 96.6419
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of June-2021 |  |  |  | Reliability for cumulative period from Apr-21 to June-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 95:05 | 1025:25 | 1251:29 | 2152:30 | 3403:59 | 9276:42 | 3499:04 | 77:45 | 89.4939 | 89.2004 | 10302:07 | 228:56 | 90.5609 | 89.5176
2 | Dharwad Rural | 81 | 81 | 110:32 | 760:25 | 1841:45 | 3486:55 | 5328:40 | 18515:28 | 5439:12 | 67:09 | 90.8631 | 90.6735 | 19275:53 | 237:58 | 89.5336 | 89.1038
3 | Gadag | 98 | 98 | 52:25 | 326:21 | 2425:07 | 3470:18 | 5895:25 | 16010:37 | 5947:50 | 60:42 | 91.6448 | 91.5705 | 16336:58 | 166:42 | 92.5195 | 92.367
4 | Ron | 54 | 54 | 293:05 | 813:57 | 830:25 | 1140:30 | 1970:55 | 6676:26 | 2264:00 | 41:56 | 94.9308 | 94.177 | 7490:23 | 138:43 | 94.3389 | 93.6488
5 | Haveri | 196 | 196 | 1351:53 | 6275:43 | 3361:49 | 17410:54 | 20772:43 | 2267.5847 | 22124:36 | 112:53 | 85.2801 | 84.3221 | 2529.0729 | 309:41 | 87.2865 | 85.8204
6 | Ranebennur | 182 | 182 | 542:50 | 3269:29 | 4781:39 | 10194:56 | 14976:35 | 1849.7896 | 15519:25 | 85:16 | 88.571 | 88.1567 | 1986.0181 | 261:54 | 88.8311 | 88.0086
7 | Sirsi | 54 | 54 | 737:16 | 1928:59 | 1026:00 | 3492:24 | 4518:24 | 11067:15 | 5255:40 | 97:20 | 88.3786 | 86.4823 | 12996:14 | 240:40 | 90.6159 | 88.9803
8 | Dandeli | 22 | 22 | 345:38 | 522:15 | 282:41 | 645:37 | 928:18 | 2385:32 | 1273:56 | 57:54 | 94.1395 | 91.9575 | 2907:47 | 132:10 | 95.0351 | 93.9482
9 | Karwar | 30 | 30 | 474:58 | 1504:19 | 468:19 | 633:22 | 1101:41 | 5088:52 | 1576:39 | 52:33 | 94.8996 | 92.7007 | 6593:11 | 219:46 | 92.2331 | 89.9371
10 | Honnavar | 40 | 40 | 524:11 | 1802:55 | 817:25 | 1357:17 | 2174:42 | 5321:17 | 2698:53 | 67:28 | 92.449 | 90.6289 | 7124:12 | 178:06 | 93.9088 | 91.845
11 | Belagavi | 139 | 139 | 254:31 | 1171:46 | 2929:35 | 3390:10 | 6319:45 | 19626:45 | 6574:16 | 47:18 | 93.6853 | 93.431 | 20798:31 | 149:38 | 93.5348 | 93.1488
12 | Bailhongal | 192 | 192 | 1335:25 | 5726:37 | 3566:16 | 7985:52 | 11552:08 | 1227.2736 | 12887:33 | 67:07 | 91.6434 | 90.6774 | 1465.8826 | 183:14 | 92.9758 | 91.6101
13 | Ramdurg | 76 | 76 | 359:00 | 1337:44 | 1456:51 | 3460:44 | 4917:35 | 13427:19 | 5276:35 | 69:26 | 91.0132 | 90.3571 | 14765:03 | 194:17 | 91.9105 | 91.1045
14 | Ghataprabha | 161 | 161 | 173:24 | 656:56 | 1422:15 | 2700:41 | 4122:56 | 12460:45 | 4296:20 | 26:41 | 96.4433 | 96.2937 | 13117:41 | 81:29 | 96.4562 | 96.2694
15 | Raibag | 176 | 176 | 289:54 | 1241:50 | 4980:59 | 1692:24 | 6673:23 | 20563:53 | 6963:17 | 39:34 | 94.7338 | 94.505 | 21805:43 | 123:54 | 94.6502 | 94.3271
16 | Athani | 194 | 194 | 667:32 | 2136:41 | 3211:25 | 1890:56 | 5102:21 | 15901:54 | 5769:53 | 29:44 | 96.3471 | 95.8692 | 18038:35 | 92:59 | 96.2469 | 95.7426
17 | Chikkodi | 190 | 190 | 266:35 | 1536:43 | 1769:35 | 2326:00 | 4095:35 | 13526:59 | 4362:10 | 22:58 | 97.0062 | 96.8113 | 15063:42 | 79:17 | 96.7402 | 96.3698
18 | Vijayapur | 166 | 166 | 354:16 | 833:23 | 2637:35 | 6059:39 | 8697:14 | 19156:03 | 9051:30 | 54:32 | 92.7232 | 92.4268 | 19989:26 | 120:25 | 94.7162 | 94.4863
19 | Indi | 254 | 254 | 1118:39 | 4011:24 | 4127:09 | 9719:14 | 13846:23 | 1347.0819 | 14965:02 | 58:55 | 92.4287 | 91.817 | 1514.2236 | 143:05 | 94.172 | 93.4489
20 | B.Bagewadi | 139 | 139 | 1367:18 | 2472:22 | 2516:08 | 4805:03 | 7321:11 | 18058:44 | 8688:29 | 62:30 | 92.6847 | 91.3185 | 20531:06 | 147:42 | 94.0513 | 93.2369
21 | Bagalkot | 185 | 185 | 899:28 | 2801:45 | 4764:24 | 8262:16 | 13026:40 | 1360.1965 | 13926:08 | 75:17 | 90.2202 | 89.5449 | 1476.9361 | 191:36 | 91.9204 | 91.227
22 | Jamkhandi | 207 | 207 | 450:58 | 1312:47 | 2123:00 | 1826:03 | 3949:03 | 11581:21 | 4400:01 | 21:15 | 97.3503 | 97.0478 | 12894:08 | 62:17 | 97.4383 | 97.1479
23 | Mudhol | 192 | 192 | 210:43 | 1131:13 | 2707:54 | 3526:57 | 6234:51 | 14753:30 | 6445:34 | 33:34 | 95.4898 | 95.3374 | 15884:43 | 82:44 | 96.4816 | 96.2119
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of July-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of July-2021 |  |  |  | Reliability for cumulative period from Apr-21 to July-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 93:25 | 1118:50 | 813:25 | 2251:22 | 3064:47 | 12341:29 | 3158:12 | 70:11 | 90.8459 | 90.5669 | 13460:19 | 299:07 | 90.6334 | 89.7842
2 | Dharwad Rural | 81 | 81 | 95:04 | 855:29 | 1822:48 | 3664:06 | 5486:54 | 1000.0986 | 5581:58 | 68:55 | 90.8952 | 90.7375 | 1035.7437 | 306:53 | 89.8796 | 89.5189
3 | Gadag | 98 | 98 | 83:10 | 409:31 | 1737:37 | 3181:16 | 4918:53 | 20929:30 | 5002:03 | 51:02 | 93.2537 | 93.1396 | 21339:01 | 217:45 | 92.7061 | 92.5634
4 | Ron | 54 | 54 | 259:27 | 1073:24 | 962:05 | 1173:26 | 2135:31 | 8811:57 | 2394:58 | 44:21 | 94.6846 | 94.0388 | 9885:21 | 183:04 | 94.4268 | 93.7479
5 | Haveri | 198 | 198 | 671:52 | 6947:35 | 3060:03 | 14591:25 | 17651:28 | 3003.0625 | 18323:20 | 92:33 | 88.0176 | 87.5615 | 3292.5451 | 399:06 | 87.568 | 86.3697
6 | Ranebennur | 182 | 182 | 692:10 | 3961:39 | 3978:32 | 9817:44 | 13796:16 | 2424.634 | 14488:26 | 79:36 | 89.8113 | 89.3002 | 2589.7028 | 341:30 | 89.0802 | 88.3368
7 | Sirsi | 54 | 54 | 362:05 | 2291:04 | 577:24 | 2910:38 | 3488:02 | 14555:17 | 3850:07 | 71:18 | 91.3181 | 90.4169 | 16846:21 | 311:58 | 90.7943 | 89.3453
8 | Dandeli | 22 | 22 | 129:20 | 651:35 | 364:49 | 837:17 | 1202:06 | 3587:38 | 1331:26 | 60:31 | 92.6558 | 91.8656 | 4239:13 | 192:42 | 94.4305 | 93.419
9 | Karwar | 30 | 30 | 244:50 | 1749:09 | 586:47 | 1200:18 | 1787:05 | 6875:57 | 2031:55 | 67:44 | 91.9934 | 90.8964 | 8625:06 | 287:30 | 92.1722 | 90.1809
10 | Honnavar | 40 | 40 | 469:23 | 2272:18 | 528:23 | 873:42 | 1402:05 | 6723:22 | 1871:28 | 46:47 | 95.2887 | 93.7115 | 8995:40 | 224:54 | 94.2594 | 92.3193
11 | Belagavi | 142 | 142 | 780:43 | 1952:29 | 4002:23 | 3047:18 | 7049:41 | 1111.5181 | 7830:24 | 55:09 | 93.3272 | 92.5882 | 1192.8715 | 201:37 | 93.5839 | 93.1143
12 | Bailhongal | 192 | 192 | 1281:34 | 7008:11 | 3902:24 | 6136:38 | 10039:02 | 1645.5667 | 11320:36 | 58:58 | 92.9722 | 92.0751 | 1937.5743 | 242:12 | 92.9749 | 91.7283
13 | Ramdurg | 76 | 76 | 292:22 | 1630:06 | 1775:39 | 3155:42 | 4931:21 | 18358:40 | 5223:43 | 68:44 | 91.2787 | 90.7617 | 19988:46 | 263:01 | 91.75 | 91.0174
14 | Ghataprabha | 162 | 162 | 249:00 | 905:56 | 1607:50 | 3234:54 | 4842:44 | 17303:29 | 5091:44 | 31:26 | 95.9821 | 95.7755 | 18209:25 | 112:24 | 96.3521 | 96.1611
15 | Raibag | 176 | 176 | 702:00 | 1943:50 | 5220:46 | 2407:49 | 7628:35 | 1174.6861 | 8330:35 | 47:20 | 94.1742 | 93.6381 | 1255.6792 | 171:14 | 94.5292 | 94.152
16 | Athani | 194 | 194 | 732:04 | 2868:45 | 3485:49 | 2082:07 | 5567:56 | 21469:50 | 6300:00 | 32:28 | 96.1424 | 95.6352 | 1014.1076 | 125:27 | 96.2203 | 95.7153
17 | Chikkodi | 190 | 190 | 335:15 | 1871:58 | 2092:33 | 3039:43 | 5132:16 | 18659:15 | 5467:31 | 28:47 | 96.3694 | 96.1322 | 20531:13 | 108:04 | 96.646 | 96.3095
18 | Vijayapur | 166 | 166 | 380:45 | 1214:08 | 3032:25 | 5489:01 | 8521:26 | 1153.2285 | 8902:11 | 53:38 | 93.1003 | 92.792 | 1203.8174 | 174:03 | 94.3056 | 94.0558
19 | Indi | 254 | 254 | 1330:55 | 5342:19 | 5025:15 | 8312:16 | 13337:31 | 1902.8118 | 14668:26 | 57:45 | 92.9422 | 92.2379 | 2125.4083 | 200:50 | 93.8595 | 93.1412
20 | B.Bagewadi | 142 | 142 | 681:10 | 3153:32 | 3424:31 | 4588:20 | 8012:51 | 1086.316 | 8694:01 | 61:14 | 92.4155 | 91.7708 | 1217.7132 | 205:49 | 93.7294 | 92.9709
21 | Bagalkot | 185 | 185 | 800:22 | 3602:07 | 3805:08 | 6917:28 | 10722:36 | 1806.9715 | 11522:58 | 62:17 | 92.2097 | 91.6282 | 1957.0597 | 253:53 | 91.9939 | 91.3289
22 | Jamkhandi | 208 | 208 | 668:40 | 1981:27 | 2531:25 | 1916:40 | 4448:05 | 16029:26 | 5116:45 | 24:36 | 97.1257 | 96.6936 | 18010:53 | 86:35 | 97.368 | 97.0427
23 | Mudhol | 192 | 192 | 435:57 | 1567:10 | 2419:01 | 3015:20 | 5434:21 | 20187:51 | 5870:18 | 30:34 | 96.1957 | 95.8905 | 21755:01 | 113:18 | 96.409 | 96.1302
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of August-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of August-2021 |  |  |  | Reliability for cumulative period from Apr-21 to August-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 71:35 | 1190:25 | 966:38 | 1847:37 | 2814:15 | 15155:44 | 2885:50 | 64:08 | 91.5942 | 91.3804 | 16346:09 | 363:15 | 90.828 | 90.1076
2 | Dharwad Rural | 81 | 81 | 56:46 | 912:15 | 1208:22 | 1759:04 | 2967:26 | 1123.7417 | 3024:12 | 37:20 | 95.0759 | 94.9817 | 1161.7521 | 344:13 | 90.9324 | 90.6257
3 | Gadag | 98 | 98 | 46:20 | 455:51 | 1224:53 | 2243:19 | 3468:12 | 1016.5708 | 3514:32 | 35:52 | 95.2433 | 95.1798 | 1035.5646 | 253:36 | 93.2201 | 93.0935
4 | Ron | 54 | 54 | 61:25 | 1134:49 | 444:45 | 501:20 | 946:05 | 9758:02 | 1007:30 | 18:39 | 97.6452 | 97.4923 | 10892:51 | 201:43 | 95.0789 | 94.5066
5 | Haveri | 197 | 197 | 800:48 | 7748:23 | 2080:08 | 8576:39 | 10656:47 | 3447.0951 | 11457:35 | 58:10 | 92.7291 | 92.1828 | 3769.9444 | 459:17 | 88.5634 | 87.4923
6 | Ranebennur | 182 | 182 | 507:24 | 4469:03 | 2926:17 | 5217:06 | 8143:23 | 2763.9417 | 8650:47 | 47:32 | 93.986 | 93.6113 | 2950.1521 | 389:02 | 90.0742 | 89.4055
7 | Sirsi | 54 | 54 | 271:19 | 2562:23 | 533:51 | 1378:00 | 1911:51 | 16467:08 | 2183:10 | 40:26 | 95.2413 | 94.566 | 19029:31 | 352:24 | 91.6953 | 90.4031
8 | Dandeli | 22 | 22 | 69:56 | 721:31 | 215:09 | 463:36 | 678:45 | 4266:23 | 748:41 | 34:02 | 95.8532 | 95.4259 | 4987:54 | 226:43 | 94.7188 | 93.8256
9 | Karwar | 30 | 30 | 265:47 | 2014:56 | 326:02 | 480:36 | 806:38 | 7682:35 | 1072:25 | 35:45 | 96.3861 | 95.1953 | 9697:31 | 323:15 | 93.026 | 91.1969
10 | Honnavar | 40 | 40 | 285:02 | 2557:20 | 569:25 | 526:02 | 1095:27 | 7818:49 | 1380:29 | 34:31 | 96.3191 | 95.3613 | 10376:09 | 259:24 | 94.6767 | 92.9356
11 | Belagavi | 142 | 142 | 391:31 | 2344:00 | 2638:35 | 1673:22 | 4311:57 | 1291.1826 | 4703:28 | 33:07 | 95.9186 | 95.548 | 1388.8493 | 234:44 | 94.057 | 93.6074
12 | Bailhongal | 192 | 192 | 965:33 | 7973:44 | 3175:14 | 3026:37 | 6201:51 | 1903.9771 | 7167:24 | 37:20 | 95.6584 | 94.9825 | 2236.216 | 279:32 | 93.5186 | 92.3876
13 | Ramdurg | 78 | 78 | 386:55 | 2017:01 | 1506:52 | 2282:11 | 3789:03 | 22147:43 | 4175:58 | 53:32 | 93.4708 | 92.804 | 1006.8639 | 309:48 | 92.2673 | 91.5631
14 | Ghataprabha | 162 | 162 | 182:12 | 1088:08 | 1519:29 | 1250:35 | 2770:04 | 20073:33 | 2952:16 | 18:13 | 97.7017 | 97.5506 | 21161:41 | 130:38 | 96.6255 | 96.4426
15 | Raibag | 176 | 176 | 374:49 | 2318:39 | 5352:00 | 1179:54 | 6531:54 | 1446.8486 | 6906:43 | 39:15 | 95.0117 | 94.7254 | 1543.459 | 210:28 | 94.627 | 94.2682
16 | Athani | 197 | 197 | 728:11 | 3596:56 | 4244:31 | 1419:21 | 5663:52 | 1130.5708 | 6392:03 | 32:27 | 96.1357 | 95.6389 | 1280.4431 | 156:00 | 96.2491 | 95.7518
17 | Chikkodi | 190 | 190 | 142:40 | 2014:38 | 1750:05 | 892:44 | 2642:49 | 21302:04 | 2785:29 | 14:40 | 98.1304 | 98.0295 | 23316:42 | 122:43 | 96.9467 | 96.658
18 | Vijayapur | 173 | 173 | 416:33 | 1630:41 | 1904:16 | 5390:02 | 7294:18 | 1457.1576 | 7710:51 | 44:34 | 94.3329 | 94.0092 | 1525.1028 | 211:34 | 94.4949 | 94.2382
19 | Indi | 254 | 254 | 524:50 | 5867:09 | 3612:25 | 7258:48 | 10871:13 | 2355.7792 | 11396:03 | 44:52 | 94.2473 | 93.9696 | 2600.2437 | 245:42 | 93.9381 | 93.309
20 | B.Bagewadi | 142 | 142 | 284:18 | 3437:50 | 1870:58 | 2983:21 | 4854:19 | 1288.5792 | 5138:37 | 36:11 | 95.4052 | 95.1361 | 1431.8222 | 242:00 | 94.069 | 93.4096
21 | Bagalkot | 187 | 187 | 462:46 | 4064:53 | 2882:47 | 4885:10 | 7767:57 | 2130.6361 | 8230:43 | 44:01 | 94.4167 | 94.0841 | 2300.0062 | 295:11 | 92.5531 | 91.9611
22 | Jamkhandi | 210 | 210 | 792:19 | 2773:46 | 2158:06 | 1436:09 | 3594:15 | 19623:41 | 4386:34 | 20:53 | 97.6995 | 97.1924 | 22397:27 | 106:39 | 97.4552 | 97.0955
23 | Mudhol | 192 | 192 | 176:02 | 1743:12 | 2566:55 | 2264:56 | 4831:51 | 1042.4875 | 5007:53 | 26:05 | 96.6175 | 96.4943 | 1115.1208 | 139:23 | 96.4512 | 96.204
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]