## DHQ
Annex-1 | [13 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of April-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2021 |  |  |  | Reliability for cumulative period from Apr-21 to Apr-21
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 2:37 | 2:37 | 518:43 | 328:30 | 847:13 | 847:13 | 849:50 | 26:33 | 96.3228 | 96.3115 | 849:50 | 26:33 | 96.3228 | 96.3115
2 | Gadag | 16 | 16 | 27:11 | 27:11 | 94:39 | 71:11 | 165:50 | 165:50 | 193:01 | 12:04 | 98.5605 | 98.3245 | 193:01 | 12:04 | 98.5605 | 98.3245
3 | Haveri | 7 | 7 | 31:00 | 31:00 | 23:35 | 30:25 | 54:00 | 54:00 | 85:00 | 12:09 | 98.9286 | 98.3135 | 85:00 | 12:09 | 98.9286 | 98.3135
4 | Karwar | 10 | 10 | 96:28 | 96:28 | 70:30 | 61:58 | 132:28 | 132:28 | 228:56 | 22:54 | 98.1602 | 96.8204 | 228:56 | 22:54 | 98.1602 | 96.8204
5 | Belagavi | 75 | 75 | 66:42 | 66:42 | 456:46 | 144:09 | 600:55 | 600:55 | 667:37 | 8:54 | 98.8872 | 98.7637 | 667:37 | 8:54 | 98.8872 | 98.7637
6 | Vijayapur | 37 | 37 | 59:01 | 59:01 | 202:03 | 255:31 | 457:34 | 457:34 | 516:35 | 13:58 | 98.2824 | 98.0609 | 516:35 | 13:58 | 98.2824 | 98.0609
7 | Bagalkot | 11 | 11 | 51:28 | 51:28 | 61:03 | 63:37 | 124:40 | 124:40 | 176:08 | 16:01 | 98.4259 | 97.7761 | 176:08 | 16:01 | 98.4259 | 97.7761
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of May-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2021 |  |  |  | Reliability for cumulative period from Apr-21 to May-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 0:00 | 2:37 | 529:31 | 291:43 | 821:14 | 1668:27 | 821:14 | 25:40 | 96.5506 | 96.5506 | 1671:04 | 52:13 | 96.4386 | 96.433
2 | Gadag | 16 | 16 | 0:00 | 27:11 | 81:31 | 93:30 | 175:01 | 340:51 | 175:01 | 10:56 | 98.5298 | 98.5298 | 368:02 | 23:00 | 98.5449 | 98.4288
3 | Haveri | 7 | 7 | 0:00 | 31:00 | 67:30 | 83:05 | 150:35 | 204:35 | 150:35 | 21:31 | 97.1086 | 97.1086 | 235:35 | 33:39 | 98.0037 | 97.7012
4 | Karwar | 10 | 10 | 192:00 | 288:28 | 186:50 | 170:03 | 356:53 | 489:21 | 548:53 | 54:53 | 95.2032 | 92.6225 | 777:49 | 77:47 | 96.6574 | 94.687
5 | Belagavi | 75 | 75 | 142:26 | 209:08 | 389:36 | 153:04 | 542:40 | 1143:35 | 685:06 | 9:08 | 99.0275 | 98.7722 | 1352:43 | 18:02 | 98.9585 | 98.768
6 | Vijayapur | 37 | 37 | 19:36 | 78:37 | 178:41 | 319:55 | 498:36 | 956:10 | 518:12 | 14:00 | 98.1888 | 98.1176 | 1034:47 | 27:58 | 98.2348 | 98.0897
7 | Bagalkot | 11 | 11 | 0:40 | 52:08 | 54:22 | 58:02 | 112:24 | 237:04 | 113:04 | 10:17 | 98.6266 | 98.6184 | 289:12 | 26:17 | 98.5279 | 98.2042
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of June-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2021 |  |  |  | Reliability for cumulative period from Apr-21 to June-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 14:30 | 17:07 | 542:48 | 301:13 | 844:01 | 2512:28 | 858:31 | 26:50 | 96.3367 | 96.2738 | 2529:35 | 79:03 | 96.405 | 96.3805
2 | Gadag | 16 | 16 | 7:00 | 34:11 | 80:26 | 96:55 | 177:21 | 518:12 | 184:21 | 11:31 | 98.4605 | 98.3997 | 552:23 | 34:31 | 98.5171 | 98.4192
3 | Haveri | 7 | 7 | 0:00 | 31:00 | 78:40 | 67:25 | 146:05 | 350:40 | 146:05 | 20:52 | 97.1015 | 97.1015 | 381:40 | 54:31 | 97.7063 | 97.5035
4 | Karwar | 10 | 10 | 73:44 | 362:12 | 145:33 | 155:14 | 300:47 | 790:08 | 374:31 | 37:27 | 95.8225 | 94.7984 | 1152:20 | 115:14 | 96.3822 | 94.7237
5 | Belagavi | 76 | 76 | 112:56 | 322:04 | 669:26 | 116:43 | 786:09 | 1929:44 | 899:05 | 11:50 | 98.5633 | 98.3569 | 2251:48 | 29:38 | 98.8374 | 98.6434
6 | Vijayapur | 37 | 37 | 12:09 | 90:46 | 213:49 | 192:50 | 406:39 | 1362:49 | 418:48 | 11:19 | 98.4735 | 98.4279 | 1453:35 | 39:17 | 98.3135 | 98.2012
7 | Bagalkot | 11 | 11 | 4:00 | 56:08 | 105:03 | 69:45 | 174:48 | 411:52 | 178:48 | 16:15 | 97.7929 | 97.7424 | 468:00 | 42:33 | 98.2856 | 98.0519
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of July-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2021 |  |  |  | Reliability for cumulative period from Apr-21 to July-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 10:25 | 27:32 | 582:33 | 366:57 | 949:30 | 3461:58 | 959:55 | 30:00 | 96.0118 | 95.9681 | 3489:30 | 109:03 | 96.3051 | 96.2757
2 | Gadag | 16 | 16 | 25:33 | 59:44 | 89:18 | 45:24 | 134:42 | 652:54 | 160:15 | 10:01 | 98.8684 | 98.6538 | 712:38 | 44:32 | 98.6063 | 98.4788
3 | Haveri | 7 | 7 | 0:00 | 31:00 | 41:45 | 22:20 | 64:05 | 414:45 | 64:05 | 9:09 | 98.7695 | 98.7695 | 445:45 | 63:41 | 97.9764 | 97.8252
4 | Karwar | 10 | 10 | 85:08 | 447:20 | 42:49 | 66:06 | 108:55 | 899:03 | 194:03 | 19:24 | 98.5361 | 97.3918 | 1346:23 | 134:38 | 96.9295 | 95.4017
5 | Belagavi | 76 | 76 | 215:04 | 537:08 | 307:53 | 143:10 | 451:03 | 2380:47 | 666:07 | 8:46 | 99.2023 | 98.8219 | 2917:55 | 38:24 | 98.9301 | 98.6887
6 | Vijayapur | 37 | 37 | 24:40 | 115:26 | 304:30 | 156:30 | 461:00 | 1823:49 | 485:40 | 13:08 | 98.3253 | 98.2357 | 1939:15 | 52:25 | 98.3165 | 98.21
7 | Bagalkot | 11 | 11 | 20:30 | 76:38 | 83:37 | 46:02 | 129:39 | 541:31 | 150:09 | 13:39 | 98.4158 | 98.1653 | 618:09 | 56:12 | 98.3187 | 98.0808
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of August-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of August-2021 |  |  |  | Reliability for cumulative period from Apr-21 to August-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 9:15 | 36:47 | 441:57 | 130:42 | 572:39 | 4034:37 | 581:54 | 18:11 | 97.5947 | 97.5559 | 4071:24 | 127:14 | 96.5664 | 96.5351
2 | Gadag | 16 | 16 | 0:00 | 59:44 | 74:42 | 29:29 | 104:11 | 757:05 | 104:11 | 6:31 | 99.1248 | 99.1248 | 816:49 | 51:03 | 98.7114 | 98.6097
3 | Haveri | 7 | 7 | 45:10 | 76:10 | 27:00 | 15:50 | 42:50 | 457:35 | 88:00 | 12:34 | 99.1775 | 98.3103 | 533:45 | 76:15 | 98.2198 | 97.9235
4 | Karwar | 10 | 10 | 26:42 | 474:02 | 72:09 | 61:52 | 134:01 | 1033:04 | 160:43 | 16:04 | 98.1987 | 97.8398 | 1507:06 | 150:43 | 97.1866 | 95.8957
5 | Belagavi | 78 | 78 | 10:42 | 547:50 | 255:21 | 122:38 | 377:59 | 2758:46 | 388:41 | 4:59 | 99.3487 | 99.3302 | 3306:36 | 42:24 | 99.0368 | 98.8455
6 | Vijayapur | 37 | 37 | 0:25 | 115:51 | 249:14 | 200:28 | 449:42 | 2273:31 | 450:07 | 12:10 | 98.3664 | 98.3649 | 2389:22 | 64:35 | 98.3266 | 98.2414
7 | Bagalkot | 11 | 11 | 0:00 | 76:38 | 67:05 | 35:49 | 102:54 | 644:25 | 102:54 | 9:21 | 98.7427 | 98.7427 | 721:03 | 65:33 | 98.4046 | 98.2149
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of September-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of September-2021 |  |  |  | Reliability for cumulative period from Apr-21 to September-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 5:45 | 42:32 | 485:26 | 100:37 | 586:03 | 4620:40 | 591:48 | 18:30 | 97.4564 | 97.4314 | 4663:12 | 145:44 | 96.7123 | 96.682
2 | Gadag | 16 | 16 | 0:00 | 59:44 | 86:00 | 20:54 | 106:54 | 863:59 | 106:54 | 6:41 | 99.072 | 99.072 | 923:43 | 57:44 | 98.7705 | 98.6855
3 | Haveri | 7 | 7 | 3:20 | 79:30 | 133:25 | 18:30 | 151:55 | 609:30 | 155:15 | 22:11 | 96.9858 | 96.9196 | 689:00 | 98:26 | 98.0175 | 97.7589
4 | Karwar | 10 | 10 | 11:00 | 485:02 | 65:16 | 72:46 | 138:02 | 1171:06 | 149:02 | 14:54 | 98.0829 | 97.9301 | 1656:08 | 165:37 | 97.3336 | 96.2292
5 | Belagavi | 79 | 79 | 94:57 | 642:47 | 417:03 | 119:56 | 536:59 | 3295:45 | 631:56 | 8:00 | 99.0559 | 98.889 | 3938:32 | 49:51 | 99.0501 | 98.8649
6 | Vijayapur | 37 | 37 | 43:33 | 159:24 | 448:08 | 452:16 | 900:24 | 3173:55 | 943:57 | 25:31 | 96.6201 | 96.4566 | 3333:19 | 90:05 | 98.0469 | 97.9488
7 | Bagalkot | 12 | 12 | 96:08 | 172:46 | 63:25 | 36:03 | 99:28 | 743:53 | 195:36 | 16:18 | 98.8488 | 97.7361 | 916:39 | 76:23 | 98.5886 | 98.2608
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of October-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of October-2021 |  |  |  | Reliability for cumulative period from Apr-21 to October-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 8:55 | 51:27 | 246:31 | 133:31 | 380:02 | 5000:42 | 388:57 | 12:09 | 98.4038 | 98.3663 | 5052:09 | 157:53 | 96.9573 | 96.926
2 | Gadag | 16 | 16 | 0:00 | 59:44 | 49:39 | 45:56 | 95:35 | 959:34 | 95:35 | 5:58 | 99.197 | 99.197 | 1019:18 | 63:42 | 98.8323 | 98.7596
3 | Haveri | 7 | 7 | 57:30 | 137:00 | 37:10 | 41:30 | 78:40 | 688:10 | 136:10 | 19:27 | 98.4895 | 97.3854 | 825:10 | 117:53 | 98.0859 | 97.7048
4 | Karwar | 10 | 10 | 2:30 | 487:32 | 60:40 | 91:50 | 152:30 | 1323:36 | 155:00 | 15:30 | 97.9503 | 97.9167 | 1811:08 | 181:07 | 97.4229 | 96.4737
5 | Belagavi | 80 | 80 | 135:34 | 778:21 | 422:34 | 135:19 | 557:53 | 3853:38 | 693:27 | 8:40 | 99.0627 | 98.8349 | 4631:59 | 57:54 | 99.0621 | 98.8727
6 | Vijayapur | 37 | 37 | 20:13 | 179:37 | 144:36 | 318:05 | 462:41 | 3636:36 | 482:54 | 13:03 | 98.3192 | 98.2458 | 3816:13 | 103:08 | 98.0863 | 97.9918
7 | Bagalkot | 12 | 12 | 6:30 | 179:16 | 28:11 | 17:06 | 45:17 | 789:10 | 51:47 | 4:19 | 99.4928 | 99.42 | 968:26 | 80:42 | 98.7196 | 98.4287
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of November-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of November-2021 |  |  |  | Reliability for cumulative period from Apr-21 to November-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 17:05 | 68:32 | 296:30 | 161:12 | 457:42 | 5458:24 | 474:47 | 14:50 | 98.0135 | 97.9393 | 5526:56 | 172:43 | 97.0872 | 97.0506
2 | Gadag | 16 | 16 | 0:00 | 59:44 | 93:19 | 31:30 | 124:49 | 1084:23 | 124:49 | 7:48 | 98.9165 | 98.9165 | 1144:07 | 71:30 | 98.8427 | 98.7789
3 | Haveri | 7 | 7 | 0:00 | 137:00 | 31:50 | 19:25 | 51:15 | 739:25 | 51:15 | 7:19 | 98.9831 | 98.9831 | 876:25 | 125:12 | 98.1962 | 97.862
4 | Karwar | 10 | 10 | 7:28 | 495:00 | 64:29 | 79:25 | 143:54 | 1467:30 | 151:22 | 15:08 | 98.0014 | 97.8977 | 1962:30 | 196:15 | 97.494 | 96.6487
5 | Belagavi | 80 | 80 | 155:07 | 933:28 | 273:14 | 73:49 | 347:03 | 4200:41 | 502:10 | 6:17 | 99.3975 | 99.1282 | 5134:09 | 64:11 | 99.1033 | 98.9041
6 | Vijayapur | 37 | 37 | 18:29 | 198:06 | 146:13 | 155:56 | 302:09 | 3938:45 | 320:38 | 8:40 | 98.8658 | 98.7964 | 4136:51 | 111:48 | 98.1822 | 98.0907
7 | Bagalkot | 12 | 12 | 34:10 | 213:26 | 69:58 | 34:50 | 104:48 | 893:58 | 138:58 | 11:35 | 98.787 | 98.3916 | 1107:24 | 92:17 | 98.7278 | 98.4241
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of December-2021
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of December-2021 |  |  |  | Reliability for cumulative period from Apr-21 to December-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 0:00 | 68:32 | 241:24 | 53:11 | 294:35 | 5752:59 | 294:35 | 9:12 | 98.7627 | 98.7627 | 5821:31 | 181:55 | 97.276 | 97.2436
2 | Gadag | 16 | 16 | 25:25 | 85:09 | 76:16 | 17:12 | 93:28 | 1177:51 | 118:53 | 7:26 | 99.2148 | 99.0013 | 1263:00 | 78:56 | 98.8846 | 98.804
3 | Haveri | 7 | 7 | 0:00 | 137:00 | 32:25 | 15:35 | 48:00 | 787:25 | 48:00 | 6:51 | 99.0783 | 99.0783 | 924:25 | 132:04 | 98.2956 | 97.9991
4 | Karwar | 10 | 10 | 4:20 | 499:20 | 65:30 | 55:33 | 121:03 | 1588:33 | 125:23 | 12:32 | 98.373 | 98.3147 | 2087:53 | 208:47 | 97.5931 | 96.8365
5 | Belagavi | 80 | 80 | 68:09 | 1001:37 | 86:42 | 71:45 | 158:27 | 4359:08 | 226:36 | 2:50 | 99.7338 | 99.6193 | 5360:45 | 67:01 | 99.1744 | 98.9847
6 | Vijayapur | 37 | 37 | 17:40 | 215:46 | 92:18 | 139:48 | 232:06 | 4170:51 | 249:46 | 6:45 | 99.1569 | 99.0927 | 4386:37 | 118:33 | 98.292 | 98.2037
7 | Bagalkot | 12 | 12 | 2:10 | 215:36 | 36:35 | 21:08 | 57:43 | 951:41 | 59:53 | 4:59 | 99.3535 | 99.3293 | 1167:17 | 97:16 | 98.7984 | 98.5262
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of JANUARY-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of January-2022 |  |  |  | Reliability for cumulative period from Apr-21 to Jan-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 15:25 | 83:57 | 522:09 | 82:25 | 604:34 | 6357:33 | 619:59 | 19:22 | 97.4607 | 97.3959 | 6441:30 | 201:18 | 96.9898 | 96.95
2 | Gadag | 16 | 16 | 0:00 | 85:09 | 78:14 | 23:20 | 101:34 | 1279:25 | 101:34 | 6:21 | 99.1468 | 99.1468 | 1364:34 | 85:17 | 98.7884 | 98.7078
3 | Haveri | 7 | 7 | 0:00 | 137:00 | 173:40 | 10:30 | 184:10 | 971:35 | 184:10 | 26:19 | 96.4638 | 96.4638 | 1108:35 | 158:22 | 97.897 | 97.6005
4 | Karwar | 10 | 10 | 5:54 | 505:14 | 35:48 | 32:28 | 68:16 | 1656:49 | 74:10 | 7:25 | 99.0824 | 99.0031 | 2162:03 | 216:12 | 97.4897 | 96.7242
5 | Belagavi | 80 | 80 | 234:49 | 1236:26 | 231:45 | 85:30 | 317:15 | 4676:23 | 552:04 | 6:54 | 99.467 | 99.0725 | 5912:49 | 73:55 | 99.1143 | 98.8801
6 | Vijayapur | 37 | 37 | 1:45 | 217:31 | 101:56 | 277:12 | 379:08 | 4549:59 | 380:53 | 10:18 | 98.6227 | 98.6164 | 4767:30 | 128:51 | 98.1368 | 98.0477
7 | Bagalkot | 12 | 12 | 1:20 | 216:56 | 60:39 | 9:14 | 69:53 | 1021:34 | 71:13 | 5:56 | 99.2173 | 99.2023 | 1238:30 | 103:12 | 98.7101 | 98.4362
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of FEBRUARY-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of February-2022 |  |  |  | Reliability for cumulative period from Apr-21 to February-2022
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 3:00 | 86:57 | 484:23 | 44:21 | 528:44 | 6886:17 | 531:44 | 16:37 | 97.5412 | 97.5273 | 6973:14 | 217:55 | 97.3154 | 97.2815
2 | Gadag | 16 | 16 | 0:00 | 85:09 | 28:25 | 7:23 | 35:48 | 1315:13 | 35:48 | 2:14 | 99.667 | 99.667 | 1400:22 | 87:31 | 98.9745 | 98.9081
3 | Haveri | 7 | 7 | 0:00 | 137:00 | 29:05 | 12:45 | 41:50 | 1013:25 | 41:50 | 5:59 | 99.1107 | 99.1107 | 1150:25 | 164:21 | 98.1939 | 97.9498
4 | Karwar | 10 | 10 | 12:12 | 517:26 | 34:25 | 32:40 | 67:05 | 1723:54 | 79:17 | 7:56 | 99.0017 | 98.8202 | 2241:20 | 224:08 | 97.8494 | 97.2039
5 | Belagavi | 80 | 80 | 107:35 | 1344:01 | 207:01 | 143:12 | 350:13 | 5026:36 | 457:48 | 5:43 | 99.3486 | 99.1484 | 6370:37 | 79:38 | 99.2162 | 99.0066
6 | Vijayapur | 37 | 37 | 33:58 | 251:29 | 90:24 | 52:06 | 142:30 | 4692:29 | 176:28 | 4:46 | 99.4269 | 99.2903 | 4943:58 | 133:37 | 98.4179 | 98.3331
7 | Bagalkot | 12 | 12 | 1:00 | 217:56 | 51:57 | 10:16 | 62:13 | 1083:47 | 63:13 | 5:16 | 99.2285 | 99.2161 | 1301:43 | 108:29 | 98.8733 | 98.6468
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of MARCH-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of March-2022 |  |  |  | Reliability for cumulative period from Apr-21 to March-2022
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 32 | 32 | 12:00 | 98:57 | 595:29 | 171:51 | 767:20 | 7653:37 | 779:20 | 24:21 | 96.777 | 96.7266 | 7752:34 | 242:16 | 97.2697 | 97.2344
2 | Gadag | 15 | 15 | 0:00 | 85:09 | 130:37 | 14:28 | 145:05 | 1460:18 | 145:05 | 9:40 | 98.7 | 98.7 | 1545:27 | 103:02 | 98.8887 | 98.8239
3 | Haveri | 8 | 8 | 0:00 | 137:00 | 44:30 | 18:25 | 62:55 | 1076:20 | 62:55 | 7:52 | 98.9429 | 98.9429 | 1213:20 | 151:40 | 98.4641 | 98.2686
4 | Karwar | 10 | 10 | 95:06 | 612:32 | 60:33 | 54:18 | 114:51 | 1838:45 | 209:57 | 21:00 | 98.4563 | 97.1781 | 2451:17 | 245:08 | 97.901 | 97.2017
5 | Belagavi | 80 | 80 | 254:11 | 1598:12 | 388:21 | 204:08 | 592:29 | 5619:05 | 846:40 | 10:35 | 99.0046 | 98.5775 | 7217:17 | 90:13 | 99.1982 | 98.9701
6 | Vijayapur | 37 | 37 | 19:55 | 271:24 | 108:51 | 79:29 | 188:20 | 4880:49 | 208:15 | 5:38 | 99.3158 | 99.2435 | 5152:13 | 139:15 | 98.4941 | 98.4104
7 | Bagalkot | 12 | 12 | 117:40 | 335:36 | 50:38 | 21:29 | 72:07 | 1155:54 | 189:47 | 15:49 | 99.1922 | 97.8743 | 1491:30 | 124:17 | 98.9004 | 98.5811
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]

## URBAN
Annex-II | [13 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of April-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2021 |  |  |  | Reliability for cumulative period from Apr-21 to Apr-21
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 77 | 77 | 9:10 | 9:10 | 313:25 | 525:48 | 839:13 | 839:13 | 848:23 | 11:01 | 98.4863 | 98.4697 | 848:23 | 11:01 | 98.4863 | 98.4697
2 | Dharwad(R) | 19 | 19 | 9:45 | 9:45 | 259:38 | 242:11 | 501:49 | 501:49 | 511:34 | 26:55 | 96.3317 | 96.2605 | 511:34 | 26:55 | 96.3317 | 96.2605
3 | Kundagol | 1 | 1 | 46:10 | 46:10 | 6:15 | 12:45 | 19:00 | 19:00 | 65:10 | 65:10 | 97.3611 | 90.9491 | 65:10 | 65:10 | 97.3611 | 90.9491
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 5:16 | 7:36 | 12:52 | 12:52 | 12:52 | 12:52 | 98.213 | 98.213 | 12:52 | 12:52 | 98.213 | 98.213
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 13:18 | 4:27 | 17:45 | 17:45 | 17:45 | 17:45 | 97.5347 | 97.5347 | 17:45 | 17:45 | 97.5347 | 97.5347
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 73:35 | 53:10 | 126:45 | 126:45 | 126:45 | 63:22 | 91.1979 | 91.1979 | 126:45 | 63:22 | 91.1979 | 91.1979
7 | Alnavar | 1 | 1 | 6:10 | 6:10 | 10:55 | 6:05 | 17:00 | 17:00 | 23:10 | 23:10 | 97.6389 | 96.7824 | 23:10 | 23:10 | 97.6389 | 96.7824
8 | Naragund | 2 | 2 | 9:20 | 9:20 | 32:50 | 25:45 | 58:35 | 58:35 | 67:55 | 33:58 | 95.9317 | 95.2836 | 67:55 | 33:58 | 95.9317 | 95.2836
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 22:00 | 31:35 | 53:35 | 53:35 | 53:35 | 13:24 | 98.1395 | 98.1395 | 53:35 | 13:24 | 98.1395 | 98.1395
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 44:47 | 49:57 | 94:44 | 94:44 | 94:44 | 23:41 | 96.7106 | 96.7106 | 94:44 | 23:41 | 96.7106 | 96.7106
11 | Naregal | 1 | 1 | 0:00 | 0:00 | 9:05 | 10:15 | 19:20 | 19:20 | 19:20 | 19:20 | 97.3148 | 97.3148 | 19:20 | 19:20 | 97.3148 | 97.3148
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 34:10 | 21:20 | 55:30 | 55:30 | 55:30 | 27:45 | 96.1458 | 96.1458 | 55:30 | 27:45 | 96.1458 | 96.1458
13 | Ron | 3 | 3 | 0:00 | 0:00 | 34:55 | 31:35 | 66:30 | 66:30 | 66:30 | 22:10 | 96.9213 | 96.9213 | 66:30 | 22:10 | 96.9213 | 96.9213
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 11:15 | 15:55 | 27:10 | 27:10 | 27:10 | 9:03 | 98.7423 | 98.7423 | 27:10 | 9:03 | 98.7423 | 98.7423
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 19:35 | 27:28 | 47:03 | 47:03 | 47:03 | 47:03 | 93.4653 | 93.4653 | 47:03 | 47:03 | 93.4653 | 93.4653
16 | G.C.T.M | 1 | 1 | 9:10 | 9:10 | 7:40 | 4:00 | 11:40 | 11:40 | 20:50 | 20:50 | 98.3796 | 97.1065 | 20:50 | 20:50 | 98.3796 | 97.1065
17 | F.C.S.M | 2 | 2 | 9:00 | 9:00 | 5:35 | 4:50 | 10:25 | 10:25 | 19:25 | 9:42 | 99.2766 | 98.6516 | 19:25 | 9:42 | 99.2766 | 98.6516
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 9:46 | 2:25 | 12:11 | 12:11 | 12:11 | 12:11 | 98.3079 | 98.3079 | 12:11 | 12:11 | 98.3079 | 98.3079
19 | Hole-Alur | 1 | 1 | 20:40 | 20:40 | 20:15 | 5:15 | 25:30 | 25:30 | 46:10 | 46:10 | 96.4583 | 93.588 | 46:10 | 46:10 | 96.4583 | 93.588
20 | Savanur | 2 | 2 | 2:30 | 2:30 | 16:45 | 15:55 | 32:40 | 32:40 | 35:10 | 17:35 | 97.7315 | 97.5579 | 35:10 | 17:35 | 97.7315 | 97.5579
21 | Shiggaon | 2 | 2 | 13:35 | 13:35 | 75:50 | 26:20 | 102:10 | 102:10 | 115:45 | 57:52 | 92.9051 | 91.9618 | 115:45 | 57:52 | 92.9051 | 91.9618
22 | Bankapur | 1 | 1 | 7:15 | 7:15 | 11:10 | 7:25 | 18:35 | 18:35 | 25:50 | 25:50 | 97.419 | 96.412 | 25:50 | 25:50 | 97.419 | 96.412
23 | Hangal | 2 | 2 | 32:40 | 32:40 | 34:30 | 22:00 | 56:30 | 56:30 | 89:10 | 44:35 | 96.0764 | 93.8079 | 89:10 | 44:35 | 96.0764 | 93.8079
24 | Ranebennur | 16 | 16 | 40:55 | 40:55 | 76:16 | 38:57 | 115:13 | 115:13 | 156:08 | 9:45 | 98.9999 | 98.6447 | 156:08 | 9:45 | 98.9999 | 98.6447
25 | Halageri | 2 | 2 | 54:20 | 54:20 | 26:50 | 2:50 | 29:40 | 29:40 | 84:00 | 42:00 | 97.9398 | 94.1667 | 84:00 | 42:00 | 97.9398 | 94.1667
26 | Tuminakatti | 2 | 2 | 2:00 | 2:00 | 33:00 | 5:05 | 38:05 | 38:05 | 40:05 | 20:02 | 97.3553 | 97.2164 | 40:05 | 20:02 | 97.3553 | 97.2164
27 | Kahanderayanahalli | 1 | 1 | 1:00 | 1:00 | 26:40 | 50:10 | 76:50 | 76:50 | 77:50 | 77:50 | 89.3287 | 89.1898 | 77:50 | 77:50 | 89.3287 | 89.1898
28 | Rattihalli | 1 | 1 | 2:40 | 2:40 | 16:10 | 9:15 | 25:25 | 25:25 | 28:05 | 28:05 | 96.4699 | 96.0995 | 28:05 | 28:05 | 96.4699 | 96.0995
29 | Hirekerur | 2 | 2 | 30:20 | 30:20 | 35:50 | 14:50 | 50:40 | 50:40 | 81:00 | 40:30 | 96.4815 | 94.375 | 81:00 | 40:30 | 96.4815 | 94.375
30 | Byadagi | 8 | 8 | 30:10 | 30:10 | 153:45 | 120:00 | 273:45 | 273:45 | 303:55 | 37:59 | 95.2474 | 94.7237 | 303:55 | 37:59 | 95.2474 | 94.7237
31 | Sirsi | 5 | 5 | 4:35 | 4:35 | 28:11 | 35:14 | 63:25 | 63:25 | 68:00 | 13:36 | 98.2384 | 98.1111 | 68:00 | 13:36 | 98.2384 | 98.1111
32 | Yellapur | 3 | 3 | 12:03 | 12:03 | 15:00 | 9:50 | 24:50 | 24:50 | 36:53 | 12:18 | 98.8503 | 98.2924 | 36:53 | 12:18 | 98.8503 | 98.2924
33 | Mundagod | 3 | 3 | 0:00 | 0:00 | 49:30 | 46:00 | 95:30 | 95:30 | 95:30 | 31:50 | 95.5787 | 95.5787 | 95:30 | 31:50 | 95.5787 | 95.5787
34 | Siddapur | 2 | 2 | 4:10 | 4:10 | 4:15 | 20:30 | 24:45 | 24:45 | 28:55 | 14:28 | 98.2812 | 97.9919 | 28:55 | 14:28 | 98.2812 | 97.9919
35 | Dandeli | 8 | 8 | 38:40 | 38:40 | 33:30 | 68:48 | 102:18 | 102:18 | 140:58 | 17:37 | 98.224 | 97.5527 | 140:58 | 17:37 | 98.224 | 97.5527
36 | Haliyal | 3 | 3 | 0:19 | 0:19 | 38:20 | 26:04 | 64:24 | 64:24 | 64:43 | 21:34 | 97.0185 | 97.0039 | 64:43 | 21:34 | 97.0185 | 97.0039
37 | Ankola | 3 | 3 | 16:23 | 16:23 | 14:49 | 5:40 | 20:29 | 20:29 | 36:52 | 12:17 | 99.0517 | 98.2932 | 36:52 | 12:17 | 99.0517 | 98.2932
38 | Kumta | 3 | 3 | 3:30 | 3:30 | 16:03 | 9:21 | 25:24 | 25:24 | 28:54 | 9:38 | 98.8241 | 98.662 | 28:54 | 9:38 | 98.8241 | 98.662
39 | Gokarna | 1 | 1 | 4:57 | 4:57 | 1:25 | 1:25 | 2:50 | 2:50 | 7:47 | 7:47 | 99.6065 | 98.919 | 7:47 | 7:47 | 99.6065 | 98.919
40 | Kasarkod | 1 | 1 | 38:40 | 38:40 | 6:55 | 7:45 | 14:40 | 14:40 | 53:20 | 53:20 | 97.963 | 92.5926 | 53:20 | 53:20 | 97.963 | 92.5926
41 | Honnavar | 3 | 3 | 13:15 | 13:15 | 10:03 | 13:17 | 23:20 | 23:20 | 36:35 | 12:12 | 98.9198 | 98.3063 | 36:35 | 12:12 | 98.9198 | 98.3063
42 | Murdeshwar | 4 | 4 | 20:36 | 20:36 | 46:32 | 38:23 | 84:55 | 84:55 | 105:31 | 26:23 | 97.0515 | 96.3362 | 105:31 | 26:23 | 97.0515 | 96.3362
43 | Bhatkal | 3 | 3 | 10:03 | 10:03 | 16:59 | 11:20 | 28:19 | 28:19 | 38:22 | 12:47 | 98.689 | 98.2238 | 38:22 | 12:47 | 98.689 | 98.2238
44 | Khanapur | 2 | 2 | 6:50 | 6:50 | 7:45 | 21:25 | 29:10 | 29:10 | 36:00 | 18:00 | 97.9745 | 97.5 | 36:00 | 18:00 | 97.9745 | 97.5
45 | Bailhongal | 3 | 3 | 46:25 | 46:25 | 106:15 | 62:40 | 168:55 | 168:55 | 215:20 | 71:47 | 92.1798 | 90.0309 | 215:20 | 71:47 | 92.1798 | 90.0309
46 | Soundatti | 3 | 3 | 1:00 | 1:00 | 58:40 | 30:09 | 88:49 | 88:49 | 89:49 | 29:56 | 95.8881 | 95.8418 | 89:49 | 29:56 | 95.8881 | 95.8418
47 | Ramdurg | 2 | 2 | 6:30 | 6:30 | 19:35 | 5:55 | 25:30 | 25:30 | 32:00 | 16:00 | 98.2292 | 97.7778 | 32:00 | 16:00 | 98.2292 | 97.7778
48 | Gokak | 11 | 11 | 10:27 | 10:27 | 32:18 | 22:35 | 54:53 | 54:53 | 65:20 | 5:56 | 99.307 | 99.1751 | 65:20 | 5:56 | 99.307 | 99.1751
49 | Mudalagi | 2 | 2 | 2:20 | 2:20 | 16:05 | 6:00 | 22:05 | 22:05 | 24:25 | 12:12 | 98.4664 | 98.3044 | 24:25 | 12:12 | 98.4664 | 98.3044
50 | Konnur | 1 | 1 | 0:15 | 0:15 | 42:40 | 8:30 | 51:10 | 51:10 | 51:25 | 51:25 | 92.8935 | 92.8588 | 51:25 | 51:25 | 92.8935 | 92.8588
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 19:35 | 9:00 | 28:35 | 28:35 | 28:35 | 28:35 | 96.0301 | 96.0301 | 28:35 | 28:35 | 96.0301 | 96.0301
52 | Kudachi | 1 | 1 | 0:00 | 0:00 | 61:30 | 8:35 | 70:05 | 70:05 | 70:05 | 70:05 | 90.2662 | 90.2662 | 70:05 | 70:05 | 90.2662 | 90.2662
53 | Athani | 6 | 6 | 42:58 | 42:58 | 59:02 | 94:37 | 153:39 | 153:39 | 196:37 | 32:46 | 96.4433 | 95.4487 | 196:37 | 32:46 | 96.4433 | 95.4487
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 8:15 | 8:35 | 16:50 | 16:50 | 16:50 | 8:25 | 98.831 | 98.831 | 16:50 | 8:25 | 98.831 | 98.831
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 76:50 | 47:20 | 124:10 | 124:10 | 124:10 | 24:50 | 96.5509 | 96.5509 | 124:10 | 24:50 | 96.5509 | 96.5509
56 | Sadalaga | 1 | 1 | 0:00 | 0:00 | 11:00 | 4:00 | 15:00 | 15:00 | 15:00 | 15:00 | 97.9167 | 97.9167 | 15:00 | 15:00 | 97.9167 | 97.9167
57 | Muddebihal | 2 | 2 | 6:00 | 6:00 | 58:55 | 26:00 | 84:55 | 84:55 | 90:55 | 45:28 | 94.103 | 93.6863 | 90:55 | 45:28 | 94.103 | 93.6863
58 | Talikoti | 1 | 1 | 8:00 | 8:00 | 8:30 | 6:25 | 14:55 | 14:55 | 22:55 | 22:55 | 97.9282 | 96.8171 | 22:55 | 22:55 | 97.9282 | 96.8171
59 | B.Bagewadi | 1 | 1 | 3:27 | 3:27 | 2:40 | 3:40 | 6:20 | 6:20 | 9:47 | 9:47 | 99.1204 | 98.6412 | 9:47 | 9:47 | 99.1204 | 98.6412
60 | Indi | 3 | 3 | 5:33 | 5:33 | 14:38 | 14:31 | 29:09 | 29:09 | 34:42 | 11:34 | 98.6505 | 98.3935 | 34:42 | 11:34 | 98.6505 | 98.3935
61 | Sindagi | 2 | 2 | 8:40 | 8:40 | 26:45 | 9:30 | 36:15 | 36:15 | 44:55 | 22:28 | 97.4826 | 96.8808 | 44:55 | 22:28 | 97.4826 | 96.8808
62 | Guledgudda | 1 | 1 | 4:54 | 4:54 | 44:39 | 5:45 | 50:24 | 50:24 | 55:18 | 55:18 | 93 | 92.3194 | 55:18 | 55:18 | 93 | 92.3194
63 | Ilkal | 8 | 8 | 47:35 | 47:35 | 186:12 | 154:59 | 341:11 | 341:11 | 388:46 | 48:36 | 94.0767 | 93.2506 | 388:46 | 48:36 | 94.0767 | 93.2506
64 | Kerur | 2 | 2 | 10:25 | 10:25 | 11:10 | 17:17 | 28:27 | 28:27 | 38:52 | 19:26 | 98.0243 | 97.3009 | 38:52 | 19:26 | 98.0243 | 97.3009
65 | Hungund | 4 | 4 | 24:52 | 24:52 | 32:49 | 50:07 | 82:56 | 82:56 | 107:48 | 26:57 | 97.1204 | 96.2569 | 107:48 | 26:57 | 97.1204 | 96.2569
66 | Gaddankeri | 3 | 3 | 15:18 | 15:18 | 41:50 | 36:57 | 78:47 | 78:47 | 94:05 | 31:22 | 96.3526 | 95.6443 | 94:05 | 31:22 | 96.3526 | 95.6443
67 | Rampur | 1 | 1 | 5:33 | 5:33 | 21:12 | 1:15 | 22:27 | 22:27 | 28:00 | 28:00 | 96.8819 | 96.1111 | 28:00 | 28:00 | 96.8819 | 96.1111
68 | Kaladagi | 2 | 2 | 4:42 | 4:42 | 19:21 | 20:15 | 39:36 | 39:36 | 44:18 | 22:09 | 97.25 | 96.9236 | 44:18 | 22:09 | 97.25 | 96.9236
69 | Achanur | 1 | 1 | 3:03 | 3:03 | 11:33 | 7:21 | 18:54 | 18:54 | 21:57 | 21:57 | 97.375 | 96.9514 | 21:57 | 21:57 | 97.375 | 96.9514
70 | Shirur | 1 | 1 | 8:15 | 8:15 | 2:27 | 5:48 | 8:15 | 8:15 | 16:30 | 16:30 | 98.8542 | 97.7083 | 16:30 | 16:30 | 98.8542 | 97.7083
71 | Badami | 1 | 1 | 6:12 | 6:12 | 11:54 | 11:19 | 23:13 | 23:13 | 29:25 | 29:25 | 96.7755 | 95.9144 | 29:25 | 29:25 | 96.7755 | 95.9144
72 | Kulageri | 1 | 1 | 4:56 | 4:56 | 5:35 | 0:15 | 5:50 | 5:50 | 10:46 | 10:46 | 99.1898 | 98.5046 | 10:46 | 10:46 | 99.1898 | 98.5046
73 | Jamkhandi | 6 | 6 | 7:30 | 7:30 | 90:50 | 15:15 | 106:05 | 106:05 | 113:35 | 18:56 | 97.5444 | 97.3708 | 113:35 | 18:56 | 97.5444 | 97.3708
74 | Mahalingapur | 3 | 3 | 1:00 | 1:00 | 49:52 | 27:09 | 77:01 | 77:01 | 78:01 | 26:00 | 96.4344 | 96.3881 | 78:01 | 26:00 | 96.4344 | 96.3881
75 | Rabakavi | 2 | 2 | 7:45 | 7:45 | 16:50 | 4:00 | 20:50 | 20:50 | 28:35 | 14:17 | 98.5532 | 98.015 | 28:35 | 14:17 | 98.5532 | 98.015
76 | Banahatti | 2 | 2 | 0:30 | 0:30 | 13:50 | 0:35 | 14:25 | 14:25 | 14:55 | 7:28 | 98.9988 | 98.9641 | 14:55 | 7:28 | 98.9988 | 98.9641
77 | Terdal | 2 | 2 | 0:00 | 0:00 | 21:00 | 2:40 | 23:40 | 23:40 | 23:40 | 11:50 | 98.3565 | 98.3565 | 23:40 | 11:50 | 98.3565 | 98.3565
78 | Mudhol | 4 | 4 | 4:26 | 4:26 | 29:58 | 14:53 | 44:51 | 44:51 | 49:17 | 12:19 | 98.4427 | 98.2888 | 49:17 | 12:19 | 98.4427 | 98.2888
79 | Bilagi | 1 | 1 | 6:50 | 6:50 | 8:50 | 2:50 | 11:40 | 11:40 | 18:30 | 18:30 | 98.3796 | 97.4306 | 18:30 | 18:30 | 98.3796 | 97.4306
80 | Lokapur | 2 | 2 | 6:20 | 6:20 | 52:15 | 22:00 | 74:15 | 74:15 | 80:35 | 40:18 | 94.8438 | 94.4039 | 80:35 | 40:18 | 94.8438 | 94.4039
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of May-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2021 |  |  |  | Reliability for cumulative period from Apr-21 to May-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 77 | 77 | 10:50 | 20:00 | 297:47 | 278:16 | 576:03 | 1415:16 | 586:53 | 7:37 | 98.9945 | 98.9756 | 1435:16 | 18:38 | 98.7445 | 98.7268
2 | Dharwad(R) | 19 | 19 | 130:45 | 140:30 | 261:21 | 254:04 | 515:25 | 1017:14 | 646:10 | 34:01 | 96.3539 | 95.4289 | 1157:44 | 60:56 | 96.343 | 95.8379
3 | Kundagol | 1 | 1 | 28:50 | 75:00 | 2:45 | 15:20 | 18:05 | 37:05 | 46:55 | 46:55 | 97.5694 | 93.694 | 112:05 | 112:05 | 97.467 | 92.344
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 5:07 | 8:43 | 13:50 | 26:42 | 13:50 | 13:50 | 98.1407 | 98.1407 | 26:42 | 26:42 | 98.1762 | 98.1762
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 7:10 | 14:49 | 21:59 | 39:44 | 21:59 | 21:59 | 97.0453 | 97.0453 | 39:44 | 39:44 | 97.286 | 97.286
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 15:00 | 31:30 | 46:30 | 173:15 | 46:30 | 23:15 | 96.875 | 96.875 | 173:15 | 86:38 | 94.083 | 94.083
7 | Alnavar | 1 | 1 | 0:00 | 6:10 | 4:25 | 10:50 | 15:15 | 32:15 | 15:15 | 15:15 | 97.9503 | 97.9503 | 38:25 | 38:25 | 97.7971 | 97.3759
8 | Naragund | 2 | 2 | 5:40 | 15:00 | 26:00 | 34:00 | 60:00 | 118:35 | 65:40 | 32:50 | 95.9677 | 95.5869 | 133:35 | 66:48 | 95.95 | 95.4377
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 35:50 | 48:30 | 84:20 | 137:55 | 84:20 | 21:05 | 97.1662 | 97.1662 | 137:55 | 34:29 | 97.6449 | 97.6449
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 52:32 | 61:20 | 113:52 | 208:36 | 113:52 | 28:28 | 96.1738 | 96.1738 | 208:36 | 52:09 | 96.4378 | 96.4378
11 | Naregal | 1 | 1 | 0:00 | 0:00 | 7:50 | 8:50 | 16:40 | 36:00 | 16:40 | 16:40 | 97.7599 | 97.7599 | 36:00 | 36:00 | 97.541 | 97.541
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 23:30 | 31:50 | 55:20 | 110:50 | 55:20 | 27:40 | 96.2814 | 96.2814 | 110:50 | 55:25 | 96.2147 | 96.2147
13 | Ron | 3 | 3 | 0:00 | 0:00 | 26:45 | 107:31 | 134:16 | 200:46 | 134:16 | 44:45 | 93.9845 | 93.9845 | 200:46 | 66:55 | 95.4288 | 95.4288
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 11:15 | 15:55 | 27:10 | 54:20 | 27:10 | 9:03 | 98.7829 | 98.7829 | 54:20 | 18:07 | 98.7629 | 98.7629
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 30:35 | 39:28 | 70:03 | 117:06 | 70:03 | 70:03 | 90.5847 | 90.5847 | 117:06 | 117:06 | 92.0014 | 92.0014
16 | G.C.T.M | 1 | 1 | 12:25 | 21:35 | 17:30 | 3:25 | 20:55 | 32:35 | 33:20 | 33:20 | 97.1886 | 95.5197 | 54:10 | 54:10 | 97.7744 | 96.3001
17 | F.C.S.M | 2 | 2 | 23:20 | 32:20 | 30:40 | 4:20 | 35:00 | 45:25 | 58:20 | 29:10 | 97.6478 | 96.0797 | 77:45 | 38:52 | 98.4489 | 97.3446
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 6:43 | 7:14 | 13:57 | 26:08 | 13:57 | 13:57 | 98.125 | 98.125 | 26:08 | 26:08 | 98.2149 | 98.2149
19 | Hole-Alur | 1 | 1 | 5:40 | 26:20 | 8:40 | 2:45 | 11:25 | 36:55 | 17:05 | 17:05 | 98.4655 | 97.7039 | 63:15 | 63:15 | 97.4784 | 95.6796
20 | Savanur | 2 | 2 | 1:40 | 4:10 | 16:35 | 15:25 | 32:00 | 64:40 | 33:40 | 16:50 | 97.8495 | 97.7375 | 68:50 | 34:25 | 97.7914 | 97.6491
21 | Shiggaon | 2 | 2 | 0:45 | 14:20 | 11:20 | 26:05 | 37:25 | 139:35 | 38:10 | 19:05 | 97.4854 | 97.435 | 153:55 | 76:57 | 95.2328 | 94.7433
22 | Bankapur | 1 | 1 | 11:55 | 19:10 | 20:40 | 8:55 | 29:35 | 48:10 | 41:30 | 41:30 | 96.0237 | 94.422 | 67:20 | 67:20 | 96.7099 | 95.4007
23 | Hangal | 2 | 2 | 21:30 | 54:10 | 67:05 | 44:15 | 111:20 | 167:50 | 132:50 | 66:25 | 92.5179 | 91.073 | 222:00 | 111:00 | 94.268 | 92.418
24 | Ranebennur | 16 | 16 | 5:36 | 46:31 | 158:15 | 191:29 | 349:44 | 464:57 | 355:20 | 22:12 | 97.0621 | 97.015 | 511:28 | 31:58 | 98.0151 | 97.8165
25 | Halageri | 2 | 2 | 56:50 | 111:10 | 42:15 | 165:15 | 207:30 | 237:10 | 264:20 | 132:10 | 86.0551 | 82.2357 | 348:20 | 174:10 | 91.9 | 88.1034
26 | Tuminakatti | 2 | 2 | 0:10 | 2:10 | 27:50 | 13:30 | 41:20 | 79:25 | 41:30 | 20:45 | 97.2222 | 97.211 | 81:35 | 40:48 | 97.2877 | 97.2137
27 | Kahanderayanahalli | 1 | 1 | 1:42 | 2:42 | 19:40 | 85:55 | 105:35 | 182:25 | 107:17 | 107:17 | 85.8087 | 85.5802 | 185:07 | 185:07 | 87.5398 | 87.3554
28 | Rattihalli | 1 | 1 | 0:20 | 3:00 | 10:25 | 14:35 | 25:00 | 50:25 | 25:20 | 25:20 | 96.6398 | 96.595 | 53:25 | 53:25 | 96.5562 | 96.3513
29 | Hirekerur | 2 | 2 | 5:15 | 35:35 | 16:00 | 24:20 | 40:20 | 91:00 | 45:35 | 22:47 | 97.2894 | 96.9366 | 126:35 | 63:18 | 96.8921 | 95.6768
30 | Byadagi | 8 | 8 | 51:40 | 81:50 | 161:50 | 416:30 | 578:20 | 852:05 | 630:00 | 78:45 | 90.2834 | 89.4153 | 933:55 | 116:44 | 92.7247 | 92.026
31 | Sirsi | 5 | 5 | 5:15 | 9:50 | 16:36 | 37:34 | 54:10 | 117:35 | 59:25 | 11:53 | 98.5439 | 98.4028 | 127:25 | 25:29 | 98.3937 | 98.2593
32 | Yellapur | 3 | 3 | 79:15 | 91:18 | 19:25 | 15:25 | 34:50 | 59:40 | 114:05 | 38:02 | 98.4394 | 94.8887 | 150:58 | 50:19 | 98.6415 | 96.5627
33 | Mundagod | 3 | 3 | 4:15 | 4:15 | 31:20 | 47:20 | 78:40 | 174:10 | 82:55 | 27:38 | 96.4755 | 96.2851 | 178:25 | 59:28 | 96.0345 | 95.9377
34 | Siddapur | 2 | 2 | 0:10 | 4:20 | 10:05 | 13:10 | 23:15 | 48:00 | 23:25 | 11:42 | 98.4375 | 98.4263 | 52:20 | 26:10 | 98.3607 | 98.2127
35 | Dandeli | 8 | 8 | 14:24 | 53:04 | 120:18 | 97:28 | 217:46 | 320:04 | 232:10 | 29:01 | 96.3413 | 96.0994 | 373:08 | 46:38 | 97.2672 | 96.8141
36 | Haliyal | 3 | 3 | 1:33 | 1:52 | 20:23 | 31:17 | 51:40 | 116:04 | 53:13 | 17:44 | 97.6852 | 97.6157 | 117:56 | 39:19 | 97.3573 | 97.3148
37 | Ankola | 3 | 3 | 41:25 | 57:48 | 17:40 | 17:40 | 35:20 | 55:49 | 76:45 | 25:35 | 98.417 | 96.5614 | 113:37 | 37:52 | 98.7291 | 97.4131
38 | Kumta | 3 | 3 | 2:36 | 6:06 | 20:00 | 32:01 | 52:01 | 77:25 | 54:37 | 18:12 | 97.6695 | 97.553 | 83:31 | 27:50 | 98.2373 | 98.0984
39 | Gokarna | 1 | 1 | 14:04 | 19:01 | 10:35 | 1:45 | 12:20 | 15:10 | 26:24 | 26:24 | 98.3423 | 96.4516 | 34:11 | 34:11 | 98.964 | 97.6651
40 | Kasarkod | 1 | 1 | 26:21 | 65:01 | 16:20 | 13:15 | 29:35 | 44:15 | 55:56 | 55:56 | 96.0237 | 92.4821 | 109:16 | 109:16 | 96.9775 | 92.5364
41 | Honnavar | 3 | 3 | 12:30 | 25:45 | 29:27 | 55:14 | 84:41 | 108:01 | 97:11 | 32:24 | 96.2059 | 95.6459 | 133:46 | 44:35 | 97.5406 | 96.9543
42 | Murdeshwar | 4 | 4 | 32:04 | 52:40 | 127:11 | 130:05 | 257:16 | 342:11 | 289:20 | 72:20 | 91.3553 | 90.2778 | 394:51 | 98:43 | 94.1567 | 93.2573
43 | Bhatkal | 3 | 3 | 81:09 | 91:12 | 29:15 | 43:02 | 72:17 | 100:36 | 153:26 | 51:09 | 96.7615 | 93.1257 | 191:48 | 63:56 | 97.7095 | 95.633
44 | Khanapur | 2 | 2 | 8:30 | 15:20 | 22:45 | 26:15 | 49:00 | 78:10 | 57:30 | 28:45 | 96.707 | 96.1358 | 93:30 | 46:45 | 97.3304 | 96.8067
45 | Bailhongal | 3 | 3 | 1:30 | 47:55 | 58:50 | 86:40 | 145:30 | 314:25 | 147:00 | 49:00 | 93.4812 | 93.414 | 362:20 | 120:47 | 92.8412 | 91.7502
46 | Soundatti | 3 | 3 | 12:00 | 13:00 | 53:51 | 37:23 | 91:14 | 180:03 | 103:14 | 34:25 | 95.9125 | 95.3749 | 193:03 | 64:21 | 95.9005 | 95.6045
47 | Ramdurg | 2 | 2 | 0:40 | 7:10 | 23:22 | 18:58 | 42:20 | 67:50 | 43:00 | 21:30 | 97.155 | 97.1102 | 75:00 | 37:30 | 97.6833 | 97.4385
48 | Gokak | 10 | 10 | 3:47 | 14:14 | 24:24 | 17:51 | 42:15 | 97:08 | 46:02 | 4:36 | 99.4321 | 99.3813 | 111:22 | 11:08 | 99.3365 | 99.2393
49 | Mudalagi | 2 | 2 | 2:00 | 4:20 | 13:00 | 15:05 | 28:05 | 50:10 | 30:05 | 15:02 | 98.1127 | 97.9783 | 54:30 | 27:15 | 98.2867 | 98.1387
50 | Konnur | 1 | 1 | 0:00 | 0:15 | 21:25 | 6:35 | 28:00 | 79:10 | 28:00 | 28:00 | 96.2366 | 96.2366 | 79:25 | 79:25 | 94.5924 | 94.5754
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 22:00 | 23:50 | 45:50 | 74:25 | 45:50 | 45:50 | 93.8396 | 93.8396 | 74:25 | 74:25 | 94.9169 | 94.9169
52 | Kudachi | 1 | 1 | 0:00 | 0:00 | 25:00 | 5:00 | 30:00 | 100:05 | 30:00 | 30:00 | 95.9677 | 95.9677 | 100:05 | 100:05 | 93.1637 | 93.1637
53 | Athani | 5 | 5 | 34:12 | 77:10 | 58:36 | 103:31 | 162:07 | 315:46 | 196:19 | 39:16 | 95.642 | 94.7227 | 392:56 | 78:35 | 95.6862 | 94.6321
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 18:35 | 35:25 | 54:00 | 70:50 | 54:00 | 27:00 | 96.371 | 96.371 | 70:50 | 35:25 | 97.5808 | 97.5808
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 52:30 | 32:25 | 84:55 | 209:05 | 84:55 | 16:59 | 97.7173 | 97.7173 | 209:05 | 41:49 | 97.1437 | 97.1437
56 | Sadalaga | 1 | 1 | 0:00 | 0:00 | 7:45 | 13:15 | 21:00 | 36:00 | 21:00 | 21:00 | 97.1774 | 97.1774 | 36:00 | 36:00 | 97.541 | 97.541
57 | Muddebihal | 2 | 2 | 2:10 | 8:10 | 37:25 | 34:55 | 72:20 | 157:15 | 74:30 | 37:15 | 95.1389 | 94.9933 | 165:25 | 82:42 | 94.6294 | 94.3505
58 | Talikoti | 1 | 1 | 3:35 | 11:35 | 12:55 | 8:25 | 21:20 | 36:15 | 24:55 | 24:55 | 97.1326 | 96.651 | 47:50 | 47:50 | 97.5239 | 96.7327
59 | B.Bagewadi | 1 | 1 | 2:10 | 5:37 | 10:02 | 9:40 | 19:42 | 26:02 | 21:52 | 21:52 | 97.3522 | 97.0609 | 31:39 | 31:39 | 98.2218 | 97.8381
60 | Indi | 3 | 3 | 0:00 | 5:33 | 4:20 | 17:30 | 21:50 | 50:59 | 21:50 | 7:17 | 99.0218 | 99.0218 | 56:32 | 18:51 | 98.8392 | 98.7128
61 | Sindagi | 2 | 2 | 27:00 | 35:40 | 22:55 | 12:45 | 35:40 | 71:55 | 62:40 | 31:20 | 97.603 | 95.7885 | 107:35 | 53:48 | 97.5438 | 96.3257
62 | Guledgudda | 1 | 1 | 0:00 | 4:54 | 5:08 | 11:53 | 17:01 | 67:25 | 17:01 | 17:01 | 97.7128 | 97.7128 | 72:19 | 72:19 | 95.395 | 95.0603
63 | Ilkal | 8 | 8 | 56:24 | 103:59 | 126:18 | 282:29 | 408:47 | 749:58 | 465:11 | 58:09 | 93.132 | 92.1844 | 853:57 | 106:45 | 93.5966 | 92.7088
64 | Kerur | 2 | 2 | 0:05 | 10:30 | 14:36 | 22:25 | 37:01 | 65:28 | 37:06 | 18:33 | 97.5123 | 97.5067 | 75:58 | 37:59 | 97.7641 | 97.4055
65 | Hungund | 4 | 4 | 22:16 | 47:08 | 50:16 | 95:53 | 146:09 | 229:05 | 168:25 | 42:06 | 95.089 | 94.3408 | 276:13 | 69:03 | 96.0881 | 95.2832
66 | Gaddankeri | 3 | 3 | 3:02 | 18:20 | 33:17 | 21:27 | 54:44 | 133:31 | 57:46 | 19:15 | 97.5478 | 97.4119 | 151:51 | 50:37 | 96.96 | 96.5426
67 | Rampur | 1 | 1 | 0:15 | 5:48 | 7:27 | 5:51 | 13:18 | 35:45 | 13:33 | 13:33 | 98.2124 | 98.1788 | 41:33 | 41:33 | 97.5581 | 97.1619
68 | Kaladagi | 2 | 2 | 0:00 | 4:42 | 15:54 | 27:51 | 43:45 | 83:21 | 43:45 | 21:52 | 97.0598 | 97.0598 | 88:03 | 44:02 | 97.1533 | 96.9928
69 | Achanur | 1 | 1 | 0:09 | 3:12 | 24:09 | 9:42 | 33:51 | 52:45 | 34:00 | 34:00 | 95.4503 | 95.4301 | 55:57 | 55:57 | 96.3969 | 96.1783
70 | Shirur | 1 | 1 | 5:33 | 13:48 | 6:30 | 37:54 | 44:24 | 52:39 | 49:57 | 49:57 | 94.0323 | 93.2863 | 66:27 | 66:27 | 96.4037 | 95.4611
71 | Badami | 1 | 1 | 0:15 | 6:27 | 5:07 | 19:46 | 24:53 | 48:06 | 25:08 | 25:08 | 96.6555 | 96.6219 | 54:33 | 54:33 | 96.7145 | 96.2739
72 | Kulageri | 1 | 1 | 2:00 | 6:56 | 4:15 | 3:50 | 8:05 | 13:55 | 10:05 | 10:05 | 98.9135 | 98.6447 | 20:51 | 20:51 | 99.0494 | 98.5758
73 | Jamkhandi | 6 | 6 | 0:00 | 7:30 | 52:25 | 29:25 | 81:50 | 187:55 | 81:50 | 13:38 | 98.1668 | 98.1668 | 195:25 | 32:34 | 97.8607 | 97.7753
74 | Mahalingapur | 3 | 3 | 0:00 | 1:00 | 52:07 | 15:40 | 67:47 | 144:48 | 67:47 | 22:36 | 96.9631 | 96.9631 | 145:48 | 48:36 | 96.7031 | 96.6803
75 | Rabakavi | 2 | 2 | 1:00 | 8:45 | 14:40 | 6:45 | 21:25 | 42:15 | 22:25 | 11:12 | 98.5607 | 98.4935 | 51:00 | 25:30 | 98.557 | 98.2582
76 | Banahatti | 2 | 2 | 0:00 | 0:30 | 27:25 | 4:25 | 31:50 | 46:15 | 31:50 | 15:55 | 97.8607 | 97.8607 | 46:45 | 23:22 | 98.4204 | 98.4033
77 | Terdal | 2 | 2 | 0:00 | 0:00 | 28:50 | 6:45 | 35:35 | 59:15 | 35:35 | 17:48 | 97.6086 | 97.6086 | 59:15 | 29:38 | 97.9764 | 97.9764
78 | Mudhol | 4 | 4 | 1:35 | 6:01 | 54:56 | 34:41 | 89:37 | 134:28 | 91:12 | 22:48 | 96.9887 | 96.9355 | 140:29 | 35:07 | 97.7038 | 97.601
79 | Bilagi | 1 | 1 | 4:58 | 11:48 | 8:10 | 5:10 | 13:20 | 25:00 | 18:18 | 18:18 | 98.2079 | 97.5403 | 36:48 | 36:48 | 98.2923 | 97.4863
80 | Lokapur | 2 | 2 | 0:00 | 6:20 | 39:40 | 23:05 | 62:45 | 137:00 | 62:45 | 31:22 | 95.7829 | 95.7829 | 143:20 | 71:40 | 95.321 | 95.1047
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of June-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2021 |  |  |  | Reliability for cumulative period from Apr-21 to June-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 77 | 77 | 1:15 | 21:15 | 259:44 | 297:50 | 557:34 | 1972:50 | 558:49 | 7:15 | 98.9943 | 98.992 | 1994:05 | 25:54 | 98.8269 | 98.8142
2 | Dharwad(R) | 19 | 19 | 2:15 | 142:45 | 256:59 | 181:43 | 438:42 | 1455:56 | 440:57 | 23:12 | 96.7931 | 96.7767 | 1598:41 | 84:08 | 96.4914 | 96.1474
3 | Kundagol | 1 | 1 | 6:40 | 81:40 | 7:45 | 10:40 | 18:25 | 55:30 | 25:05 | 25:05 | 97.4421 | 96.5162 | 137:10 | 137:10 | 97.4588 | 93.7195
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 3:23 | 5:42 | 9:05 | 35:47 | 9:05 | 9:05 | 98.7384 | 98.7384 | 35:47 | 35:47 | 98.3616 | 98.3616
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 6:45 | 7:10 | 13:55 | 53:39 | 13:55 | 13:55 | 98.0671 | 98.0671 | 53:39 | 53:39 | 97.5435 | 97.5435
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 10:05 | 127:20 | 137:25 | 310:40 | 137:25 | 68:42 | 90.4572 | 90.4572 | 310:40 | 155:20 | 92.8877 | 92.8877
7 | Alnavar | 1 | 1 | 0:00 | 6:10 | 12:10 | 17:45 | 29:55 | 62:10 | 29:55 | 29:55 | 95.8449 | 95.8449 | 68:20 | 68:20 | 97.1535 | 96.8712
8 | Naragund | 2 | 2 | 4:20 | 19:20 | 20:00 | 27:05 | 47:05 | 165:40 | 51:25 | 25:42 | 96.7303 | 96.4294 | 185:00 | 92:30 | 96.2073 | 95.7647
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 43:15 | 53:35 | 96:50 | 234:45 | 96:50 | 24:12 | 96.6377 | 96.6377 | 234:45 | 58:41 | 97.3128 | 97.3128
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 54:36 | 47:17 | 101:53 | 310:29 | 101:53 | 25:28 | 96.4624 | 96.4624 | 310:29 | 77:37 | 96.4459 | 96.4459
11 | Naregal | 1 | 1 | 5:05 | 5:05 | 9:15 | 2:55 | 12:10 | 48:10 | 17:15 | 17:15 | 98.3102 | 97.6042 | 53:15 | 53:15 | 97.7946 | 97.5618
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 26:25 | 17:00 | 43:25 | 154:15 | 43:25 | 21:42 | 96.985 | 96.985 | 154:15 | 77:08 | 96.4686 | 96.4686
13 | Ron | 3 | 3 | 14:15 | 14:15 | 28:10 | 31:15 | 59:25 | 260:11 | 73:40 | 24:33 | 97.2492 | 96.5895 | 274:26 | 91:29 | 96.0289 | 95.8115
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 13:45 | 15:45 | 29:30 | 83:50 | 29:30 | 9:50 | 98.6343 | 98.6343 | 83:50 | 27:57 | 98.7205 | 98.7205
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 21:35 | 18:53 | 40:28 | 157:34 | 40:28 | 40:28 | 94.3796 | 94.3796 | 157:34 | 157:34 | 92.7854 | 92.7854
16 | G.C.T.M | 1 | 1 | 4:10 | 25:45 | 13:20 | 4:10 | 17:30 | 50:05 | 21:40 | 21:40 | 97.5694 | 96.9907 | 75:50 | 75:50 | 97.7068 | 96.5278
17 | F.C.S.M | 2 | 2 | 10:45 | 43:05 | 10:45 | 3:20 | 14:05 | 59:30 | 24:50 | 12:25 | 99.022 | 98.2755 | 102:35 | 51:18 | 98.6378 | 97.6515
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 6:31 | 3:08 | 9:39 | 35:47 | 9:39 | 9:39 | 98.6597 | 98.6597 | 35:47 | 35:47 | 98.3616 | 98.3616
19 | Hole-Alur | 1 | 1 | 13:20 | 39:40 | 7:40 | 3:05 | 10:45 | 47:40 | 24:05 | 24:05 | 98.5069 | 96.6551 | 87:20 | 87:20 | 97.8175 | 96.0012
20 | Savanur | 3 | 3 | 0:00 | 4:10 | 13:10 | 40:50 | 54:00 | 118:40 | 54:00 | 18:00 | 97.5 | 97.5 | 122:50 | 40:57 | 98.1888 | 98.1253
21 | Shiggaon | 2 | 2 | 0:00 | 14:20 | 27:15 | 46:45 | 74:00 | 213:35 | 74:00 | 37:00 | 94.8611 | 94.8611 | 227:55 | 113:57 | 95.1103 | 94.7821
22 | Bankapur | 1 | 1 | 2:00 | 21:10 | 19:20 | 13:50 | 33:10 | 81:20 | 35:10 | 35:10 | 95.3935 | 95.1157 | 102:30 | 102:30 | 96.2759 | 95.3068
23 | Hangal | 2 | 2 | 0:30 | 54:40 | 23:05 | 45:25 | 68:30 | 236:20 | 69:00 | 34:30 | 95.2431 | 95.2083 | 291:00 | 145:30 | 94.5894 | 93.3379
24 | Ranebennur | 16 | 16 | 8:25 | 54:56 | 105:44 | 105:52 | 211:36 | 676:33 | 220:01 | 13:45 | 98.1632 | 98.0901 | 731:29 | 45:43 | 98.0639 | 97.9067
25 | Halageri | 2 | 2 | 7:55 | 119:05 | 37:20 | 2:10 | 39:30 | 276:40 | 47:25 | 23:42 | 97.2569 | 96.7072 | 395:45 | 197:52 | 93.6661 | 90.9398
26 | Tuminakatti | 2 | 2 | 0:10 | 2:20 | 18:00 | 3:45 | 21:45 | 101:10 | 21:55 | 10:58 | 98.4896 | 98.478 | 103:30 | 51:45 | 97.6839 | 97.6305
27 | Kahanderayanahalli | 1 | 1 | 0:10 | 2:52 | 13:55 | 39:05 | 53:00 | 235:25 | 53:10 | 53:10 | 92.6389 | 92.6157 | 238:17 | 238:17 | 89.2208 | 89.0896
28 | Rattihalli | 1 | 1 | 0:10 | 3:10 | 21:00 | 3:15 | 24:15 | 74:40 | 24:25 | 24:25 | 96.6319 | 96.6088 | 77:50 | 77:50 | 96.5812 | 96.4362
29 | Hirekerur | 2 | 2 | 1:55 | 37:30 | 21:55 | 15:45 | 37:40 | 128:40 | 39:35 | 19:48 | 97.3843 | 97.2512 | 166:10 | 83:05 | 97.0543 | 96.1958
30 | Byadagi | 8 | 8 | 18:10 | 100:00 | 106:00 | 57:45 | 163:45 | 1015:50 | 181:55 | 22:44 | 97.1571 | 96.8417 | 1115:50 | 139:29 | 94.1859 | 93.6136
31 | Sirsi | 5 | 5 | 9:10 | 19:00 | 15:17 | 43:28 | 58:45 | 176:20 | 67:55 | 13:35 | 98.3681 | 98.1134 | 195:20 | 39:04 | 98.3852 | 98.2112
32 | Yellapur | 3 | 3 | 34:45 | 126:03 | 2:25 | 18:20 | 20:45 | 80:25 | 55:30 | 18:30 | 99.0394 | 97.4306 | 206:28 | 68:49 | 98.7726 | 96.8488
33 | Mundagod | 3 | 3 | 1:03 | 5:18 | 23:23 | 43:20 | 66:43 | 240:53 | 67:46 | 22:35 | 96.9113 | 96.8627 | 246:11 | 82:04 | 96.3235 | 96.2426
34 | Siddapur | 2 | 2 | 8:00 | 12:20 | 11:05 | 27:10 | 38:15 | 86:15 | 46:15 | 23:08 | 97.3438 | 96.7882 | 98:35 | 49:17 | 98.0254 | 97.7431
35 | Dandeli | 8 | 8 | 6:20 | 59:24 | 35:33 | 104:20 | 139:53 | 459:57 | 146:13 | 18:17 | 97.5715 | 97.4615 | 519:21 | 64:55 | 97.3675 | 97.0275
36 | Haliyal | 3 | 3 | 4:24 | 6:16 | 12:10 | 20:15 | 32:25 | 148:29 | 36:49 | 12:16 | 98.4992 | 98.2955 | 154:45 | 51:35 | 97.7338 | 97.6381
37 | Ankola | 3 | 3 | 38:22 | 96:10 | 16:03 | 17:36 | 33:39 | 89:28 | 72:01 | 24:00 | 98.4421 | 96.6659 | 185:38 | 61:53 | 98.6345 | 97.1668
38 | Kumta | 3 | 3 | 3:33 | 9:39 | 15:51 | 23:46 | 39:37 | 117:02 | 43:10 | 14:23 | 98.1659 | 98.0015 | 126:41 | 42:14 | 98.2138 | 98.0665
39 | Gokarna | 1 | 1 | 21:45 | 40:46 | 20:00 | 3:55 | 23:55 | 39:05 | 45:40 | 45:40 | 96.6782 | 93.6574 | 79:51 | 79:51 | 98.2105 | 96.3439
40 | Kasarkod | 1 | 1 | 33:56 | 98:57 | 26:57 | 12:03 | 39:00 | 83:15 | 72:56 | 72:56 | 94.5833 | 89.8704 | 182:12 | 182:12 | 96.1882 | 91.6575
41 | Honnavar | 3 | 3 | 3:33 | 29:18 | 47:55 | 22:41 | 70:36 | 178:37 | 74:09 | 24:43 | 96.7315 | 96.5671 | 207:55 | 69:18 | 97.2739 | 96.8267
42 | Murdeshwar | 4 | 4 | 4:48 | 57:28 | 54:51 | 21:29 | 76:20 | 418:31 | 81:08 | 20:17 | 97.3495 | 97.1829 | 475:59 | 119:00 | 95.2093 | 94.5515
43 | Bhatkal | 3 | 3 | 24:45 | 115:57 | 31:15 | 18:01 | 49:16 | 149:52 | 74:01 | 24:40 | 97.7191 | 96.5733 | 265:49 | 88:36 | 97.7127 | 95.943
44 | Khanapur | 2 | 2 | 10:10 | 25:30 | 30:30 | 14:50 | 45:20 | 123:30 | 55:30 | 27:45 | 96.8519 | 96.1458 | 149:00 | 74:30 | 97.1726 | 96.5888
45 | Bailhongal | 3 | 3 | 0:00 | 47:55 | 56:40 | 85:45 | 142:25 | 456:50 | 142:25 | 47:28 | 93.4066 | 93.4066 | 504:45 | 168:15 | 93.0276 | 92.2962
46 | Soundatti | 3 | 3 | 5:05 | 18:05 | 63:35 | 25:03 | 88:38 | 268:41 | 93:43 | 31:14 | 95.8966 | 95.6613 | 286:46 | 95:35 | 95.8992 | 95.6232
47 | Ramdurg | 2 | 2 | 6:50 | 14:00 | 26:20 | 21:55 | 48:15 | 116:05 | 55:05 | 27:32 | 96.6493 | 96.1748 | 130:05 | 65:02 | 97.3424 | 97.0219
48 | Gokak | 10 | 10 | 4:51 | 19:05 | 14:57 | 26:09 | 41:06 | 138:14 | 45:57 | 4:36 | 99.4292 | 99.3618 | 157:19 | 15:44 | 99.3671 | 99.2797
49 | Mudalagi | 2 | 2 | 1:10 | 5:30 | 29:10 | 16:25 | 45:35 | 95:45 | 46:45 | 23:23 | 96.8345 | 96.7535 | 101:15 | 50:38 | 97.8079 | 97.682
50 | Konnur | 1 | 1 | 0:00 | 0:15 | 17:50 | 2:30 | 20:20 | 99:30 | 20:20 | 20:20 | 97.1759 | 97.1759 | 99:45 | 99:45 | 95.4441 | 95.4327
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 14:35 | 10:10 | 24:45 | 99:10 | 24:45 | 24:45 | 96.5625 | 96.5625 | 99:10 | 99:10 | 95.4594 | 95.4594
52 | Kudachi | 1 | 1 | 1:10 | 1:10 | 31:05 | 0:00 | 31:05 | 131:10 | 32:15 | 32:15 | 95.6829 | 95.5208 | 132:20 | 132:20 | 93.9942 | 93.9408
53 | Athani | 6 | 6 | 17:42 | 94:52 | 54:45 | 66:37 | 121:22 | 437:08 | 139:04 | 23:11 | 97.1906 | 96.7809 | 532:00 | 88:40 | 96.6641 | 95.9402
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 10:30 | 11:35 | 22:05 | 92:55 | 22:05 | 11:02 | 98.4664 | 98.4664 | 92:55 | 46:28 | 97.8728 | 97.8728
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 65:10 | 56:25 | 121:35 | 330:40 | 121:35 | 24:19 | 96.6227 | 96.6227 | 330:40 | 66:08 | 96.9719 | 96.9719
56 | Sadalaga | 1 | 1 | 0:10 | 0:10 | 9:10 | 10:05 | 19:15 | 55:15 | 19:25 | 19:25 | 97.3264 | 97.3032 | 55:25 | 55:25 | 97.4702 | 97.4626
57 | Muddebihal | 2 | 2 | 39:40 | 47:50 | 64:20 | 37:20 | 101:40 | 258:55 | 141:20 | 70:40 | 92.9398 | 90.1852 | 306:45 | 153:22 | 94.0724 | 92.9773
58 | Talikoti | 1 | 1 | 2:30 | 14:05 | 11:00 | 8:00 | 19:00 | 55:15 | 21:30 | 21:30 | 97.3611 | 97.0139 | 69:20 | 69:20 | 97.4702 | 96.8254
59 | B.Bagewadi | 1 | 1 | 2:20 | 7:57 | 4:00 | 3:45 | 7:45 | 33:47 | 10:05 | 10:05 | 98.9236 | 98.5995 | 41:44 | 41:44 | 98.4531 | 98.0891
60 | Indi | 3 | 3 | 0:00 | 5:33 | 5:43 | 9:27 | 15:10 | 66:09 | 15:10 | 5:03 | 99.2978 | 99.2978 | 71:42 | 23:54 | 98.9904 | 98.9057
61 | Sindagi | 2 | 2 | 4:20 | 40:00 | 19:10 | 17:30 | 36:40 | 108:35 | 41:00 | 20:30 | 97.4537 | 97.1528 | 148:35 | 74:18 | 97.5141 | 96.5984
62 | Guledgudda | 1 | 1 | 0:00 | 4:54 | 17:04 | 6:48 | 23:52 | 91:17 | 23:52 | 23:52 | 96.6852 | 96.6852 | 96:11 | 96:11 | 95.8204 | 95.596
63 | Ilkal | 8 | 8 | 40:03 | 144:02 | 162:00 | 222:00 | 384:00 | 1133:58 | 424:03 | 53:00 | 93.3333 | 92.638 | 1278:00 | 159:45 | 93.5098 | 92.6854
64 | Kerur | 2 | 2 | 1:55 | 12:25 | 18:25 | 14:57 | 33:22 | 98:50 | 35:17 | 17:39 | 97.6829 | 97.5498 | 111:15 | 55:38 | 97.7373 | 97.4531
65 | Hungund | 4 | 4 | 24:52 | 72:00 | 32:49 | 50:07 | 82:56 | 312:01 | 107:48 | 26:57 | 97.1204 | 96.2569 | 384:01 | 96:00 | 96.4284 | 95.6042
66 | Gaddankeri | 3 | 3 | 6:50 | 25:10 | 72:21 | 28:37 | 100:58 | 234:29 | 107:48 | 35:56 | 95.3256 | 95.0093 | 259:39 | 86:33 | 96.4212 | 96.0371
67 | Rampur | 1 | 1 | 0:12 | 6:00 | 16:18 | 3:18 | 19:36 | 55:21 | 19:48 | 19:48 | 97.2778 | 97.25 | 61:21 | 61:21 | 97.4657 | 97.1909
68 | Kaladagi | 2 | 2 | 1:00 | 5:42 | 40:24 | 27:48 | 68:12 | 151:33 | 69:12 | 34:36 | 95.2639 | 95.1944 | 157:15 | 78:38 | 96.5304 | 96.4
69 | Achanur | 1 | 1 | 0:12 | 3:24 | 28:03 | 24:42 | 52:45 | 105:30 | 52:57 | 52:57 | 92.6736 | 92.6458 | 108:54 | 108:54 | 95.1694 | 95.0137
70 | Shirur | 1 | 1 | 9:26 | 23:14 | 7:21 | 42:07 | 49:28 | 102:07 | 58:54 | 58:54 | 93.1296 | 91.8194 | 125:21 | 125:21 | 95.3243 | 94.2605
71 | Badami | 1 | 1 | 5:58 | 12:25 | 17:25 | 20:35 | 38:00 | 86:06 | 43:58 | 43:58 | 94.7222 | 93.8935 | 98:31 | 98:31 | 96.0577 | 95.4892
72 | Kulageri | 1 | 1 | 1:55 | 8:51 | 5:15 | 6:05 | 11:20 | 25:15 | 13:15 | 13:15 | 98.4259 | 98.1597 | 34:06 | 34:06 | 98.8439 | 98.4386
73 | Jamkhandi | 6 | 6 | 42:00 | 49:30 | 59:35 | 30:10 | 89:45 | 277:40 | 131:45 | 21:57 | 97.9225 | 96.9502 | 327:10 | 54:32 | 97.8811 | 97.5033
74 | Mahalingapur | 3 | 3 | 1:38 | 2:38 | 30:27 | 10:39 | 41:06 | 185:54 | 42:44 | 14:15 | 98.0972 | 98.0216 | 188:32 | 62:51 | 97.1627 | 97.1225
75 | Rabakavi | 2 | 2 | 5:20 | 14:05 | 11:25 | 5:00 | 16:25 | 58:40 | 21:45 | 10:52 | 98.86 | 98.4896 | 72:45 | 36:22 | 98.6569 | 98.3345
76 | Banahatti | 2 | 2 | 5:40 | 6:10 | 19:20 | 5:40 | 25:00 | 71:15 | 30:40 | 15:20 | 98.2639 | 97.8704 | 77:25 | 38:42 | 98.3688 | 98.2276
77 | Terdal | 2 | 2 | 1:10 | 1:10 | 28:00 | 7:45 | 35:45 | 95:00 | 36:55 | 18:28 | 97.5174 | 97.4363 | 96:10 | 48:05 | 97.8251 | 97.7984
78 | Mudhol | 4 | 4 | 11:06 | 17:07 | 30:34 | 12:37 | 43:11 | 177:39 | 54:17 | 13:34 | 98.5006 | 98.1152 | 194:46 | 48:42 | 97.9665 | 97.7705
79 | Bilagi | 1 | 1 | 1:25 | 13:13 | 9:50 | 6:00 | 15:50 | 40:50 | 17:15 | 17:15 | 97.8009 | 97.6042 | 54:03 | 54:03 | 98.1303 | 97.5252
80 | Lokapur | 2 | 2 | 0:00 | 6:20 | 51:25 | 30:30 | 81:55 | 218:55 | 81:55 | 40:58 | 94.3113 | 94.3113 | 225:15 | 112:38 | 94.9882 | 94.8432
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of July-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2021 |  |  |  | Reliability for cumulative period from Apr-21 to July-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 78 | 78 | 10:07 | 31:22 | 232:18 | 257:09 | 489:27 | 2462:17 | 499:34 | 6:24 | 99.1566 | 99.1392 | 2493:39 | 31:58 | 98.9219 | 98.9081
2 | Dharwad(R) | 19 | 19 | 8:50 | 151:35 | 208:46 | 472:34 | 681:20 | 2137:16 | 690:10 | 36:19 | 95.1802 | 95.1177 | 2288:51 | 120:28 | 96.1582 | 95.8857
3 | Kundagol | 1 | 1 | 12:05 | 93:45 | 1:05 | 2:15 | 3:20 | 58:50 | 15:25 | 15:25 | 99.552 | 97.9279 | 152:35 | 152:35 | 97.9907 | 94.7888
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 4:52 | 12:52 | 17:44 | 53:31 | 17:44 | 17:44 | 97.6165 | 97.6165 | 53:31 | 53:31 | 98.1722 | 98.1722
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 5:50 | 3:45 | 9:35 | 63:14 | 9:35 | 9:35 | 98.7119 | 98.7119 | 63:14 | 63:14 | 97.8404 | 97.8404
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 7:40 | 18:05 | 25:45 | 336:25 | 25:45 | 12:52 | 98.2695 | 98.2695 | 336:25 | 168:12 | 94.2552 | 94.2552
7 | Alnavar | 1 | 1 | 0:00 | 6:10 | 10:25 | 14:40 | 25:05 | 87:15 | 25:05 | 25:05 | 96.6286 | 96.6286 | 93:25 | 93:25 | 97.0202 | 96.8095
8 | Naragund | 2 | 2 | 16:20 | 35:40 | 21:55 | 25:10 | 47:05 | 212:45 | 63:25 | 31:42 | 96.8358 | 95.7381 | 248:25 | 124:12 | 96.367 | 95.7579
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 23:10 | 32:15 | 55:25 | 290:10 | 55:25 | 13:51 | 98.1379 | 98.1379 | 290:10 | 72:32 | 97.5225 | 97.5225
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 56:13 | 25:58 | 82:11 | 392:40 | 82:11 | 20:33 | 97.2385 | 97.2385 | 392:40 | 98:10 | 96.6473 | 96.6473
11 | Naregal | 1 | 1 | 5:50 | 10:55 | 1:35 | 1:55 | 3:30 | 51:40 | 9:20 | 9:20 | 99.5296 | 98.7455 | 62:35 | 62:35 | 98.2354 | 97.8626
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 27:30 | 10:00 | 37:30 | 191:45 | 37:30 | 18:45 | 97.4798 | 97.4798 | 191:45 | 95:52 | 96.7256 | 96.7256
13 | Ron | 3 | 3 | 0:00 | 14:15 | 22:55 | 27:26 | 50:21 | 310:32 | 50:21 | 16:47 | 97.7442 | 97.7442 | 324:47 | 108:16 | 96.4648 | 96.3026
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 31:45 | 21:50 | 53:35 | 137:25 | 53:35 | 17:52 | 97.5993 | 97.5993 | 137:25 | 45:48 | 98.4356 | 98.4356
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 14:41 | 0:25 | 15:06 | 172:40 | 15:06 | 15:06 | 97.9704 | 97.9704 | 172:40 | 172:40 | 94.1029 | 94.1029
16 | G.C.T.M | 1 | 1 | 4:40 | 30:25 | 10:05 | 5:00 | 15:05 | 65:10 | 19:45 | 19:45 | 97.9727 | 97.3454 | 95:35 | 95:35 | 97.7744 | 96.7355
17 | F.C.S.M | 2 | 2 | 9:20 | 52:25 | 14:55 | 2:55 | 17:50 | 77:20 | 27:10 | 13:35 | 98.8015 | 98.1743 | 129:45 | 64:52 | 98.6794 | 97.7843
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 7:25 | 1:31 | 8:56 | 44:43 | 8:56 | 8:56 | 98.7993 | 98.7993 | 44:43 | 44:43 | 98.4728 | 98.4728
19 | Hole-Alur | 1 | 1 | 17:20 | 57:00 | 5:45 | 0:45 | 6:30 | 54:10 | 23:50 | 23:50 | 99.1263 | 96.7966 | 111:10 | 111:10 | 98.15 | 96.2033
20 | Savanur | 3 | 3 | 0:00 | 4:10 | 129:00 | 26:25 | 155:25 | 274:05 | 155:25 | 51:48 | 93.0369 | 93.0369 | 278:15 | 92:45 | 96.8797 | 96.8323
21 | Shiggaon | 2 | 2 | 0:00 | 14:20 | 18:00 | 60:15 | 78:15 | 291:50 | 78:15 | 39:08 | 94.7413 | 94.7413 | 306:10 | 153:05 | 95.0165 | 94.7717
22 | Bankapur | 1 | 1 | 11:20 | 32:30 | 17:40 | 9:40 | 27:20 | 108:40 | 38:40 | 38:40 | 96.3262 | 94.8029 | 141:10 | 141:10 | 96.2887 | 95.1787
23 | Hangal | 2 | 2 | 0:50 | 55:30 | 27:10 | 17:30 | 44:40 | 281:00 | 45:30 | 22:45 | 96.9982 | 96.9422 | 336:30 | 168:15 | 95.2015 | 94.2538
24 | Ranebennur | 16 | 16 | 1:30 | 56:26 | 98:49 | 53:01 | 151:50 | 828:23 | 153:20 | 9:35 | 98.7245 | 98.7119 | 884:49 | 55:18 | 98.2318 | 98.1113
25 | Halageri | 2 | 2 | 36:00 | 155:05 | 49:40 | 6:50 | 56:30 | 333:10 | 92:30 | 46:15 | 96.203 | 93.7836 | 488:15 | 244:08 | 94.3107 | 91.6624
26 | Tuminakatti | 2 | 2 | 0:00 | 2:20 | 17:55 | 1:55 | 19:50 | 121:00 | 19:50 | 9:55 | 98.6671 | 98.6671 | 123:20 | 61:40 | 97.9337 | 97.8939
27 | Kahanderayanahalli | 1 | 1 | 0:55 | 3:47 | 10:00 | 58:35 | 68:35 | 304:00 | 69:30 | 69:30 | 90.7818 | 90.6586 | 307:47 | 307:47 | 89.6175 | 89.4883
28 | Rattihalli | 1 | 1 | 0:00 | 3:10 | 23:55 | 7:00 | 30:55 | 105:35 | 30:55 | 30:55 | 95.8445 | 95.8445 | 108:45 | 108:45 | 96.394 | 96.2859
29 | Hirekerur | 2 | 2 | 0:45 | 38:15 | 43:00 | 67:10 | 110:10 | 238:50 | 110:55 | 55:28 | 92.5963 | 92.5459 | 277:05 | 138:32 | 95.9216 | 95.2684
30 | Byadagi | 8 | 8 | 19:15 | 119:15 | 74:50 | 100:10 | 175:00 | 1190:50 | 194:15 | 24:17 | 97.0598 | 96.7364 | 1310:05 | 163:46 | 94.9162 | 94.4071
31 | Sirsi | 5 | 5 | 36:55 | 55:55 | 22:09 | 18:04 | 40:13 | 216:33 | 77:08 | 15:26 | 98.9189 | 97.9265 | 272:28 | 54:30 | 98.5208 | 98.1389
32 | Yellapur | 3 | 3 | 18:30 | 144:33 | 4:35 | 13:35 | 18:10 | 98:35 | 36:40 | 12:13 | 99.1861 | 98.3572 | 243:08 | 81:03 | 98.8777 | 97.2321
33 | Mundagod | 3 | 3 | 1:30 | 6:48 | 24:00 | 48:00 | 72:00 | 312:53 | 73:30 | 24:30 | 96.7742 | 96.707 | 319:41 | 106:34 | 96.438 | 96.3606
34 | Siddapur | 2 | 2 | 29:46 | 42:06 | 15:55 | 37:40 | 53:35 | 139:50 | 83:21 | 41:40 | 96.399 | 94.3985 | 181:56 | 90:58 | 97.6121 | 96.8932
35 | Dandeli | 8 | 8 | 10:32 | 69:56 | 106:22 | 144:48 | 251:10 | 711:07 | 261:42 | 32:43 | 95.7801 | 95.6032 | 781:03 | 97:38 | 96.9642 | 96.6656
36 | Haliyal | 3 | 3 | 2:58 | 9:14 | 34:37 | 25:03 | 59:40 | 208:09 | 62:38 | 20:53 | 97.3268 | 97.1938 | 217:23 | 72:28 | 97.6304 | 97.5252
37 | Ankola | 3 | 3 | 23:32 | 119:42 | 23:41 | 26:56 | 50:37 | 140:05 | 74:09 | 24:43 | 97.7322 | 96.6779 | 259:47 | 86:36 | 98.4052 | 97.0425
38 | Kumta | 3 | 3 | 0:09 | 9:48 | 21:13 | 17:34 | 38:47 | 155:49 | 38:56 | 12:59 | 98.2624 | 98.2557 | 165:37 | 55:12 | 98.2261 | 98.1146
39 | Gokarna | 1 | 1 | 15:40 | 56:26 | 4:40 | 2:30 | 7:10 | 46:15 | 22:50 | 22:50 | 99.0367 | 96.931 | 102:41 | 102:41 | 98.4204 | 96.4931
40 | Kasarkod | 1 | 1 | 47:32 | 146:29 | 3:37 | 3:35 | 7:12 | 90:27 | 54:44 | 54:44 | 99.0323 | 92.6434 | 236:56 | 236:56 | 96.9109 | 91.908
41 | Honnavar | 3 | 3 | 0:09 | 29:27 | 30:23 | 92:48 | 123:11 | 301:48 | 123:20 | 41:07 | 94.481 | 94.4743 | 331:15 | 110:25 | 96.5642 | 96.2289
42 | Murdeshwar | 4 | 4 | 5:56 | 63:24 | 25:48 | 28:58 | 54:46 | 473:17 | 60:42 | 15:10 | 98.1597 | 97.9603 | 536:41 | 134:10 | 95.959 | 95.4177
43 | Bhatkal | 3 | 3 | 21:02 | 136:59 | 24:08 | 11:35 | 35:43 | 185:35 | 56:45 | 18:55 | 98.3998 | 97.4574 | 322:34 | 107:31 | 97.8873 | 96.3278
44 | Khanapur | 2 | 2 | 11:30 | 37:00 | 56:15 | 7:45 | 64:00 | 187:30 | 75:30 | 37:45 | 95.6989 | 94.9261 | 224:30 | 112:15 | 96.7982 | 96.1663
45 | Bailhongal | 3 | 3 | 8:36 | 56:31 | 91:40 | 42:35 | 134:15 | 591:05 | 142:51 | 47:37 | 93.9852 | 93.5999 | 647:36 | 215:52 | 93.2709 | 92.6275
46 | Soundatti | 3 | 3 | 2:23 | 20:28 | 23:22 | 15:05 | 38:27 | 307:08 | 40:50 | 13:37 | 98.2773 | 98.1705 | 327:36 | 109:12 | 96.5035 | 96.2705
47 | Ramdurg | 2 | 2 | 1:58 | 15:58 | 26:18 | 7:28 | 33:46 | 149:51 | 35:44 | 17:52 | 97.7307 | 97.5986 | 165:49 | 82:54 | 97.4411 | 97.1684
48 | Gokak | 10 | 10 | 10:53 | 29:58 | 30:26 | 102:23 | 132:49 | 271:03 | 143:42 | 14:22 | 98.2148 | 98.0685 | 301:01 | 30:06 | 99.0743 | 98.9719
49 | Mudalagi | 2 | 2 | 2:15 | 7:45 | 29:40 | 22:00 | 51:40 | 147:25 | 53:55 | 26:58 | 96.5278 | 96.3766 | 155:10 | 77:35 | 97.4826 | 97.3503
50 | Konnur | 1 | 1 | 0:40 | 0:55 | 17:05 | 2:50 | 19:55 | 119:25 | 20:35 | 20:35 | 97.323 | 97.2334 | 120:20 | 120:20 | 95.9216 | 95.8903
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 19:00 | 15:41 | 34:41 | 133:51 | 34:41 | 34:41 | 95.3383 | 95.3383 | 133:51 | 133:51 | 95.4286 | 95.4286
52 | Kudachi | 1 | 1 | 1:00 | 2:10 | 38:00 | 11:00 | 49:00 | 180:10 | 50:00 | 50:00 | 93.414 | 93.2796 | 182:20 | 182:20 | 93.8468 | 93.7728
53 | Athani | 6 | 6 | 47:18 | 142:10 | 30:39 | 57:21 | 88:00 | 525:08 | 135:18 | 22:33 | 98.0287 | 96.9691 | 667:18 | 111:13 | 97.0109 | 96.2016
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 6:40 | 10:35 | 17:15 | 110:10 | 17:15 | 8:38 | 98.8407 | 98.8407 | 110:10 | 55:05 | 98.1187 | 98.1187
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 65:00 | 46:18 | 111:18 | 441:58 | 111:18 | 22:16 | 97.0081 | 97.0081 | 441:58 | 88:24 | 96.9811 | 96.9811
56 | Sadalaga | 1 | 1 | 0:00 | 0:10 | 29:40 | 12:00 | 41:40 | 96:55 | 41:40 | 41:40 | 94.3996 | 94.3996 | 97:05 | 97:05 | 96.69 | 96.6843
57 | Muddebihal | 2 | 2 | 16:30 | 64:20 | 45:55 | 16:35 | 62:30 | 321:25 | 79:00 | 39:30 | 95.7997 | 94.6909 | 385:45 | 192:52 | 94.5113 | 93.4127
58 | Talikoti | 1 | 1 | 2:45 | 16:50 | 7:05 | 7:15 | 14:20 | 69:35 | 17:05 | 17:05 | 98.0735 | 97.7039 | 86:25 | 86:25 | 97.6235 | 97.0486
59 | B.Bagewadi | 1 | 1 | 6:13 | 14:10 | 1:30 | 0:00 | 1:30 | 35:17 | 7:43 | 7:43 | 99.7984 | 98.9628 | 49:27 | 49:27 | 98.795 | 98.3111
60 | Indi | 3 | 3 | 2:50 | 8:23 | 7:30 | 7:20 | 14:50 | 80:59 | 17:40 | 5:53 | 99.3354 | 99.2085 | 89:22 | 29:47 | 99.0781 | 98.9826
61 | Sindagi | 2 | 2 | 19:00 | 59:00 | 32:25 | 9:20 | 41:45 | 150:20 | 60:45 | 30:22 | 97.1942 | 95.9173 | 209:20 | 104:40 | 97.4328 | 96.4253
62 | Guledgudda | 1 | 1 | 2:41 | 7:35 | 12:14 | 5:15 | 17:29 | 108:46 | 20:10 | 20:10 | 97.6501 | 97.2894 | 116:21 | 116:21 | 96.2853 | 96.0263
63 | Ilkal | 8 | 8 | 21:45 | 165:47 | 134:36 | 126:19 | 260:55 | 1394:53 | 282:40 | 35:20 | 95.6163 | 95.2509 | 1560:40 | 195:05 | 94.0451 | 93.3373
64 | Kerur | 2 | 2 | 6:05 | 18:30 | 7:53 | 2:34 | 10:27 | 109:17 | 16:32 | 8:16 | 99.2977 | 98.8889 | 127:47 | 63:54 | 98.1338 | 97.8179
65 | Hungund | 4 | 4 | 8:12 | 80:12 | 65:13 | 39:35 | 104:48 | 416:49 | 113:00 | 28:15 | 96.4785 | 96.203 | 497:01 | 124:15 | 96.4411 | 95.7563
66 | Gaddankeri | 3 | 3 | 10:42 | 35:52 | 44:38 | 20:40 | 65:18 | 299:47 | 76:00 | 25:20 | 97.0744 | 96.595 | 335:39 | 111:53 | 96.5872 | 96.1788
67 | Rampur | 1 | 1 | 4:09 | 10:09 | 15:06 | 2:39 | 17:45 | 73:06 | 21:54 | 21:54 | 97.6142 | 97.0565 | 83:15 | 83:15 | 97.5034 | 97.1568
68 | Kaladagi | 2 | 2 | 6:45 | 12:27 | 20:42 | 8:51 | 29:33 | 181:06 | 36:18 | 18:09 | 98.0141 | 97.5605 | 193:33 | 96:46 | 96.9074 | 96.6948
69 | Achanur | 1 | 1 | 5:06 | 8:30 | 30:12 | 38:30 | 68:42 | 174:12 | 73:48 | 73:48 | 90.7661 | 90.0806 | 182:42 | 182:42 | 94.0505 | 93.7602
70 | Shirur | 1 | 1 | 11:27 | 34:41 | 0:00 | 21:06 | 21:06 | 123:13 | 32:33 | 32:33 | 97.164 | 95.625 | 157:54 | 157:54 | 95.7918 | 94.6072
71 | Badami | 1 | 1 | 3:30 | 15:55 | 14:43 | 5:11 | 19:54 | 106:00 | 23:24 | 23:24 | 97.3253 | 96.8548 | 121:55 | 121:55 | 96.3798 | 95.8362
72 | Kulageri | 1 | 1 | 1:50 | 10:41 | 4:20 | 2:55 | 7:15 | 32:30 | 9:05 | 9:05 | 99.0255 | 98.7791 | 43:11 | 43:11 | 98.89 | 98.5252
73 | Jamkhandi | 7 | 7 | 32:45 | 82:15 | 102:05 | 37:00 | 139:05 | 416:45 | 171:50 | 24:33 | 97.3294 | 96.7006 | 499:00 | 71:17 | 97.9667 | 97.5654
74 | Mahalingapur | 3 | 3 | 2:56 | 5:34 | 36:21 | 14:29 | 50:50 | 236:44 | 53:46 | 17:55 | 97.7225 | 97.5911 | 242:18 | 80:46 | 97.3049 | 97.2416
75 | Rabakavi | 2 | 2 | 2:40 | 16:45 | 9:45 | 7:15 | 17:00 | 75:40 | 19:40 | 9:50 | 98.8575 | 98.6783 | 92:25 | 46:12 | 98.7079 | 98.4218
76 | Banahatti | 2 | 2 | 4:10 | 10:20 | 30:30 | 2:20 | 32:50 | 104:05 | 37:00 | 18:30 | 97.7935 | 97.5134 | 114:25 | 57:13 | 98.2226 | 98.0462
77 | Terdal | 2 | 2 | 0:00 | 1:10 | 32:55 | 7:35 | 40:30 | 135:30 | 40:30 | 20:15 | 97.2782 | 97.2782 | 136:40 | 68:20 | 97.6861 | 97.6662
78 | Mudhol | 4 | 4 | 4:38 | 21:45 | 62:45 | 32:41 | 95:26 | 273:05 | 100:04 | 25:01 | 96.7932 | 96.6375 | 294:50 | 73:42 | 97.6683 | 97.4826
79 | Bilagi | 1 | 1 | 5:10 | 18:23 | 11:40 | 4:00 | 15:40 | 56:30 | 20:50 | 20:50 | 97.8943 | 97.1998 | 74:53 | 74:53 | 98.0704 | 97.4425
80 | Lokapur | 2 | 2 | 3:25 | 9:45 | 50:25 | 17:10 | 67:35 | 286:30 | 71:00 | 35:30 | 95.4581 | 95.2285 | 296:15 | 148:08 | 95.1076 | 94.9411
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of August-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of August-2021 |  |  |  | Reliability for cumulative period from Apr-21 to August-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 78 | 78 | 58:23 | 89:45 | 217:10 | 238:36 | 455:46 | 2918:03 | 514:09 | 6:35 | 99.2146 | 99.114 | 3007:48 | 38:34 | 98.9812 | 98.9498
2 | Dharwad(R) | 19 | 19 | 34:00 | 185:35 | 218:21 | 94:11 | 312:32 | 2449:48 | 346:32 | 18:14 | 97.7891 | 97.5486 | 2635:23 | 138:42 | 96.4886 | 96.2226
3 | Kundagol | 1 | 1 | 5:15 | 99:00 | 5:30 | 19:40 | 25:10 | 84:00 | 30:25 | 30:25 | 96.6174 | 95.9117 | 183:00 | 183:00 | 97.7124 | 95.0163
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 7:41 | 3:49 | 11:30 | 65:01 | 11:30 | 11:30 | 98.4543 | 98.4543 | 65:01 | 65:01 | 98.2294 | 98.2294
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 13:00 | 4:10 | 17:10 | 80:24 | 17:10 | 17:10 | 97.6927 | 97.6927 | 80:24 | 80:24 | 97.8105 | 97.8105
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 10:55 | 9:15 | 20:10 | 356:35 | 20:10 | 10:05 | 98.6447 | 98.6447 | 356:35 | 178:18 | 95.1446 | 95.1446
7 | Alnavar | 1 | 1 | 0:00 | 6:10 | 21:20 | 9:00 | 30:20 | 117:35 | 30:20 | 30:20 | 95.9229 | 95.9229 | 123:45 | 123:45 | 96.7978 | 96.6299
8 | Naragund | 2 | 2 | 2:40 | 38:20 | 10:35 | 7:45 | 18:20 | 231:05 | 21:00 | 10:30 | 98.7679 | 98.5887 | 269:25 | 134:42 | 96.8534 | 96.3315
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 16:20 | 28:10 | 44:30 | 334:40 | 44:30 | 11:08 | 98.5047 | 98.5047 | 334:40 | 83:40 | 97.7215 | 97.7215
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 40:54 | 19:39 | 60:33 | 453:13 | 60:33 | 15:08 | 97.9654 | 97.9654 | 453:13 | 113:18 | 96.9144 | 96.9144
11 | Naregal | 1 | 1 | 0:00 | 10:55 | 0:35 | 1:00 | 1:35 | 53:15 | 1:35 | 1:35 | 99.7872 | 99.7872 | 64:10 | 64:10 | 98.5498 | 98.2525
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 12:35 | 4:21 | 16:56 | 208:41 | 16:56 | 8:28 | 98.862 | 98.862 | 208:41 | 104:20 | 97.1585 | 97.1585
13 | Ron | 3 | 3 | 0:00 | 14:15 | 29:20 | 7:00 | 36:20 | 346:52 | 36:20 | 12:07 | 98.3722 | 98.3722 | 361:07 | 120:22 | 96.8512 | 96.7219
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 28:05 | 36:45 | 64:50 | 202:15 | 64:50 | 21:37 | 97.0953 | 97.0953 | 202:15 | 67:25 | 98.164 | 98.164
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 13:52 | 4:32 | 18:24 | 191:04 | 18:24 | 18:24 | 97.5269 | 97.5269 | 191:04 | 191:04 | 94.7967 | 94.7967
16 | G.C.T.M | 1 | 1 | 4:40 | 35:05 | 8:40 | 2:55 | 11:35 | 76:45 | 16:15 | 16:15 | 98.4431 | 97.8159 | 111:50 | 111:50 | 97.9099 | 96.9544
17 | F.C.S.M | 2 | 2 | 8:50 | 61:15 | 6:20 | 3:40 | 10:00 | 87:20 | 18:50 | 9:25 | 99.328 | 98.7343 | 148:35 | 74:18 | 98.8108 | 97.9768
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 2:55 | 4:07 | 7:02 | 51:45 | 7:02 | 7:02 | 99.0547 | 99.0547 | 51:45 | 51:45 | 98.5907 | 98.5907
19 | Hole-Alur | 1 | 1 | 4:55 | 61:55 | 5:55 | 0:20 | 6:15 | 60:25 | 11:10 | 11:10 | 99.1599 | 98.4991 | 122:20 | 122:20 | 98.3547 | 96.6685
20 | Savanur | 3 | 3 | 3:10 | 7:20 | 11:25 | 5:25 | 16:50 | 290:55 | 20:00 | 6:40 | 99.2458 | 99.1039 | 298:15 | 99:25 | 97.3591 | 97.2926
21 | Shiggaon | 2 | 2 | 3:20 | 17:40 | 17:10 | 26:50 | 44:00 | 335:50 | 47:20 | 23:40 | 97.043 | 96.819 | 353:30 | 176:45 | 95.4271 | 95.1865
22 | Bankapur | 1 | 1 | 10:10 | 42:40 | 17:55 | 3:45 | 21:40 | 130:20 | 31:50 | 31:50 | 97.0878 | 95.7213 | 173:00 | 173:00 | 96.4506 | 95.2887
23 | Hangal | 2 | 2 | 0:35 | 56:05 | 15:30 | 19:35 | 35:05 | 316:05 | 35:40 | 17:50 | 97.6422 | 97.603 | 372:10 | 186:05 | 95.696 | 94.9324
24 | Ranebennur | 16 | 16 | 19:50 | 76:16 | 127:51 | 43:32 | 171:23 | 999:46 | 191:13 | 11:57 | 98.5603 | 98.3937 | 1076:02 | 67:15 | 98.2983 | 98.1685
25 | Halageri | 2 | 2 | 13:10 | 168:15 | 32:15 | 0:40 | 32:55 | 366:05 | 46:05 | 23:02 | 97.7879 | 96.903 | 534:20 | 267:10 | 95.0152 | 92.7242
26 | Tuminakatti | 2 | 2 | 1:45 | 4:05 | 8:20 | 0:55 | 9:15 | 130:15 | 11:00 | 5:30 | 99.3784 | 99.2608 | 134:20 | 67:10 | 98.2264 | 98.1708
27 | Kahanderayanahalli | 1 | 1 | 1:40 | 5:27 | 8:30 | 1:15 | 9:45 | 313:45 | 11:25 | 11:25 | 98.6895 | 98.4655 | 319:12 | 319:12 | 91.4556 | 91.3072
28 | Rattihalli | 1 | 1 | 0:40 | 3:50 | 14:30 | 4:00 | 18:30 | 124:05 | 19:10 | 19:10 | 97.5134 | 97.4238 | 127:55 | 127:55 | 96.6208 | 96.5164
29 | Hirekerur | 2 | 2 | 5:30 | 43:45 | 31:00 | 5:50 | 36:50 | 275:40 | 42:20 | 21:10 | 97.5246 | 97.155 | 319:25 | 159:42 | 96.2464 | 95.6506
30 | Byadagi | 8 | 8 | 20:30 | 139:45 | 39:40 | 24:30 | 64:10 | 1255:00 | 84:40 | 10:35 | 98.9219 | 98.5775 | 1394:45 | 174:21 | 95.7278 | 95.2521
31 | Sirsi | 5 | 5 | 3:45 | 59:40 | 49:22 | 9:37 | 58:59 | 275:32 | 62:44 | 12:33 | 98.4144 | 98.3136 | 335:12 | 67:02 | 98.4993 | 98.1743
32 | Yellapur | 3 | 3 | 23:40 | 168:13 | 13:30 | 3:10 | 16:40 | 115:15 | 40:20 | 13:27 | 99.2533 | 98.193 | 283:28 | 94:29 | 98.9538 | 97.4268
33 | Mundagod | 3 | 3 | 10:30 | 17:18 | 68:18 | 9:50 | 78:08 | 391:01 | 88:38 | 29:33 | 96.4994 | 96.029 | 408:19 | 136:06 | 96.4505 | 96.2934
34 | Siddapur | 2 | 2 | 0:10 | 42:16 | 5:55 | 7:55 | 13:50 | 153:40 | 14:00 | 7:00 | 99.0703 | 99.0591 | 195:56 | 97:58 | 97.9076 | 97.3321
35 | Dandeli | 8 | 8 | 12:52 | 82:48 | 63:44 | 52:57 | 116:41 | 827:48 | 129:33 | 16:12 | 98.0396 | 97.8234 | 910:36 | 113:50 | 97.1821 | 96.9002
36 | Haliyal | 3 | 3 | 4:15 | 13:29 | 25:35 | 18:06 | 43:41 | 251:50 | 47:56 | 15:59 | 98.0429 | 97.8524 | 265:19 | 88:26 | 97.7139 | 97.5915
37 | Ankola | 3 | 3 | 14:55 | 134:37 | 30:48 | 38:12 | 69:00 | 209:05 | 83:55 | 27:58 | 96.9086 | 96.2403 | 343:42 | 114:34 | 98.102 | 96.88
38 | Kumta | 3 | 3 | 3:45 | 13:33 | 12:04 | 12:48 | 24:52 | 180:41 | 28:37 | 9:32 | 98.8859 | 98.7179 | 194:14 | 64:45 | 98.3598 | 98.2368
39 | Gokarna | 1 | 1 | 4:36 | 61:02 | 5:00 | 3:15 | 8:15 | 54:30 | 12:51 | 12:51 | 98.8911 | 98.2728 | 115:32 | 115:32 | 98.5158 | 96.8537
40 | Kasarkod | 1 | 1 | 13:57 | 160:26 | 6:13 | 9:57 | 16:10 | 106:37 | 30:07 | 30:07 | 97.8271 | 95.9521 | 267:03 | 267:03 | 97.0965 | 92.7274
41 | Honnavar | 3 | 3 | 3:51 | 33:18 | 18:09 | 10:52 | 29:01 | 330:49 | 32:52 | 10:57 | 98.7 | 98.5275 | 364:07 | 121:22 | 96.9969 | 96.6947
42 | Murdeshwar | 4 | 4 | 5:52 | 69:16 | 37:31 | 19:15 | 56:46 | 530:03 | 62:38 | 15:39 | 98.0925 | 97.8954 | 599:19 | 149:50 | 96.3913 | 95.9197
43 | Bhatkal | 3 | 3 | 25:48 | 162:47 | 25:16 | 4:57 | 30:13 | 215:48 | 56:01 | 18:40 | 98.6462 | 97.4903 | 378:35 | 126:12 | 98.041 | 96.5633
44 | Khanapur | 2 | 2 | 1:30 | 38:30 | 10:35 | 4:45 | 15:20 | 202:50 | 16:50 | 8:25 | 98.9695 | 98.8687 | 241:20 | 120:40 | 97.2381 | 96.7139
45 | Bailhongal | 3 | 3 | 0:00 | 56:31 | 98:16 | 40:30 | 138:46 | 729:51 | 138:46 | 46:15 | 93.7829 | 93.7829 | 786:22 | 262:07 | 93.3746 | 92.8616
46 | Soundatti | 3 | 3 | 0:00 | 20:28 | 39:34 | 6:16 | 45:50 | 352:58 | 45:50 | 15:17 | 97.9465 | 97.9465 | 373:26 | 124:29 | 96.7959 | 96.6101
47 | Ramdurg | 2 | 2 | 18:20 | 34:18 | 9:53 | 6:55 | 16:48 | 166:39 | 35:08 | 17:34 | 98.871 | 97.6389 | 200:57 | 100:28 | 97.7308 | 97.2638
48 | Gokak | 10 | 10 | 8:11 | 38:09 | 58:11 | 16:36 | 74:47 | 345:50 | 82:58 | 8:18 | 98.9948 | 98.8849 | 383:59 | 38:24 | 99.0582 | 98.9543
49 | Mudalagi | 2 | 2 | 12:10 | 19:55 | 25:45 | 7:20 | 33:05 | 180:30 | 45:15 | 22:38 | 97.7767 | 96.959 | 200:25 | 100:12 | 97.5422 | 97.271
50 | Konnur | 1 | 1 | 0:00 | 0:55 | 9:00 | 1:10 | 10:10 | 129:35 | 10:10 | 10:10 | 98.6335 | 98.6335 | 130:30 | 130:30 | 96.471 | 96.4461
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 19:30 | 17:58 | 37:28 | 171:19 | 37:28 | 37:28 | 94.9642 | 94.9642 | 171:19 | 171:19 | 95.3345 | 95.3345
52 | Kudachi | 1 | 1 | 0:05 | 2:15 | 47:50 | 6:10 | 54:00 | 234:10 | 54:05 | 54:05 | 92.7419 | 92.7307 | 236:25 | 236:25 | 93.6229 | 93.5616
53 | Athani | 7 | 7 | 9:22 | 151:32 | 42:05 | 36:14 | 78:19 | 603:27 | 87:41 | 12:32 | 98.4962 | 98.3164 | 754:59 | 107:51 | 97.6523 | 97.0628
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 6:10 | 6:35 | 12:45 | 122:55 | 12:45 | 6:22 | 99.1431 | 99.1431 | 122:55 | 61:28 | 98.3263 | 98.3263
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 29:35 | 17:00 | 46:35 | 488:33 | 46:35 | 9:19 | 98.7478 | 98.7478 | 488:33 | 97:43 | 97.3391 | 97.3391
56 | Sadalaga | 1 | 1 | 6:25 | 6:35 | 22:20 | 5:10 | 27:30 | 124:25 | 33:55 | 33:55 | 96.3038 | 95.4413 | 131:00 | 131:00 | 96.6117 | 96.4325
57 | Muddebihal | 2 | 2 | 2:10 | 66:30 | 31:25 | 9:00 | 40:25 | 361:50 | 42:35 | 21:18 | 97.2838 | 97.1382 | 428:20 | 214:10 | 95.0731 | 94.1676
58 | Talikoti | 1 | 1 | 2:05 | 18:55 | 11:30 | 7:00 | 18:30 | 88:05 | 20:35 | 20:35 | 97.5134 | 97.2334 | 107:00 | 107:00 | 97.6012 | 97.0861
59 | B.Bagewadi | 1 | 1 | 2:15 | 16:25 | 6:12 | 5:42 | 11:54 | 47:11 | 14:09 | 14:09 | 98.4005 | 98.0981 | 63:36 | 63:36 | 98.7151 | 98.268
60 | Indi | 3 | 3 | 0:00 | 8:23 | 33:19 | 3:31 | 36:50 | 117:49 | 36:50 | 12:17 | 98.3498 | 98.3498 | 126:12 | 42:04 | 98.9305 | 98.8544
61 | Sindagi | 2 | 2 | 1:20 | 60:20 | 34:35 | 4:30 | 39:05 | 189:25 | 40:25 | 20:12 | 97.3734 | 97.2838 | 249:45 | 124:52 | 97.4208 | 96.5993
62 | Guledgudda | 1 | 1 | 0:00 | 7:35 | 12:05 | 8:25 | 20:30 | 129:16 | 20:30 | 20:30 | 97.2446 | 97.2446 | 136:51 | 136:51 | 96.4797 | 96.2731
63 | Ilkal | 8 | 8 | 3:40 | 169:27 | 76:39 | 77:33 | 154:12 | 1549:05 | 157:52 | 19:44 | 97.4093 | 97.3477 | 1718:32 | 214:49 | 94.7267 | 94.1499
64 | Kerur | 2 | 2 | 7:25 | 25:55 | 9:13 | 9:28 | 18:41 | 127:58 | 26:06 | 13:03 | 98.7444 | 98.246 | 153:53 | 76:57 | 98.2575 | 97.9046
65 | Hungund | 4 | 4 | 0:00 | 80:12 | 67:47 | 35:18 | 103:05 | 519:54 | 103:05 | 25:46 | 96.5362 | 96.5362 | 600:06 | 150:02 | 96.4604 | 95.9144
66 | Gaddankeri | 3 | 3 | 3:00 | 38:52 | 35:30 | 31:36 | 67:06 | 366:53 | 70:06 | 23:22 | 96.9937 | 96.8593 | 405:45 | 135:15 | 96.6695 | 96.3167
67 | Rampur | 1 | 1 | 2:32 | 12:41 | 8:27 | 5:45 | 14:12 | 87:18 | 16:44 | 16:44 | 98.0914 | 97.7509 | 99:59 | 99:59 | 97.6225 | 97.2771
68 | Kaladagi | 2 | 2 | 10:54 | 23:21 | 5:51 | 25:03 | 30:54 | 212:00 | 41:48 | 20:54 | 97.9234 | 97.1909 | 235:21 | 117:40 | 97.1133 | 96.7953
69 | Achanur | 1 | 1 | 1:12 | 9:42 | 18:21 | 36:52 | 55:13 | 229:25 | 56:25 | 56:25 | 92.5784 | 92.4171 | 239:07 | 239:07 | 93.7523 | 93.4881
70 | Shirur | 1 | 1 | 3:24 | 38:05 | 0:27 | 21:45 | 22:12 | 145:25 | 25:36 | 25:36 | 97.0161 | 96.5591 | 183:30 | 183:30 | 96.0399 | 95.0027
71 | Badami | 1 | 1 | 0:33 | 16:28 | 14:05 | 8:22 | 22:27 | 128:27 | 23:00 | 23:00 | 96.9825 | 96.9086 | 144:55 | 144:55 | 96.5019 | 96.0535
72 | Kulageri | 1 | 1 | 1:28 | 12:09 | 3:30 | 0:55 | 4:25 | 36:55 | 5:53 | 5:53 | 99.4064 | 99.2092 | 49:04 | 49:04 | 98.9946 | 98.6638
73 | Jamkhandi | 7 | 7 | 5:15 | 87:30 | 42:15 | 12:00 | 54:15 | 471:00 | 59:30 | 8:30 | 98.9583 | 98.8575 | 558:30 | 79:47 | 98.1676 | 97.8272
74 | Mahalingapur | 3 | 3 | 0:00 | 5:34 | 36:54 | 8:02 | 44:56 | 281:40 | 44:56 | 14:59 | 97.9869 | 97.9869 | 287:14 | 95:45 | 97.4431 | 97.3926
75 | Rabakavi | 2 | 2 | 4:20 | 21:05 | 23:45 | 15:10 | 38:55 | 114:35 | 43:15 | 21:38 | 97.3846 | 97.0934 | 135:40 | 67:50 | 98.4398 | 98.1527
76 | Banahatti | 2 | 2 | 0:30 | 10:50 | 17:15 | 3:35 | 20:50 | 124:55 | 21:20 | 10:40 | 98.5999 | 98.5663 | 135:45 | 67:53 | 98.2991 | 98.1516
77 | Terdal | 2 | 2 | 2:35 | 3:45 | 33:10 | 4:35 | 37:45 | 173:15 | 40:20 | 20:10 | 97.463 | 97.2894 | 177:00 | 88:30 | 97.6409 | 97.5899
78 | Mudhol | 4 | 4 | 7:35 | 29:20 | 41:49 | 15:44 | 57:33 | 330:38 | 65:08 | 16:17 | 98.0662 | 97.8114 | 359:58 | 90:00 | 97.749 | 97.5492
79 | Bilagi | 1 | 1 | 0:15 | 18:38 | 22:03 | 4:55 | 26:58 | 83:28 | 27:13 | 27:13 | 96.3754 | 96.3418 | 102:06 | 102:06 | 97.7269 | 97.2195
80 | Lokapur | 2 | 2 | 0:45 | 10:30 | 33:00 | 4:45 | 37:45 | 324:15 | 38:30 | 19:15 | 97.463 | 97.4126 | 334:45 | 167:22 | 95.5848 | 95.4419
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of September-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of September-2021 |  |  |  | Reliability for cumulative period from Apr-21 to September-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 62:48 | 152:33 | 205:09 | 183:12 | 388:21 | 3306:24 | 451:09 | 5:43 | 99.3172 | 99.2068 | 3458:57 | 43:47 | 99.0471 | 99.0031
2 | Dharwad(R) | 19 | 19 | 136:10 | 321:45 | 183:44 | 94:44 | 278:28 | 2728:16 | 414:38 | 21:49 | 97.9644 | 96.9691 | 3050:01 | 160:32 | 96.7306 | 96.345
3 | Kundagol | 1 | 1 | 2:35 | 101:35 | 2:05 | 2:20 | 4:25 | 88:25 | 7:00 | 7:00 | 99.3866 | 99.0278 | 190:00 | 190:00 | 97.9869 | 95.674
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 5:04 | 3:31 | 8:35 | 73:36 | 8:35 | 8:35 | 98.8079 | 98.8079 | 73:36 | 73:36 | 98.3242 | 98.3242
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 6:10 | 5:25 | 11:35 | 91:59 | 11:35 | 11:35 | 98.3912 | 98.3912 | 91:59 | 91:59 | 97.9057 | 97.9057
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 22:22 | 21:32 | 43:54 | 400:29 | 43:54 | 21:57 | 96.9514 | 96.9514 | 400:29 | 200:14 | 95.4408 | 95.4408
7 | Alnavar | 1 | 1 | 0:00 | 6:10 | 3:35 | 5:20 | 8:55 | 126:30 | 8:55 | 8:55 | 98.7616 | 98.7616 | 132:40 | 132:40 | 97.1198 | 96.9794
8 | Naragund | 2 | 2 | 1:30 | 39:50 | 7:10 | 4:50 | 12:00 | 243:05 | 13:30 | 6:45 | 99.1667 | 99.0625 | 282:55 | 141:28 | 97.2327 | 96.7792
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 27:20 | 122:40 | 150:00 | 484:40 | 150:00 | 37:30 | 94.7917 | 94.7917 | 484:40 | 121:10 | 97.2412 | 97.2412
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 55:44 | 45:30 | 101:14 | 554:27 | 101:14 | 25:19 | 96.485 | 96.485 | 554:27 | 138:37 | 96.844 | 96.844
11 | Naregal | 1 | 1 | 0:00 | 10:55 | 1:10 | 3:40 | 4:50 | 58:05 | 4:50 | 4:50 | 99.3287 | 99.3287 | 69:00 | 69:00 | 98.6775 | 98.429
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 38:50 | 5:25 | 44:15 | 252:56 | 44:15 | 22:08 | 96.9271 | 96.9271 | 252:56 | 126:28 | 97.1205 | 97.1205
13 | Ron | 3 | 3 | 0:00 | 14:15 | 35:05 | 7:35 | 42:40 | 389:32 | 42:40 | 14:13 | 98.0247 | 98.0247 | 403:47 | 134:36 | 97.0436 | 96.9355
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 16:40 | 16:30 | 33:10 | 235:25 | 33:10 | 11:03 | 98.4645 | 98.4645 | 235:25 | 78:28 | 98.2133 | 98.2133
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 35:01 | 4:00 | 39:01 | 230:05 | 39:01 | 39:01 | 94.581 | 94.581 | 230:05 | 230:05 | 94.7613 | 94.7613
16 | G.C.T.M | 1 | 1 | 5:00 | 40:05 | 9:15 | 4:20 | 13:35 | 90:20 | 18:35 | 18:35 | 98.1134 | 97.419 | 130:25 | 130:25 | 97.9432 | 97.0306
17 | F.C.S.M | 2 | 2 | 12:00 | 73:15 | 5:25 | 0:50 | 6:15 | 93:35 | 18:15 | 9:08 | 99.566 | 98.7326 | 166:50 | 83:25 | 98.9346 | 98.1007
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 10:10 | 2:40 | 12:50 | 64:35 | 12:50 | 12:50 | 98.2176 | 98.2176 | 64:35 | 64:35 | 98.5295 | 98.5295
19 | Hole-Alur | 1 | 1 | 0:40 | 62:35 | 13:50 | 0:50 | 14:40 | 75:05 | 15:20 | 15:20 | 97.963 | 97.8704 | 137:40 | 137:40 | 98.2905 | 96.8655
20 | Savanur | 3 | 3 | 0:00 | 7:20 | 58:45 | 8:40 | 67:25 | 358:20 | 67:25 | 22:28 | 96.8789 | 96.8789 | 365:40 | 121:53 | 97.2804 | 97.2248
21 | Shiggaon | 2 | 2 | 1:40 | 19:20 | 26:35 | 11:00 | 37:35 | 373:25 | 39:15 | 19:38 | 97.39 | 97.2743 | 392:45 | 196:22 | 95.7489 | 95.5288
22 | Bankapur | 1 | 1 | 10:50 | 53:30 | 13:10 | 2:10 | 15:20 | 145:40 | 26:10 | 26:10 | 97.8704 | 96.3657 | 199:10 | 199:10 | 96.6834 | 95.4652
23 | Hangal | 2 | 2 | 3:50 | 59:55 | 18:25 | 12:40 | 31:05 | 347:10 | 34:55 | 17:28 | 97.8414 | 97.5752 | 407:05 | 203:33 | 96.0477 | 95.3656
24 | Ranebennur | 16 | 16 | 4:05 | 80:21 | 226:24 | 119:48 | 346:12 | 1345:58 | 350:17 | 21:54 | 96.9948 | 96.9593 | 1426:19 | 89:09 | 98.0846 | 97.9703
25 | Halageri | 2 | 2 | 21:30 | 189:45 | 23:35 | 6:45 | 30:20 | 396:25 | 51:50 | 25:55 | 97.8935 | 96.4005 | 586:10 | 293:05 | 95.4871 | 93.3269
26 | Tuminakatti | 2 | 2 | 0:00 | 4:05 | 92:05 | 0:25 | 92:30 | 222:45 | 92:30 | 46:15 | 93.5764 | 93.5764 | 226:50 | 113:25 | 97.4641 | 97.4177
27 | Kahanderayanahalli | 1 | 1 | 1:08 | 6:35 | 14:05 | 2:30 | 16:35 | 330:20 | 17:43 | 17:43 | 97.6968 | 97.5394 | 336:55 | 336:55 | 92.4787 | 92.3289
28 | Rattihalli | 1 | 1 | 0:15 | 4:05 | 17:55 | 4:20 | 22:15 | 146:20 | 22:30 | 22:30 | 96.9097 | 96.875 | 150:25 | 150:25 | 96.6682 | 96.5752
29 | Hirekerur | 2 | 2 | 10:30 | 54:15 | 26:15 | 4:20 | 30:35 | 306:15 | 41:05 | 20:32 | 97.8762 | 97.147 | 360:30 | 180:15 | 96.5135 | 95.8959
30 | Byadagi | 8 | 8 | 26:20 | 166:05 | 42:25 | 17:10 | 59:35 | 1314:35 | 85:55 | 10:44 | 98.9656 | 98.5084 | 1480:40 | 185:05 | 96.2586 | 95.7859
31 | Sirsi | 5 | 5 | 2:05 | 61:45 | 25:30 | 13:40 | 39:10 | 314:42 | 41:15 | 8:15 | 98.912 | 98.8542 | 376:27 | 75:17 | 98.5669 | 98.2857
32 | Yellapur | 3 | 3 | 2:38 | 170:51 | 6:45 | 5:20 | 12:05 | 127:20 | 14:43 | 4:54 | 99.4406 | 99.3187 | 298:11 | 99:24 | 99.0336 | 97.7369
33 | Mundagod | 3 | 3 | 0:00 | 17:18 | 16:20 | 29:56 | 46:16 | 437:17 | 46:16 | 15:25 | 97.858 | 97.858 | 454:35 | 151:32 | 96.6812 | 96.5499
34 | Siddapur | 2 | 2 | 11:10 | 53:26 | 12:25 | 11:20 | 23:45 | 177:25 | 34:55 | 17:27 | 98.3507 | 97.5752 | 230:51 | 115:25 | 97.9802 | 97.3719
35 | Dandeli | 8 | 8 | 5:52 | 88:40 | 51:44 | 23:29 | 75:13 | 903:01 | 81:05 | 10:08 | 98.6942 | 98.5923 | 991:41 | 123:58 | 97.4299 | 97.1776
36 | Haliyal | 3 | 3 | 4:56 | 18:25 | 16:42 | 16:38 | 33:20 | 285:10 | 38:16 | 12:45 | 98.4568 | 98.2284 | 303:35 | 101:12 | 97.8357 | 97.6959
37 | Ankola | 3 | 3 | 34:01 | 168:38 | 29:20 | 7:38 | 36:58 | 246:03 | 70:59 | 23:40 | 98.2886 | 96.7137 | 414:41 | 138:14 | 98.1326 | 96.8527
38 | Kumta | 3 | 3 | 1:45 | 15:18 | 23:53 | 14:51 | 38:44 | 219:25 | 40:29 | 13:30 | 98.2068 | 98.1258 | 234:43 | 78:14 | 98.3347 | 98.2186
39 | Gokarna | 1 | 1 | 9:20 | 70:22 | 10:00 | 1:15 | 11:15 | 65:45 | 20:35 | 20:35 | 98.4375 | 97.1412 | 136:07 | 136:07 | 98.503 | 96.9008
40 | Kasarkod | 1 | 1 | 12:07 | 172:33 | 9:54 | 5:05 | 14:59 | 121:36 | 27:06 | 27:06 | 97.919 | 96.2361 | 294:09 | 294:09 | 97.2313 | 93.3026
41 | Honnavar | 3 | 3 | 1:51 | 35:09 | 17:48 | 16:41 | 34:29 | 365:18 | 36:20 | 12:07 | 98.4035 | 98.3179 | 400:27 | 133:29 | 97.2275 | 96.9608
42 | Murdeshwar | 4 | 4 | 2:32 | 71:48 | 32:56 | 17:51 | 50:47 | 580:50 | 53:19 | 13:20 | 98.2367 | 98.1487 | 652:38 | 163:09 | 96.6938 | 96.2851
43 | Bhatkal | 3 | 3 | 19:48 | 182:35 | 8:45 | 4:29 | 13:14 | 229:02 | 33:02 | 11:01 | 99.3873 | 98.4707 | 411:37 | 137:12 | 98.2617 | 96.876
44 | Khanapur | 2 | 2 | 4:50 | 43:20 | 19:00 | 11:05 | 30:05 | 232:55 | 34:55 | 17:28 | 97.9109 | 97.5752 | 276:15 | 138:08 | 97.3484 | 96.8551
45 | Bailhongal | 3 | 3 | 1:00 | 57:31 | 52:30 | 21:00 | 73:30 | 803:21 | 74:30 | 24:50 | 96.5972 | 96.5509 | 860:52 | 286:57 | 93.9029 | 93.4664
46 | Soundatti | 3 | 3 | 24:25 | 44:53 | 54:28 | 7:02 | 61:30 | 414:28 | 85:55 | 28:38 | 97.1528 | 96.0224 | 459:21 | 153:07 | 96.8544 | 96.5137
47 | Ramdurg | 2 | 2 | 2:50 | 37:08 | 32:05 | 8:00 | 40:05 | 206:44 | 42:55 | 21:27 | 97.2164 | 97.0197 | 243:52 | 121:56 | 97.6465 | 97.2237
48 | Gokak | 10 | 10 | 10:03 | 48:12 | 79:42 | 59:23 | 139:05 | 484:55 | 149:08 | 14:55 | 98.0683 | 97.9287 | 533:07 | 53:19 | 98.8959 | 98.7862
49 | Mudalagi | 2 | 2 | 2:20 | 22:15 | 17:25 | 7:20 | 24:45 | 205:15 | 27:05 | 13:33 | 98.2812 | 98.1192 | 227:30 | 113:45 | 97.6634 | 97.4101
50 | Konnur | 1 | 1 | 0:10 | 1:05 | 16:50 | 1:25 | 18:15 | 147:50 | 18:25 | 18:25 | 97.4653 | 97.4421 | 148:55 | 148:55 | 96.634 | 96.6094
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 28:11 | 3:55 | 32:06 | 203:25 | 32:06 | 32:06 | 95.5417 | 95.5417 | 203:25 | 203:25 | 95.3685 | 95.3685
52 | Kudachi | 1 | 1 | 1:55 | 4:10 | 56:25 | 6:45 | 63:10 | 297:20 | 65:05 | 65:05 | 91.2269 | 90.9606 | 301:30 | 301:30 | 93.2301 | 93.1352
53 | Athani | 7 | 7 | 9:11 | 160:43 | 28:33 | 71:37 | 100:10 | 703:37 | 109:21 | 15:37 | 98.0126 | 97.8304 | 864:20 | 123:29 | 97.7114 | 97.1886
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 19:50 | 3:40 | 23:30 | 146:25 | 23:30 | 11:45 | 98.3681 | 98.3681 | 146:25 | 73:12 | 98.3331 | 98.3331
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 56:45 | 24:40 | 81:25 | 569:58 | 81:25 | 16:17 | 97.7384 | 97.7384 | 569:58 | 114:00 | 97.4045 | 97.4045
56 | Sadalaga | 1 | 1 | 0:00 | 6:35 | 24:10 | 1:15 | 25:25 | 149:50 | 25:25 | 25:25 | 96.4699 | 96.4699 | 156:25 | 156:25 | 96.5885 | 96.4386
57 | Muddebihal | 2 | 2 | 2:00 | 68:30 | 37:05 | 28:20 | 65:25 | 427:15 | 67:25 | 33:43 | 95.4572 | 95.3183 | 495:45 | 247:53 | 95.136 | 94.3562
58 | Talikoti | 1 | 1 | 2:35 | 21:30 | 23:05 | 8:20 | 31:25 | 119:30 | 34:00 | 34:00 | 95.6366 | 95.2778 | 141:00 | 141:00 | 97.2791 | 96.7896
59 | B.Bagewadi | 1 | 1 | 0:20 | 16:45 | 5:25 | 1:55 | 7:20 | 54:31 | 7:40 | 7:40 | 98.9815 | 98.9352 | 71:16 | 71:16 | 98.7587 | 98.3774
60 | Indi | 3 | 3 | 11:14 | 19:37 | 15:15 | 5:31 | 20:46 | 138:35 | 32:00 | 10:40 | 99.0386 | 98.5185 | 158:12 | 52:44 | 98.9482 | 98.7993
61 | Sindagi | 2 | 2 | 20:20 | 80:40 | 43:25 | 11:55 | 55:20 | 244:45 | 75:40 | 37:50 | 96.1574 | 94.7454 | 325:25 | 162:42 | 97.2137 | 96.2953
62 | Guledgudda | 1 | 1 | 1:33 | 9:08 | 18:38 | 9:21 | 27:59 | 157:15 | 29:32 | 29:32 | 96.1134 | 95.8981 | 166:23 | 166:23 | 96.4196 | 96.2117
63 | Ilkal | 8 | 8 | 12:40 | 182:07 | 94:43 | 100:37 | 195:20 | 1744:25 | 208:00 | 26:00 | 96.6088 | 96.3889 | 1926:32 | 240:49 | 95.0352 | 94.5169
64 | Kerur | 2 | 2 | 12:13 | 38:08 | 15:00 | 6:07 | 21:07 | 149:05 | 33:20 | 16:40 | 98.5336 | 97.6852 | 187:13 | 93:37 | 98.3028 | 97.8687
65 | Hungund | 4 | 4 | 5:40 | 85:52 | 37:23 | 27:02 | 64:25 | 584:19 | 70:05 | 17:31 | 97.7633 | 97.5666 | 670:11 | 167:33 | 96.674 | 96.1852
66 | Gaddankeri | 3 | 3 | 31:32 | 70:24 | 39:50 | 19:12 | 59:02 | 425:55 | 90:34 | 30:11 | 97.267 | 95.8071 | 496:19 | 165:26 | 96.7675 | 96.2332
67 | Rampur | 1 | 1 | 4:21 | 17:02 | 16:03 | 4:06 | 20:09 | 107:27 | 24:30 | 24:30 | 97.2014 | 96.5972 | 124:29 | 124:29 | 97.5535 | 97.1657
68 | Kaladagi | 2 | 2 | 18:12 | 41:33 | 13:18 | 18:15 | 31:33 | 243:33 | 49:45 | 24:52 | 97.809 | 96.5451 | 285:06 | 142:33 | 97.2273 | 96.7543
69 | Achanur | 1 | 1 | 0:00 | 9:42 | 39:09 | 11:39 | 50:48 | 280:13 | 50:48 | 50:48 | 92.9444 | 92.9444 | 289:55 | 289:55 | 93.6198 | 93.399
70 | Shirur | 1 | 1 | 18:21 | 56:26 | 0:00 | 23:30 | 23:30 | 168:55 | 41:51 | 41:51 | 96.7361 | 94.1875 | 225:21 | 225:21 | 96.154 | 94.8691
71 | Badami | 1 | 1 | 9:23 | 25:51 | 15:02 | 11:02 | 26:04 | 154:31 | 35:27 | 35:27 | 96.3796 | 95.0764 | 180:22 | 180:22 | 96.4819 | 95.8933
72 | Kulageri | 1 | 1 | 0:58 | 13:07 | 3:32 | 0:55 | 4:27 | 41:22 | 5:25 | 5:25 | 99.3819 | 99.2477 | 54:29 | 54:29 | 99.0581 | 98.7595
73 | Jamkhandi | 7 | 7 | 16:20 | 103:50 | 79:25 | 17:05 | 96:30 | 567:30 | 112:50 | 16:07 | 98.0853 | 97.7612 | 671:20 | 95:54 | 98.1541 | 97.8164
74 | Mahalingapur | 3 | 3 | 7:01 | 12:35 | 35:35 | 13:14 | 48:49 | 330:29 | 55:50 | 18:37 | 97.74 | 97.4151 | 343:04 | 114:21 | 97.4918 | 97.3963
75 | Rabakavi | 2 | 2 | 9:15 | 30:20 | 7:40 | 3:45 | 11:25 | 126:00 | 20:40 | 10:20 | 99.2072 | 98.5648 | 156:20 | 78:10 | 98.5656 | 98.2202
76 | Banahatti | 2 | 2 | 3:30 | 14:20 | 11:25 | 1:05 | 12:30 | 137:25 | 16:00 | 8:00 | 99.1319 | 98.8889 | 151:45 | 75:53 | 98.4356 | 98.2724
77 | Terdal | 2 | 2 | 0:00 | 3:45 | 34:35 | 4:35 | 39:10 | 212:25 | 39:10 | 19:35 | 97.2801 | 97.2801 | 216:10 | 108:05 | 97.5818 | 97.5391
78 | Mudhol | 4 | 4 | 2:14 | 31:34 | 54:01 | 4:41 | 58:42 | 389:20 | 60:56 | 15:14 | 97.9618 | 97.8843 | 420:54 | 105:13 | 97.7838 | 97.6042
79 | Bilagi | 1 | 1 | 1:55 | 20:33 | 15:35 | 1:50 | 17:25 | 100:53 | 19:20 | 19:20 | 97.581 | 97.3148 | 121:26 | 121:26 | 97.703 | 97.2351
80 | Lokapur | 2 | 2 | 0:00 | 10:30 | 54:10 | 7:30 | 61:40 | 385:55 | 61:40 | 30:50 | 95.7176 | 95.7176 | 396:25 | 198:12 | 95.6066 | 95.4871
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of October-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of October-2021 |  |  |  | Reliability for cumulative period from Apr-21 to October-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 26:52 | 179:25 | 271:21 | 286:06 | 557:27 | 3863:51 | 584:19 | 7:24 | 99.0516 | 99.0059 | 4043:16 | 51:11 | 99.0477 | 99.0035
2 | Dharwad(R) | 16 | 16 | 15:48 | 337:33 | 159:26 | 114:43 | 274:09 | 3002:25 | 289:57 | 18:07 | 97.697 | 97.5643 | 3339:58 | 208:45 | 96.3464 | 95.9356
3 | Kundagol | 1 | 1 | 15:20 | 116:55 | 3:50 | 11:50 | 15:40 | 104:05 | 31:00 | 31:00 | 97.8943 | 95.8333 | 221:00 | 221:00 | 97.9735 | 95.697
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 6:26 | 24:34 | 31:00 | 104:36 | 31:00 | 31:00 | 95.8333 | 95.8333 | 104:36 | 104:36 | 97.9634 | 97.9634
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 8:43 | 22:17 | 31:00 | 122:59 | 31:00 | 31:00 | 95.8333 | 95.8333 | 122:59 | 122:59 | 97.6055 | 97.6055
6 | Kalghatagi | 2 | 2 | 160:00 | 160:00 | 9:05 | 16:40 | 25:45 | 426:14 | 185:45 | 92:52 | 98.2695 | 87.5168 | 586:14 | 293:07 | 95.8505 | 94.2929
7 | Alnavar | 2 | 2 | 0:00 | 6:10 | 43:30 | 13:10 | 56:40 | 183:10 | 56:40 | 28:20 | 96.1918 | 96.1918 | 189:20 | 94:40 | 98.2168 | 98.1568
8 | Naragund | 2 | 2 | 21:10 | 61:00 | 15:05 | 9:40 | 24:45 | 267:50 | 45:55 | 22:58 | 98.3367 | 96.9142 | 328:50 | 164:25 | 97.3926 | 96.7987
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 38:10 | 34:50 | 73:00 | 557:40 | 73:00 | 18:15 | 97.547 | 97.547 | 557:40 | 139:25 | 97.2855 | 97.2855
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 20:27 | 19:41 | 40:08 | 594:35 | 40:08 | 10:02 | 98.6514 | 98.6514 | 594:35 | 148:39 | 97.1058 | 97.1058
11 | Naregal | 1 | 1 | 0:00 | 10:55 | 9:05 | 2:05 | 11:10 | 69:15 | 11:10 | 11:10 | 98.4991 | 98.4991 | 80:10 | 80:10 | 98.6517 | 98.4391
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 18:15 | 8:10 | 26:25 | 279:21 | 26:25 | 13:12 | 98.2247 | 98.2247 | 279:21 | 139:40 | 97.2805 | 97.2805
13 | Ron | 3 | 3 | 0:00 | 14:15 | 8:35 | 13:50 | 22:25 | 411:57 | 22:25 | 7:28 | 98.9957 | 98.9957 | 426:12 | 142:04 | 97.3264 | 97.2339
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 52:45 | 6:55 | 59:40 | 295:05 | 59:40 | 19:53 | 97.3268 | 97.3268 | 295:05 | 98:22 | 98.0849 | 98.0849
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 18:36 | 37:55 | 56:31 | 286:36 | 56:31 | 56:31 | 92.4037 | 92.4037 | 286:36 | 286:36 | 94.4198 | 94.4198
16 | G.C.T.M | 1 | 1 | 2:55 | 43:00 | 12:50 | 5:20 | 18:10 | 108:30 | 21:05 | 21:05 | 97.5582 | 97.1662 | 151:30 | 151:30 | 97.8875 | 97.0502
17 | F.C.S.M | 2 | 2 | 7:50 | 81:05 | 8:05 | 4:40 | 12:45 | 106:20 | 20:35 | 10:18 | 99.1431 | 98.6167 | 187:25 | 93:43 | 98.9648 | 98.1755
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 8:53 | 2:03 | 10:56 | 75:31 | 10:56 | 10:56 | 98.5305 | 98.5305 | 75:31 | 75:31 | 98.5297 | 98.5297
19 | Hole-Alur | 1 | 1 | 12:45 | 75:20 | 6:55 | 1:45 | 8:40 | 83:45 | 21:25 | 21:25 | 98.8351 | 97.1214 | 159:05 | 159:05 | 98.3694 | 96.9026
20 | Savanur | 3 | 3 | 1:25 | 8:45 | 14:00 | 15:40 | 29:40 | 388:00 | 31:05 | 10:22 | 98.6708 | 98.6074 | 396:45 | 132:15 | 97.4818 | 97.425
21 | Shiggaon | 2 | 2 | 1:50 | 21:10 | 18:45 | 37:20 | 56:05 | 429:30 | 57:55 | 28:57 | 96.231 | 96.1078 | 450:40 | 225:20 | 95.8187 | 95.6127
22 | Bankapur | 1 | 1 | 11:10 | 64:40 | 14:10 | 11:05 | 25:15 | 170:55 | 36:25 | 36:25 | 96.6062 | 95.1053 | 235:35 | 235:35 | 96.6722 | 95.4131
23 | Hangal | 2 | 2 | 3:40 | 63:35 | 16:40 | 15:25 | 32:05 | 379:15 | 35:45 | 17:52 | 97.8439 | 97.5974 | 442:50 | 221:25 | 96.3079 | 95.6889
24 | Ranebennur | 16 | 16 | 30:03 | 110:24 | 124:44 | 104:26 | 229:10 | 1575:08 | 259:13 | 16:12 | 98.0749 | 97.8224 | 1685:32 | 105:21 | 98.0832 | 97.9489
25 | Halageri | 2 | 2 | 19:20 | 209:05 | 28:55 | 2:55 | 31:50 | 428:15 | 51:10 | 25:35 | 97.8607 | 96.5614 | 637:20 | 318:40 | 95.8309 | 93.7954
26 | Tuminakatti | 2 | 2 | 50:00 | 54:05 | 4:25 | 0:00 | 4:25 | 227:10 | 54:25 | 27:12 | 99.7032 | 96.343 | 281:15 | 140:38 | 97.7885 | 97.262
27 | Kahanderayanahalli | 1 | 1 | 1:15 | 7:50 | 15:00 | 3:00 | 18:00 | 348:20 | 19:15 | 19:15 | 97.5806 | 97.4126 | 356:10 | 356:10 | 93.2178 | 93.0653
28 | Rattihalli | 1 | 1 | 2:00 | 6:05 | 5:10 | 5:00 | 10:10 | 156:30 | 12:10 | 12:10 | 98.6335 | 98.3647 | 162:35 | 162:35 | 96.9529 | 96.8344
29 | Hirekerur | 2 | 2 | 22:05 | 76:20 | 77:50 | 22:05 | 99:55 | 406:10 | 122:00 | 61:00 | 93.2852 | 91.8011 | 482:30 | 241:15 | 96.0459 | 95.3028
30 | Byadagi | 8 | 8 | 17:55 | 184:00 | 73:05 | 124:55 | 198:00 | 1512:35 | 215:55 | 26:59 | 96.6734 | 96.3724 | 1696:35 | 212:04 | 96.3187 | 95.8709
31 | Sirsi | 5 | 5 | 26:15 | 88:00 | 59:25 | 18:15 | 77:40 | 392:22 | 103:55 | 20:47 | 97.9122 | 97.2065 | 480:22 | 96:04 | 98.4721 | 98.1294
32 | Yellapur | 3 | 3 | 40:30 | 211:21 | 6:25 | 11:30 | 17:55 | 145:15 | 58:25 | 19:28 | 99.1973 | 97.3828 | 356:36 | 118:52 | 99.0573 | 97.6856
33 | Mundagod | 3 | 3 | 4:00 | 21:18 | 14:35 | 30:10 | 44:45 | 482:02 | 48:45 | 16:15 | 97.9951 | 97.8159 | 503:20 | 167:47 | 96.8715 | 96.7333
34 | Siddapur | 2 | 2 | 7:14 | 60:40 | 9:05 | 13:20 | 22:25 | 199:50 | 29:39 | 14:50 | 98.4935 | 98.0074 | 260:30 | 130:15 | 98.0546 | 97.464
35 | Dandeli | 8 | 8 | 2:12 | 90:52 | 45:44 | 47:50 | 93:34 | 996:35 | 95:46 | 11:58 | 98.428 | 98.391 | 1087:27 | 135:56 | 97.5745 | 97.3534
36 | Haliyal | 3 | 3 | 0:00 | 18:25 | 11:03 | 10:50 | 21:53 | 307:03 | 21:53 | 7:18 | 99.0196 | 99.0196 | 325:28 | 108:29 | 98.0072 | 97.8877
37 | Ankola | 3 | 3 | 32:23 | 201:01 | 14:38 | 11:23 | 26:01 | 272:04 | 58:24 | 19:28 | 98.8344 | 97.3835 | 473:05 | 157:42 | 98.2343 | 96.9296
38 | Kumta | 3 | 3 | 4:51 | 20:09 | 14:56 | 14:30 | 29:26 | 248:51 | 34:17 | 11:26 | 98.6813 | 98.464 | 269:00 | 89:40 | 98.3849 | 98.2542
39 | Gokarna | 1 | 1 | 10:15 | 80:37 | 1:25 | 0:00 | 1:25 | 67:10 | 11:40 | 11:40 | 99.8096 | 98.4319 | 147:47 | 147:47 | 98.6922 | 97.1226
40 | Kasarkod | 1 | 1 | 1:20 | 173:53 | 4:07 | 5:16 | 9:23 | 130:59 | 10:43 | 10:43 | 98.7388 | 98.5596 | 304:52 | 304:52 | 97.4497 | 94.0641
41 | Honnavar | 3 | 3 | 18:45 | 53:54 | 15:37 | 12:46 | 28:23 | 393:41 | 47:08 | 15:43 | 98.7283 | 97.8883 | 447:35 | 149:12 | 97.4449 | 97.0951
42 | Murdeshwar | 4 | 4 | 8:00 | 79:48 | 23:07 | 22:51 | 45:58 | 626:48 | 53:58 | 13:30 | 98.4554 | 98.1866 | 706:36 | 176:39 | 96.949 | 96.5606
43 | Bhatkal | 3 | 3 | 30:33 | 213:08 | 15:19 | 4:36 | 19:55 | 248:57 | 50:28 | 16:49 | 99.1077 | 97.7389 | 462:05 | 154:02 | 98.3843 | 97.001
44 | Khanapur | 2 | 2 | 28:00 | 71:20 | 29:45 | 10:50 | 40:35 | 273:30 | 68:35 | 34:18 | 97.2726 | 95.3909 | 344:50 | 172:25 | 97.3374 | 96.643
45 | Bailhongal | 3 | 3 | 6:39 | 64:10 | 45:55 | 27:35 | 73:30 | 876:51 | 80:09 | 26:43 | 96.707 | 96.4091 | 941:01 | 313:40 | 94.3091 | 93.8927
46 | Soundatti | 3 | 3 | 15:13 | 60:06 | 39:07 | 6:59 | 46:06 | 460:34 | 61:19 | 20:26 | 97.9346 | 97.2528 | 520:40 | 173:33 | 97.0109 | 96.6208
47 | Ramdurg | 2 | 2 | 11:52 | 49:00 | 9:12 | 3:23 | 12:35 | 219:19 | 24:27 | 12:14 | 99.1543 | 98.3569 | 268:19 | 134:09 | 97.8649 | 97.3879
48 | Gokak | 10 | 10 | 55:15 | 103:27 | 57:00 | 25:26 | 82:26 | 567:21 | 137:41 | 13:46 | 98.892 | 98.1494 | 670:48 | 67:05 | 98.8953 | 98.6939
49 | Mudalagi | 2 | 2 | 1:30 | 23:45 | 16:30 | 15:40 | 32:10 | 237:25 | 33:40 | 16:50 | 97.8383 | 97.7375 | 261:10 | 130:35 | 97.6887 | 97.4575
50 | Konnur | 1 | 1 | 1:20 | 2:25 | 12:15 | 3:30 | 15:45 | 163:35 | 17:05 | 17:05 | 97.8831 | 97.7039 | 166:00 | 166:00 | 96.815 | 96.7679
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 39:02 | 15:05 | 54:07 | 257:32 | 54:07 | 54:07 | 92.7263 | 92.7263 | 257:32 | 257:32 | 94.9857 | 94.9857
52 | Kudachi | 1 | 1 | 3:20 | 7:30 | 37:50 | 12:55 | 50:45 | 348:05 | 54:05 | 54:05 | 93.1788 | 92.7307 | 355:35 | 355:35 | 93.2227 | 93.0766
53 | Athani | 7 | 7 | 45:32 | 206:15 | 64:29 | 84:51 | 149:20 | 852:57 | 194:52 | 27:50 | 97.1326 | 96.2583 | 1059:12 | 151:19 | 97.6275 | 97.0538
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 7:15 | 7:25 | 14:40 | 161:05 | 14:40 | 7:20 | 99.0143 | 99.0143 | 161:05 | 80:32 | 98.4318 | 98.4318
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 30:00 | 22:50 | 52:50 | 622:48 | 52:50 | 10:34 | 98.5797 | 98.5797 | 622:48 | 124:34 | 97.5748 | 97.5748
56 | Sadalaga | 1 | 1 | 10:40 | 17:15 | 14:25 | 14:00 | 28:25 | 178:15 | 39:05 | 39:05 | 96.1806 | 94.7469 | 195:30 | 195:30 | 96.5294 | 96.1935
57 | Muddebihal | 2 | 2 | 4:00 | 72:30 | 34:10 | 14:35 | 48:45 | 476:00 | 52:45 | 26:22 | 96.7238 | 96.455 | 548:30 | 274:15 | 95.366 | 94.6602
58 | Talikoti | 1 | 1 | 3:10 | 24:40 | 10:35 | 6:25 | 17:00 | 136:30 | 20:10 | 20:10 | 97.7151 | 97.2894 | 161:10 | 161:10 | 97.3423 | 96.862
59 | B.Bagewadi | 1 | 1 | 3:00 | 19:45 | 7:35 | 3:41 | 11:16 | 65:47 | 14:16 | 14:16 | 98.4857 | 98.0824 | 85:32 | 85:32 | 98.7192 | 98.3346
60 | Indi | 3 | 3 | 1:31 | 21:08 | 16:49 | 5:01 | 21:50 | 160:25 | 23:21 | 7:47 | 99.0218 | 98.9539 | 181:33 | 60:31 | 98.9589 | 98.8217
61 | Sindagi | 2 | 2 | 1:40 | 82:20 | 13:45 | 6:25 | 20:10 | 264:55 | 21:50 | 10:55 | 98.6447 | 98.5327 | 347:15 | 173:38 | 97.421 | 96.6195
62 | Guledgudda | 1 | 1 | 0:00 | 9:08 | 7:35 | 4:31 | 12:06 | 169:21 | 12:06 | 12:06 | 98.3737 | 98.3737 | 178:29 | 178:29 | 96.7027 | 96.5249
63 | Ilkal | 8 | 8 | 18:20 | 200:27 | 59:15 | 164:33 | 223:48 | 1968:13 | 242:08 | 30:16 | 96.2399 | 95.9319 | 2168:40 | 271:05 | 95.2098 | 94.7219
64 | Kerur | 2 | 2 | 6:06 | 44:14 | 51:22 | 18:12 | 69:34 | 218:39 | 75:40 | 37:50 | 95.3248 | 94.9149 | 262:53 | 131:27 | 97.8714 | 97.4408
65 | Hungund | 4 | 4 | 7:12 | 93:04 | 33:29 | 45:35 | 79:04 | 663:23 | 86:16 | 21:34 | 97.3432 | 97.1013 | 756:27 | 189:07 | 96.7709 | 96.3179
66 | Gaddankeri | 3 | 3 | 0:28 | 70:52 | 32:32 | 6:41 | 39:13 | 465:08 | 39:41 | 13:14 | 98.243 | 98.2221 | 536:00 | 178:40 | 96.9812 | 96.5213
67 | Rampur | 1 | 1 | 2:30 | 19:32 | 16:22 | 3:39 | 20:01 | 127:28 | 22:31 | 22:31 | 97.3096 | 96.9736 | 147:00 | 147:00 | 97.5182 | 97.1379
68 | Kaladagi | 2 | 2 | 0:00 | 41:33 | 22:36 | 23:30 | 46:06 | 289:39 | 46:06 | 23:03 | 96.9019 | 96.9019 | 331:12 | 165:36 | 97.1802 | 96.7757
69 | Achanur | 1 | 1 | 0:00 | 9:42 | 14:27 | 13:33 | 28:00 | 308:13 | 28:00 | 28:00 | 96.2366 | 96.2366 | 317:55 | 317:55 | 93.9989 | 93.81
70 | Shirur | 1 | 1 | 1:18 | 57:44 | 3:27 | 5:08 | 8:35 | 177:30 | 9:53 | 9:53 | 98.8463 | 98.6716 | 235:14 | 235:14 | 96.544 | 95.4199
71 | Badami | 1 | 1 | 0:26 | 26:17 | 8:23 | 8:23 | 16:46 | 171:17 | 17:12 | 17:12 | 97.7464 | 97.6882 | 197:34 | 197:34 | 96.665 | 96.1533
72 | Kulageri | 1 | 1 | 2:53 | 16:00 | 5:32 | 0:55 | 6:27 | 47:49 | 9:20 | 9:20 | 99.1331 | 98.7455 | 63:49 | 63:49 | 99.069 | 98.7575
73 | Jamkhandi | 7 | 7 | 38:10 | 142:00 | 77:20 | 18:35 | 95:55 | 663:25 | 134:05 | 19:09 | 98.1583 | 97.4254 | 805:25 | 115:04 | 98.1547 | 97.7597
74 | Mahalingapur | 3 | 3 | 14:54 | 27:29 | 178:44 | 48:14 | 226:58 | 557:27 | 241:52 | 80:37 | 89.8312 | 89.1637 | 584:56 | 194:59 | 96.3821 | 96.2037
75 | Rabakavi | 2 | 2 | 10:35 | 40:55 | 14:15 | 5:30 | 19:45 | 145:45 | 30:20 | 15:10 | 98.6727 | 97.9615 | 186:40 | 93:20 | 98.5811 | 98.1828
76 | Banahatti | 2 | 2 | 8:16 | 22:36 | 21:15 | 4:30 | 25:45 | 163:10 | 34:01 | 17:00 | 98.2695 | 97.7139 | 185:46 | 92:53 | 98.4115 | 98.1915
77 | Terdal | 2 | 2 | 0:00 | 3:45 | 60:50 | 6:45 | 67:35 | 280:00 | 67:35 | 33:48 | 95.4581 | 95.4581 | 283:45 | 141:52 | 97.2741 | 97.2376
78 | Mudhol | 4 | 4 | 1:56 | 33:30 | 47:25 | 7:40 | 55:05 | 444:25 | 57:01 | 14:15 | 98.1491 | 98.0841 | 477:55 | 119:29 | 97.8368 | 97.6737
79 | Bilagi | 1 | 1 | 1:00 | 21:33 | 14:30 | 2:10 | 16:40 | 117:33 | 17:40 | 17:40 | 97.7599 | 97.6254 | 139:06 | 139:06 | 97.7113 | 97.2917
80 | Lokapur | 2 | 2 | 1:30 | 12:00 | 28:50 | 5:50 | 34:40 | 420:35 | 36:10 | 18:05 | 97.6703 | 97.5694 | 432:35 | 216:17 | 95.9055 | 95.7887
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of November-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of November-2021 |  |  |  | Reliability for cumulative period from Apr-21 to November-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 44:53 | 224:18 | 102:27 | 292:25 | 394:52 | 4258:43 | 439:45 | 5:34 | 99.3058 | 99.2269 | 4483:01 | 56:45 | 99.0794 | 99.031
2 | Dharwad(R) | 14 | 14 | 11:15 | 348:48 | 163:16 | 84:59 | 248:15 | 3250:40 | 259:30 | 18:32 | 97.5372 | 97.4256 | 3599:28 | 257:06 | 96.035 | 95.6095
3 | Kundagol | 1 | 1 | 15:55 | 132:50 | 11:45 | 11:20 | 23:05 | 127:10 | 39:00 | 39:00 | 96.794 | 94.5833 | 260:00 | 260:00 | 97.8284 | 95.5601
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 5:47 | 5:33 | 11:20 | 115:56 | 11:20 | 11:20 | 98.4259 | 98.4259 | 115:56 | 115:56 | 98.0203 | 98.0203
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 9:13 | 2:55 | 12:08 | 135:07 | 12:08 | 12:08 | 98.3148 | 98.3148 | 135:07 | 135:07 | 97.6927 | 97.6927
6 | Kalghatagi | 2 | 2 | 22:10 | 182:10 | 24:10 | 19:35 | 43:45 | 469:59 | 65:55 | 32:58 | 96.9618 | 95.4225 | 652:09 | 326:04 | 95.9872 | 94.4318
7 | Alnavar | 2 | 2 | 0:00 | 6:10 | 4:15 | 9:25 | 13:40 | 196:50 | 13:40 | 6:50 | 99.0509 | 99.0509 | 203:00 | 101:30 | 98.3194 | 98.2667
8 | Naragund | 2 | 2 | 4:20 | 65:20 | 12:50 | 7:30 | 20:20 | 288:10 | 24:40 | 12:20 | 98.588 | 98.287 | 353:30 | 176:45 | 97.5396 | 96.9817
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 43:10 | 67:25 | 110:35 | 668:15 | 110:35 | 27:39 | 96.1603 | 96.1603 | 668:15 | 167:04 | 97.1472 | 97.1472
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 25:05 | 26:47 | 51:52 | 646:27 | 51:52 | 12:58 | 98.1991 | 98.1991 | 646:27 | 161:37 | 97.2402 | 97.2402
11 | Naregal | 1 | 1 | 1:20 | 12:15 | 0:45 | 1:20 | 2:05 | 71:20 | 3:25 | 3:25 | 99.7106 | 99.5255 | 83:35 | 83:35 | 98.7819 | 98.5727
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 11:05 | 11:55 | 23:00 | 302:21 | 23:00 | 11:30 | 98.4028 | 98.4028 | 302:21 | 151:10 | 97.4185 | 97.4185
13 | Ron | 3 | 3 | 0:00 | 14:15 | 22:35 | 8:45 | 31:20 | 443:17 | 31:20 | 10:27 | 98.5494 | 98.5494 | 457:32 | 152:31 | 97.4768 | 97.3956
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 13:40 | 12:25 | 26:05 | 321:10 | 26:05 | 8:42 | 98.7924 | 98.7924 | 321:10 | 107:03 | 98.1719 | 98.1719
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 21:25 | 0:00 | 21:25 | 308:01 | 21:25 | 21:25 | 97.0255 | 97.0255 | 308:01 | 308:01 | 94.7402 | 94.7402
16 | G.C.T.M | 1 | 1 | 7:05 | 50:05 | 8:45 | 12:10 | 20:55 | 129:25 | 28:00 | 28:00 | 97.0949 | 96.1111 | 179:30 | 179:30 | 97.79 | 96.9348
17 | F.C.S.M | 2 | 2 | 9:50 | 90:55 | 6:35 | 0:50 | 7:25 | 113:45 | 17:15 | 8:38 | 99.485 | 98.8021 | 204:40 | 102:20 | 99.0288 | 98.2525
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 8:25 | 2:32 | 10:57 | 86:28 | 10:57 | 10:57 | 98.4792 | 98.4792 | 86:28 | 86:28 | 98.5235 | 98.5235
19 | Hole-Alur | 1 | 1 | 11:10 | 86:30 | 12:35 | 1:10 | 13:45 | 97:30 | 24:55 | 24:55 | 98.0903 | 96.5394 | 184:00 | 184:00 | 98.335 | 96.8579
20 | Savanur | 3 | 3 | 12:45 | 21:30 | 21:15 | 21:30 | 42:45 | 430:45 | 55:30 | 18:30 | 98.0208 | 97.4306 | 452:15 | 150:45 | 97.5481 | 97.4257
21 | Shiggaon | 2 | 2 | 0:55 | 22:05 | 7:40 | 25:40 | 33:20 | 462:50 | 34:15 | 17:08 | 97.6852 | 97.6215 | 484:55 | 242:27 | 96.0482 | 95.8597
22 | Bankapur | 1 | 1 | 14:05 | 78:45 | 18:50 | 4:30 | 23:20 | 194:15 | 37:25 | 37:25 | 96.7593 | 94.8032 | 273:00 | 273:00 | 96.6829 | 95.3381
23 | Hangal | 2 | 2 | 3:35 | 67:10 | 19:50 | 9:30 | 29:20 | 408:35 | 32:55 | 16:27 | 97.963 | 97.7141 | 475:45 | 237:52 | 96.5114 | 95.9379
24 | Ranebennur | 11 | 11 | 6:24 | 116:48 | 54:47 | 28:21 | 83:08 | 1658:16 | 89:32 | 8:08 | 98.9503 | 98.8695 | 1775:04 | 161:22 | 97.4257 | 97.2444
25 | Halageri | 1 | 1 | 1:20 | 210:25 | 1:10 | 0:00 | 1:10 | 429:25 | 2:30 | 2:30 | 99.838 | 99.6528 | 639:50 | 639:50 | 92.6671 | 89.0739
26 | Tuminakatti | 1 | 1 | 0:25 | 54:30 | 0:00 | 30:40 | 30:40 | 257:50 | 31:05 | 31:05 | 95.7407 | 95.6829 | 312:20 | 312:20 | 95.5971 | 94.6664
27 | Kahanderayanahalli | 1 | 1 | 1:40 | 9:30 | 4:00 | 27:20 | 31:20 | 379:40 | 33:00 | 33:00 | 95.6481 | 95.4167 | 389:10 | 389:10 | 93.5166 | 93.3544
28 | Rattihalli | 1 | 1 | 0:30 | 6:35 | 11:05 | 6:20 | 17:25 | 173:55 | 17:55 | 17:55 | 97.581 | 97.5116 | 180:30 | 180:30 | 97.0301 | 96.9177
29 | Hirekerur | 2 | 2 | 6:10 | 82:30 | 41:35 | 32:05 | 73:40 | 479:50 | 79:50 | 39:55 | 94.8843 | 94.456 | 562:20 | 281:10 | 95.9031 | 95.1987
30 | Byadagi | 6 | 6 | 15:30 | 199:30 | 87:55 | 38:15 | 126:10 | 1638:45 | 141:40 | 23:37 | 97.0795 | 96.7207 | 1838:15 | 306:22 | 95.336 | 94.7682
31 | Sirsi | 5 | 5 | 26:15 | 114:15 | 100:50 | 31:30 | 132:20 | 524:42 | 158:35 | 31:43 | 96.3241 | 95.5949 | 638:57 | 127:47 | 98.208 | 97.8178
32 | Yellapur | 3 | 3 | 40:30 | 251:51 | 6:25 | 11:30 | 17:55 | 163:10 | 58:25 | 19:28 | 99.1705 | 97.2955 | 415:01 | 138:20 | 99.0712 | 97.6377
33 | Mundagod | 3 | 3 | 4:00 | 25:18 | 14:35 | 30:10 | 44:45 | 526:47 | 48:45 | 16:15 | 97.9282 | 97.7431 | 552:05 | 184:02 | 97.0015 | 96.8574
34 | Siddapur | 2 | 2 | 7:14 | 67:54 | 9:05 | 13:20 | 22:25 | 222:15 | 29:39 | 14:50 | 98.4433 | 97.941 | 290:09 | 145:04 | 98.1024 | 97.5226
35 | Dandeli | 8 | 8 | 1:16 | 92:08 | 29:21 | 87:57 | 117:18 | 1113:53 | 118:34 | 14:49 | 97.9635 | 97.9416 | 1206:01 | 150:45 | 97.6223 | 97.4257
36 | Haliyal | 3 | 3 | 0:31 | 18:56 | 13:06 | 11:08 | 24:14 | 331:17 | 24:45 | 8:15 | 98.8781 | 98.8542 | 350:13 | 116:44 | 98.1143 | 98.0065
37 | Ankola | 3 | 3 | 9:15 | 210:16 | 3:02 | 12:14 | 15:16 | 287:20 | 24:31 | 8:10 | 99.2932 | 98.865 | 497:36 | 165:52 | 98.3645 | 97.1676
38 | Kumta | 3 | 3 | 3:21 | 23:30 | 14:07 | 9:32 | 23:39 | 272:30 | 27:00 | 9:00 | 98.9051 | 98.75 | 296:00 | 98:40 | 98.4489 | 98.3151
39 | Gokarna | 1 | 1 | 6:40 | 87:17 | 7:15 | 6:25 | 13:40 | 80:50 | 20:20 | 20:20 | 98.1019 | 97.1759 | 168:07 | 168:07 | 98.6196 | 97.1292
40 | Kasarkod | 1 | 1 | 18:11 | 192:04 | 2:45 | 3:45 | 6:30 | 137:29 | 24:41 | 24:41 | 99.0972 | 96.5718 | 329:33 | 329:33 | 97.6523 | 94.3724
41 | Honnavar | 3 | 3 | 4:30 | 58:24 | 14:34 | 10:22 | 24:56 | 418:37 | 29:26 | 9:49 | 98.8457 | 98.6373 | 477:01 | 159:00 | 97.6172 | 97.2847
42 | Murdeshwar | 4 | 4 | 6:00 | 85:48 | 28:05 | 24:47 | 52:52 | 679:40 | 58:52 | 14:43 | 98.1644 | 97.956 | 765:28 | 191:22 | 97.0984 | 96.7321
43 | Bhatkal | 3 | 3 | 3:39 | 216:47 | 23:48 | 5:46 | 29:34 | 278:31 | 33:13 | 11:04 | 98.6312 | 98.4622 | 495:18 | 165:06 | 98.4146 | 97.1807
44 | Khanapur | 2 | 2 | 30:00 | 101:20 | 54:05 | 14:20 | 68:25 | 341:55 | 98:25 | 49:12 | 95.2488 | 93.1655 | 443:15 | 221:38 | 97.0806 | 96.2154
45 | Bailhongal | 3 | 3 | 3:39 | 67:49 | 67:20 | 47:30 | 114:50 | 991:41 | 118:29 | 39:30 | 94.6836 | 94.5147 | 1059:30 | 353:10 | 94.3552 | 93.9691
46 | Soundatti | 3 | 3 | 8:38 | 68:44 | 23:51 | 8:31 | 32:22 | 492:56 | 41:00 | 13:40 | 98.5015 | 98.1019 | 561:40 | 187:13 | 97.1941 | 96.8029
47 | Ramdurg | 2 | 2 | 12:10 | 61:10 | 19:20 | 3:50 | 23:10 | 242:29 | 35:20 | 17:40 | 98.3912 | 97.5463 | 303:39 | 151:49 | 97.9296 | 97.4074
48 | Gokak | 10 | 10 | 4:40 | 108:07 | 9:21 | 28:14 | 37:35 | 604:56 | 42:15 | 4:14 | 99.478 | 99.4132 | 713:03 | 71:18 | 98.967 | 98.7824
49 | Mudalagi | 2 | 2 | 11:00 | 34:45 | 37:10 | 3:20 | 40:30 | 277:55 | 51:30 | 25:45 | 97.1875 | 96.4236 | 312:40 | 156:20 | 97.6271 | 97.3304
50 | Konnur | 1 | 1 | 0:00 | 2:25 | 10:50 | 0:50 | 11:40 | 175:15 | 11:40 | 11:40 | 98.3796 | 98.3796 | 177:40 | 177:40 | 97.0073 | 96.9661
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 25:54 | 4:25 | 30:19 | 287:51 | 30:19 | 30:19 | 95.7894 | 95.7894 | 287:51 | 287:51 | 95.0845 | 95.0845
52 | Kudachi | 1 | 1 | 1:45 | 9:15 | 28:40 | 6:25 | 35:05 | 383:10 | 36:50 | 36:50 | 95.1273 | 94.8843 | 392:25 | 392:25 | 93.4569 | 93.2989
53 | Athani | 7 | 7 | 9:59 | 216:14 | 45:27 | 48:55 | 94:22 | 947:19 | 104:21 | 14:54 | 98.1276 | 97.9296 | 1163:33 | 166:13 | 97.689 | 97.1615
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 1:45 | 4:20 | 6:05 | 167:10 | 6:05 | 3:02 | 99.5775 | 99.5775 | 167:10 | 83:35 | 98.5727 | 98.5727
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 31:20 | 12:25 | 43:45 | 666:33 | 43:45 | 8:45 | 98.7847 | 98.7847 | 666:33 | 133:19 | 97.7235 | 97.7235
56 | Sadalaga | 1 | 1 | 0:00 | 17:15 | 11:15 | 2:50 | 14:05 | 192:20 | 14:05 | 14:05 | 98.044 | 98.044 | 209:35 | 209:35 | 96.7156 | 96.421
57 | Muddebihal | 2 | 2 | 0:40 | 73:10 | 31:40 | 8:25 | 40:05 | 516:05 | 40:45 | 20:22 | 97.2164 | 97.1701 | 589:15 | 294:38 | 95.5936 | 94.9688
58 | Talikoti | 1 | 1 | 8:25 | 33:05 | 8:55 | 4:05 | 13:00 | 149:30 | 21:25 | 21:25 | 98.1944 | 97.0255 | 182:35 | 182:35 | 97.4471 | 96.8821
59 | B.Bagewadi | 1 | 1 | 2:27 | 22:12 | 3:11 | 3:28 | 6:39 | 72:26 | 9:06 | 9:06 | 99.0764 | 98.7361 | 94:38 | 94:38 | 98.7631 | 98.384
60 | Indi | 3 | 3 | 1:31 | 22:39 | 8:31 | 50:45 | 59:16 | 219:41 | 60:47 | 20:16 | 97.2562 | 97.186 | 242:20 | 80:47 | 98.7495 | 98.6206
61 | Sindagi | 2 | 2 | 0:40 | 83:00 | 13:50 | 24:55 | 38:45 | 303:40 | 39:25 | 19:42 | 97.309 | 97.2627 | 386:40 | 193:20 | 97.4072 | 96.6985
62 | Guledgudda | 1 | 1 | 0:00 | 9:08 | 4:08 | 2:59 | 7:07 | 176:28 | 7:07 | 7:07 | 99.0116 | 99.0116 | 185:36 | 185:36 | 96.9866 | 96.8306
63 | Ilkal | 8 | 8 | 33:46 | 234:13 | 85:44 | 110:30 | 196:14 | 2164:27 | 230:00 | 28:45 | 96.5932 | 96.0069 | 2398:40 | 299:50 | 95.3798 | 94.8799
64 | Kerur | 2 | 2 | 0:56 | 45:10 | 9:36 | 5:18 | 14:54 | 233:33 | 15:50 | 7:55 | 98.9653 | 98.9005 | 278:43 | 139:22 | 98.0059 | 97.6202
65 | Hungund | 4 | 4 | 24:00 | 117:04 | 25:55 | 28:09 | 54:04 | 717:27 | 78:04 | 19:31 | 98.1227 | 97.2894 | 834:31 | 208:38 | 96.9371 | 96.4373
66 | Gaddankeri | 3 | 3 | 13:27 | 84:19 | 25:41 | 60:13 | 85:54 | 551:02 | 99:21 | 33:07 | 96.0231 | 95.4005 | 635:21 | 211:47 | 96.8634 | 96.3835
67 | Rampur | 1 | 1 | 4:24 | 23:56 | 4:21 | 4:03 | 8:24 | 135:52 | 12:48 | 12:48 | 98.8333 | 98.2222 | 159:48 | 159:48 | 97.6799 | 97.2712
68 | Kaladagi | 2 | 2 | 1:36 | 43:09 | 15:21 | 14:27 | 29:48 | 319:27 | 31:24 | 15:42 | 97.9306 | 97.8194 | 362:36 | 181:18 | 97.2725 | 96.904
69 | Achanur | 1 | 1 | 6:00 | 15:42 | 24:30 | 14:04 | 38:34 | 346:47 | 44:34 | 44:34 | 94.6435 | 93.8102 | 362:29 | 362:29 | 94.0782 | 93.8101
70 | Shirur | 1 | 1 | 3:12 | 60:56 | 0:00 | 26:39 | 26:39 | 204:09 | 29:51 | 29:51 | 96.2986 | 95.8542 | 265:05 | 265:05 | 96.5138 | 95.4733
71 | Badami | 1 | 1 | 0:14 | 26:31 | 6:50 | 4:08 | 10:58 | 182:15 | 11:12 | 11:12 | 98.4769 | 98.4444 | 208:46 | 208:46 | 96.8878 | 96.435
72 | Kulageri | 1 | 1 | 0:25 | 16:25 | 6:40 | 0:45 | 7:25 | 55:14 | 7:50 | 7:50 | 98.9699 | 98.912 | 71:39 | 71:39 | 99.0568 | 98.7765
73 | Jamkhandi | 6 | 6 | 9:10 | 151:10 | 54:05 | 16:45 | 70:50 | 734:15 | 80:00 | 13:20 | 98.3603 | 98.1481 | 885:25 | 147:34 | 97.9103 | 97.48
74 | Mahalingapur | 3 | 3 | 0:50 | 28:19 | 32:35 | 22:46 | 55:21 | 612:48 | 56:11 | 18:44 | 97.4375 | 97.3989 | 641:07 | 213:42 | 96.5118 | 96.3507
75 | Rabakavi | 2 | 2 | 2:20 | 43:15 | 8:45 | 2:50 | 11:35 | 157:20 | 13:55 | 6:58 | 99.1956 | 99.0336 | 200:35 | 100:18 | 98.6566 | 98.2874
76 | Banahatti | 2 | 2 | 0:10 | 22:46 | 12:10 | 1:05 | 13:15 | 176:25 | 13:25 | 6:42 | 99.0799 | 99.0683 | 199:11 | 99:36 | 98.4937 | 98.2993
77 | Terdal | 2 | 2 | 13:15 | 17:00 | 36:00 | 35:40 | 71:40 | 351:40 | 84:55 | 42:28 | 95.0231 | 94.103 | 368:40 | 184:20 | 96.9974 | 96.8522
78 | Mudhol | 4 | 4 | 0:00 | 33:30 | 39:01 | 7:33 | 46:34 | 490:59 | 46:34 | 11:38 | 98.3831 | 98.3831 | 524:29 | 131:07 | 97.9039 | 97.7609
79 | Bilagi | 1 | 1 | 8:15 | 29:48 | 14:55 | 2:50 | 17:45 | 135:18 | 26:00 | 26:00 | 97.5347 | 96.3889 | 165:06 | 165:06 | 97.6895 | 97.1807
80 | Lokapur | 2 | 2 | 0:20 | 12:20 | 53:05 | 17:10 | 70:15 | 490:50 | 70:35 | 35:18 | 95.1215 | 95.0984 | 503:10 | 251:35 | 95.8091 | 95.7038
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of December-2021
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of December-2021 |  |  |  | Reliability for cumulative period from Apr-21 to December-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 53:33 | 277:51 | 151:29 | 150:53 | 302:22 | 4561:05 | 355:55 | 4:30 | 99.4856 | 99.3945 | 4838:56 | 61:15 | 99.1252 | 99.0719
2 | Dharwad(R) | 14 | 14 | 10:55 | 359:43 | 89:01 | 21:08 | 110:09 | 3360:49 | 121:04 | 8:39 | 98.9425 | 98.8377 | 3720:32 | 265:45 | 96.3628 | 95.9734
3 | Kundagol | 1 | 1 | 6:00 | 138:50 | 8:10 | 3:05 | 11:15 | 138:25 | 17:15 | 17:15 | 98.4879 | 97.6815 | 277:15 | 277:15 | 97.9028 | 95.7992
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 2:41 | 4:44 | 7:25 | 123:21 | 7:25 | 7:25 | 99.0031 | 99.0031 | 123:21 | 123:21 | 98.1311 | 98.1311
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 2:45 | 2:45 | 5:30 | 140:37 | 5:30 | 5:30 | 99.2608 | 99.2608 | 140:37 | 140:37 | 97.8694 | 97.8694
6 | Kalghatagi | 2 | 2 | 5:25 | 187:35 | 20:25 | 9:00 | 29:25 | 499:24 | 34:50 | 17:25 | 98.0231 | 97.6591 | 686:59 | 343:30 | 96.2167 | 94.7956
7 | Alnavar | 2 | 2 | 0:00 | 6:10 | 32:45 | 4:30 | 37:15 | 234:05 | 37:15 | 18:38 | 97.4966 | 97.4966 | 240:15 | 120:08 | 98.2266 | 98.1799
8 | Naragund | 2 | 2 | 5:30 | 70:50 | 20:50 | 8:10 | 29:00 | 317:10 | 34:30 | 17:15 | 98.0511 | 97.6815 | 388:00 | 194:00 | 97.5972 | 97.0606
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 31:05 | 28:50 | 59:55 | 728:10 | 59:55 | 14:59 | 97.9867 | 97.9867 | 728:10 | 182:02 | 97.2418 | 97.2418
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 25:05 | 26:47 | 51:52 | 698:19 | 51:52 | 12:58 | 98.2572 | 98.2572 | 698:19 | 174:35 | 97.3549 | 97.3549
11 | Naregal | 1 | 1 | 1:25 | 13:40 | 3:15 | 1:35 | 4:50 | 76:10 | 6:15 | 6:15 | 99.3504 | 99.1599 | 89:50 | 89:50 | 98.846 | 98.6389
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 60:40 | 26:10 | 86:50 | 389:11 | 86:50 | 43:25 | 94.1644 | 94.1644 | 389:11 | 194:35 | 97.0516 | 97.0516
13 | Ron | 3 | 3 | 0:00 | 14:15 | 20:50 | 8:20 | 29:10 | 472:27 | 29:10 | 9:43 | 98.6932 | 98.6932 | 486:42 | 162:14 | 97.6139 | 97.5419
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 41:00 | 11:50 | 52:50 | 374:00 | 52:50 | 17:37 | 97.6329 | 97.6329 | 374:00 | 124:40 | 98.1111 | 98.1111
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 17:38 | 6:48 | 24:26 | 332:27 | 24:26 | 24:26 | 96.7159 | 96.7159 | 332:27 | 332:27 | 94.9629 | 94.9629
16 | G.C.T.M | 1 | 1 | 8:50 | 58:55 | 5:15 | 1:45 | 7:00 | 136:25 | 15:50 | 15:50 | 99.0591 | 97.8719 | 195:20 | 195:20 | 97.9331 | 97.0404
17 | F.C.S.M | 2 | 2 | 16:00 | 106:55 | 4:40 | 0:25 | 5:05 | 118:50 | 21:05 | 10:32 | 99.6584 | 98.5831 | 225:45 | 112:52 | 99.0997 | 98.2898
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 12:36 | 0:39 | 13:15 | 99:43 | 13:15 | 13:15 | 98.2191 | 98.2191 | 99:43 | 99:43 | 98.4891 | 98.4891
19 | Hole-Alur | 1 | 1 | 3:40 | 90:10 | 5:45 | 0:50 | 6:35 | 104:05 | 10:15 | 10:15 | 99.1151 | 98.6223 | 194:15 | 194:15 | 98.423 | 97.0568
20 | Savanur | 3 | 3 | 3:10 | 24:40 | 24:25 | 10:20 | 34:45 | 465:30 | 37:55 | 12:38 | 98.4431 | 98.3012 | 490:10 | 163:23 | 97.649 | 97.5244
21 | Shiggaon | 2 | 2 | 0:00 | 22:05 | 8:15 | 22:10 | 30:25 | 493:15 | 30:25 | 15:12 | 97.9559 | 97.9559 | 515:20 | 257:40 | 96.2633 | 96.096
22 | Bankapur | 1 | 1 | 14:00 | 92:45 | 7:10 | 6:15 | 13:25 | 207:40 | 27:25 | 27:25 | 98.1967 | 96.315 | 300:25 | 300:25 | 96.8535 | 95.4482
23 | Hangal | 2 | 2 | 16:50 | 84:00 | 10:15 | 8:55 | 19:10 | 427:45 | 36:00 | 18:00 | 98.7119 | 97.5806 | 511:45 | 255:52 | 96.7595 | 96.1231
24 | Ranebennur | 11 | 11 | 7:13 | 124:01 | 45:50 | 14:22 | 60:12 | 1718:28 | 67:25 | 6:08 | 99.2644 | 99.1762 | 1842:29 | 167:30 | 97.633 | 97.4621
25 | Halageri | 1 | 1 | 2:00 | 212:25 | 2:35 | 0:00 | 2:35 | 432:00 | 4:35 | 4:35 | 99.6528 | 99.384 | 644:25 | 644:25 | 93.4545 | 90.2361
26 | Tuminakatti | 1 | 1 | 0:40 | 55:10 | 17:35 | 0:30 | 18:05 | 275:55 | 18:45 | 18:45 | 97.5694 | 97.4798 | 331:05 | 331:05 | 95.8194 | 94.9836
27 | Kahanderayanahalli | 1 | 1 | 0:15 | 9:45 | 1:50 | 0:30 | 2:20 | 382:00 | 2:35 | 2:35 | 99.6864 | 99.6528 | 391:45 | 391:45 | 94.2121 | 94.0644
28 | Rattihalli | 1 | 1 | 2:50 | 9:25 | 13:55 | 3:30 | 17:25 | 191:20 | 20:15 | 20:15 | 97.6591 | 97.2782 | 200:45 | 200:45 | 97.101 | 96.9583
29 | Hirekerur | 2 | 2 | 6:15 | 88:45 | 33:50 | 13:15 | 47:05 | 526:55 | 53:20 | 26:40 | 96.8358 | 96.4158 | 615:40 | 307:50 | 96.0082 | 95.3359
30 | Byadagi | 6 | 6 | 20:25 | 219:55 | 34:00 | 10:15 | 44:15 | 1683:00 | 64:40 | 10:47 | 99.0087 | 98.5514 | 1902:55 | 317:09 | 95.75 | 95.1947
31 | Sirsi | 6 | 6 | 0:00 | 114:15 | 163:25 | 15:30 | 178:55 | 703:37 | 178:55 | 29:49 | 95.992 | 95.992 | 817:52 | 136:19 | 98.2232 | 97.9347
32 | Yellapur | 3 | 3 | 33:55 | 285:46 | 6:55 | 4:45 | 11:40 | 174:50 | 45:35 | 15:12 | 99.4773 | 97.9577 | 460:36 | 153:32 | 99.117 | 97.6737
33 | Mundagod | 2 | 2 | 14:00 | 39:18 | 21:19 | 2:50 | 24:09 | 550:56 | 38:09 | 19:04 | 98.377 | 97.4362 | 590:14 | 295:07 | 95.8263 | 95.5285
34 | Siddapur | 2 | 2 | 1:20 | 69:14 | 27:55 | 10:10 | 38:05 | 260:20 | 39:25 | 19:42 | 97.4406 | 97.351 | 329:34 | 164:47 | 98.0278 | 97.5033
35 | Dandeli | 8 | 8 | 1:08 | 93:16 | 26:05 | 38:02 | 64:07 | 1178:00 | 65:15 | 8:09 | 98.9228 | 98.9037 | 1271:16 | 158:54 | 97.7689 | 97.5923
36 | Haliyal | 3 | 3 | 0:00 | 18:56 | 5:30 | 1:10 | 6:40 | 337:57 | 6:40 | 2:13 | 99.7013 | 99.7013 | 356:53 | 118:58 | 98.2932 | 98.1976
37 | Ankola | 3 | 3 | 28:59 | 239:15 | 7:16 | 5:16 | 12:32 | 299:52 | 41:31 | 13:50 | 99.4385 | 98.1399 | 539:07 | 179:42 | 98.4855 | 97.2772
38 | Kumta | 3 | 3 | 10:54 | 34:24 | 11:48 | 8:11 | 19:59 | 292:29 | 30:53 | 10:18 | 99.1047 | 98.6163 | 326:53 | 108:58 | 98.5228 | 98.3491
39 | Gokarna | 1 | 1 | 14:55 | 102:12 | 9:50 | 0:55 | 10:45 | 91:35 | 25:40 | 25:40 | 98.5551 | 96.5502 | 193:47 | 193:47 | 98.6124 | 97.0639
40 | Kasarkod | 1 | 1 | 13:09 | 205:13 | 20:29 | 3:20 | 23:49 | 161:18 | 36:58 | 36:58 | 96.7988 | 95.0314 | 366:31 | 366:31 | 97.5561 | 94.4467
41 | Honnavar | 3 | 3 | 11:24 | 69:48 | 19:41 | 6:11 | 25:52 | 444:29 | 37:16 | 12:25 | 98.8411 | 98.3303 | 514:17 | 171:26 | 97.7551 | 97.4026
42 | Murdeshwar | 4 | 4 | 15:52 | 101:40 | 35:14 | 8:25 | 43:39 | 723:19 | 59:31 | 14:53 | 98.5333 | 98.0001 | 824:59 | 206:15 | 97.2602 | 96.8751
43 | Bhatkal | 3 | 3 | 25:00 | 241:47 | 21:30 | 3:40 | 25:10 | 303:41 | 50:10 | 16:43 | 98.8725 | 97.7524 | 545:28 | 181:49 | 98.4662 | 97.2451
44 | Khanapur | 2 | 2 | 30:00 | 131:20 | 54:05 | 62:20 | 116:25 | 458:20 | 146:25 | 73:12 | 92.1763 | 90.1602 | 589:40 | 294:50 | 96.5278 | 95.5328
45 | Bailhongal | 3 | 3 | 0:00 | 67:49 | 40:20 | 17:45 | 58:05 | 1049:46 | 58:05 | 19:22 | 97.3977 | 97.3977 | 1117:35 | 372:32 | 94.6981 | 94.3556
46 | Soundatti | 3 | 3 | 13:20 | 82:04 | 21:17 | 2:47 | 24:04 | 517:00 | 37:24 | 12:28 | 98.9217 | 98.3244 | 599:04 | 199:41 | 97.3889 | 96.9744
47 | Ramdurg | 2 | 2 | 15:10 | 76:20 | 10:50 | 1:10 | 12:00 | 254:29 | 27:10 | 13:35 | 99.1935 | 98.1743 | 330:49 | 165:24 | 98.0721 | 97.4938
48 | Gokak | 10 | 10 | 27:36 | 135:43 | 7:43 | 42:35 | 50:18 | 655:14 | 77:54 | 7:47 | 99.3239 | 98.953 | 790:57 | 79:06 | 99.0072 | 98.8016
49 | Mudalagi | 2 | 2 | 0:20 | 35:05 | 31:50 | 4:55 | 36:45 | 314:40 | 37:05 | 18:32 | 97.5302 | 97.5078 | 349:45 | 174:52 | 97.6162 | 97.3504
50 | Konnur | 1 | 1 | 0:00 | 2:25 | 13:20 | 1:40 | 15:00 | 190:15 | 15:00 | 15:00 | 97.9839 | 97.9839 | 192:40 | 192:40 | 97.1174 | 97.0808
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 22:55 | 7:00 | 29:55 | 317:46 | 29:55 | 29:55 | 95.9789 | 95.9789 | 317:46 | 317:46 | 95.1854 | 95.1854
52 | Kudachi | 1 | 1 | 2:20 | 11:35 | 22:35 | 7:55 | 30:30 | 413:40 | 32:50 | 32:50 | 95.9005 | 95.5869 | 425:15 | 425:15 | 93.7323 | 93.5568
53 | Athani | 7 | 7 | 8:27 | 224:41 | 55:19 | 38:02 | 93:21 | 1040:40 | 101:48 | 14:33 | 98.2076 | 98.0453 | 1265:21 | 180:46 | 97.7475 | 97.2611
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 2:30 | 5:50 | 8:20 | 175:30 | 8:20 | 4:10 | 99.44 | 99.44 | 175:30 | 87:45 | 98.6705 | 98.6705
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 23:25 | 64:15 | 87:40 | 754:13 | 87:40 | 17:32 | 97.6434 | 97.6434 | 754:13 | 150:51 | 97.7145 | 97.7145
56 | Sadalaga | 1 | 1 | 6:25 | 23:40 | 8:45 | 2:00 | 10:45 | 203:05 | 17:10 | 17:10 | 98.5551 | 97.6927 | 226:45 | 226:45 | 96.923 | 96.5644
57 | Muddebihal | 2 | 2 | 0:00 | 73:10 | 32:55 | 5:20 | 38:15 | 554:20 | 38:15 | 19:08 | 97.4294 | 97.4294 | 627:30 | 313:45 | 95.8005 | 95.2462
58 | Talikoti | 1 | 1 | 0:40 | 33:45 | 8:15 | 2:45 | 11:00 | 160:30 | 11:40 | 11:40 | 98.5215 | 98.4319 | 194:15 | 194:15 | 97.5682 | 97.0568
59 | B.Bagewadi | 1 | 1 | 2:48 | 25:00 | 3:42 | 0:49 | 4:31 | 76:57 | 7:19 | 7:19 | 99.3929 | 99.0166 | 101:57 | 101:57 | 98.8341 | 98.4553
60 | Indi | 3 | 3 | 3:35 | 26:14 | 12:14 | 1:28 | 13:42 | 233:23 | 17:17 | 5:46 | 99.3862 | 99.2257 | 259:37 | 86:32 | 98.8213 | 98.6888
61 | Sindagi | 2 | 2 | 26:20 | 109:20 | 17:40 | 3:35 | 21:15 | 324:55 | 47:35 | 23:48 | 98.5719 | 96.8022 | 434:15 | 217:08 | 97.5385 | 96.7102
62 | Guledgudda | 1 | 1 | 2:49 | 11:57 | 6:43 | 4:20 | 11:03 | 187:31 | 13:52 | 13:52 | 98.5148 | 98.1362 | 199:28 | 199:28 | 97.1588 | 96.9778
63 | Ilkal | 8 | 8 | 2:40 | 236:53 | 102:01 | 54:31 | 156:32 | 2320:59 | 159:12 | 19:54 | 97.3701 | 97.3253 | 2557:52 | 319:44 | 95.6042 | 95.1556
64 | Kerur | 2 | 2 | 0:16 | 45:26 | 27:33 | 9:01 | 36:34 | 270:07 | 36:50 | 18:25 | 97.5426 | 97.5246 | 315:33 | 157:46 | 97.9537 | 97.6095
65 | Hungund | 4 | 4 | 3:08 | 120:12 | 32:43 | 16:43 | 49:26 | 766:53 | 52:34 | 13:08 | 98.3389 | 98.2336 | 887:05 | 221:46 | 97.0951 | 96.6398
66 | Gaddankeri | 3 | 3 | 4:12 | 88:31 | 26:51 | 31:44 | 58:35 | 609:37 | 62:47 | 20:56 | 97.3753 | 97.1871 | 698:08 | 232:43 | 96.9211 | 96.4741
67 | Rampur | 1 | 1 | 0:00 | 23:56 | 5:00 | 0:57 | 5:57 | 141:49 | 5:57 | 5:57 | 99.2003 | 99.2003 | 165:45 | 165:45 | 97.8513 | 97.4886
68 | Kaladagi | 2 | 2 | 0:24 | 43:33 | 18:21 | 8:33 | 26:54 | 346:21 | 27:18 | 13:39 | 98.1922 | 98.1653 | 389:54 | 194:57 | 97.3761 | 97.0462
69 | Achanur | 1 | 1 | 0:21 | 16:03 | 8:33 | 4:48 | 13:21 | 360:08 | 13:42 | 13:42 | 98.2056 | 98.1586 | 376:11 | 376:11 | 94.5434 | 94.3003
70 | Shirur | 1 | 1 | 5:06 | 66:02 | 0:06 | 6:15 | 6:21 | 210:30 | 11:27 | 11:27 | 99.1465 | 98.461 | 276:32 | 276:32 | 96.8106 | 95.8101
71 | Badami | 1 | 1 | 0:20 | 26:51 | 3:33 | 4:05 | 7:38 | 189:53 | 7:58 | 7:58 | 98.974 | 98.9292 | 216:44 | 216:44 | 97.123 | 96.7162
72 | Kulageri | 1 | 1 | 1:00 | 17:25 | 1:45 | 1:15 | 3:00 | 58:14 | 4:00 | 4:00 | 99.5968 | 99.4624 | 75:39 | 75:39 | 99.1177 | 98.8538
73 | Jamkhandi | 6 | 6 | 6:00 | 157:10 | 48:55 | 13:35 | 62:30 | 796:45 | 68:30 | 11:25 | 98.5999 | 98.4655 | 953:55 | 158:59 | 97.988 | 97.5911
74 | Mahalingapur | 3 | 3 | 5:20 | 33:39 | 30:12 | 9:20 | 39:32 | 652:20 | 44:52 | 14:57 | 98.2288 | 97.9898 | 685:59 | 228:40 | 96.7054 | 96.5354
75 | Rabakavi | 2 | 2 | 7:25 | 50:40 | 6:10 | 2:10 | 8:20 | 165:40 | 15:45 | 7:52 | 99.44 | 98.9415 | 216:20 | 108:10 | 98.7449 | 98.3611
76 | Banahatti | 2 | 2 | 0:40 | 23:26 | 11:25 | 1:25 | 12:50 | 189:15 | 13:30 | 6:45 | 99.1375 | 99.0927 | 212:41 | 106:20 | 98.5663 | 98.3888
77 | Terdal | 2 | 2 | 23:30 | 40:30 | 111:20 | 15:45 | 127:05 | 478:45 | 150:35 | 75:18 | 91.4595 | 89.8802 | 519:15 | 259:38 | 96.3731 | 96.0663
78 | Mudhol | 4 | 4 | 6:04 | 39:34 | 31:00 | 5:14 | 36:14 | 527:13 | 42:18 | 10:35 | 98.7825 | 98.5786 | 566:47 | 141:42 | 98.003 | 97.8531
79 | Bilagi | 1 | 1 | 3:17 | 33:05 | 14:30 | 0:15 | 14:45 | 150:03 | 18:02 | 18:02 | 98.0175 | 97.5762 | 183:08 | 183:08 | 97.7265 | 97.2253
80 | Lokapur | 2 | 2 | 0:00 | 12:20 | 40:10 | 6:55 | 47:05 | 537:55 | 47:05 | 23:32 | 96.8358 | 96.8358 | 550:15 | 275:07 | 95.9249 | 95.8314
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of January-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of January-2022 |  |  |  | Reliability for cumulative period from Apr-21 to Jan-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 34:00 | 311:51 | 175:42 | 91:56 | 267:38 | 4828:43 | 301:38 | 3:49 | 99.5447 | 99.4868 | 5140:34 | 65:04 | 99.0739 | 99.0141
2 | Dharwad(R) | 14 | 14 | 3:19 | 363:02 | 93:36 | 34:54 | 128:30 | 3489:19 | 131:49 | 9:25 | 98.7663 | 98.7345 | 3852:21 | 275:10 | 96.2237 | 95.8308
3 | Kundagol | 1 | 1 | 0:50 | 139:40 | 5:50 | 1:10 | 7:00 | 145:25 | 7:50 | 7:50 | 99.0591 | 98.9471 | 285:05 | 285:05 | 97.7967 | 95.6806
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 3:03 | 3:28 | 6:31 | 129:52 | 6:31 | 6:31 | 99.1241 | 99.1241 | 129:52 | 129:52 | 98.0323 | 98.0323
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 3:20 | 11:00 | 14:20 | 154:57 | 14:20 | 14:20 | 98.0735 | 98.0735 | 154:57 | 154:57 | 97.6523 | 97.6523
6 | Kalghatagi | 2 | 2 | 0:40 | 188:15 | 20:15 | 13:30 | 33:45 | 533:09 | 34:25 | 17:12 | 97.7319 | 97.6871 | 721:24 | 360:42 | 95.961 | 94.5348
7 | Alnavar | 2 | 2 | 0:00 | 6:10 | 2:45 | 2:50 | 5:35 | 239:40 | 5:35 | 2:48 | 99.6248 | 99.6248 | 245:50 | 122:55 | 98.1843 | 98.1376
8 | Naragund | 2 | 2 | 13:00 | 83:50 | 13:55 | 6:10 | 20:05 | 337:15 | 33:05 | 16:33 | 98.6503 | 97.7767 | 421:05 | 210:32 | 97.4451 | 96.81
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 29:05 | 45:25 | 74:30 | 802:40 | 74:30 | 18:38 | 97.4966 | 97.4966 | 802:40 | 200:40 | 96.9596 | 96.9596
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 28:16 | 7:55 | 36:11 | 734:30 | 36:11 | 9:03 | 98.7842 | 98.7842 | 734:30 | 183:38 | 97.2178 | 97.2178
11 | Naregal | 1 | 1 | 1:05 | 14:45 | 1:55 | 0:15 | 2:10 | 78:20 | 3:15 | 3:15 | 99.7088 | 99.5632 | 93:05 | 93:05 | 98.8131 | 98.5896
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 13:30 | 5:40 | 19:10 | 408:21 | 19:10 | 9:35 | 98.7119 | 98.7119 | 408:21 | 204:10 | 96.9064 | 96.9064
13 | Ron | 3 | 3 | 0:00 | 14:15 | 12:35 | 7:30 | 20:05 | 492:32 | 20:05 | 6:42 | 99.1002 | 99.1002 | 506:47 | 168:56 | 97.5125 | 97.4405
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 10:00 | 3:20 | 13:20 | 387:20 | 13:20 | 4:27 | 99.4026 | 99.4026 | 387:20 | 129:07 | 98.0438 | 98.0438
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 10:02 | 4:25 | 14:27 | 346:54 | 14:27 | 14:27 | 98.0578 | 98.0578 | 346:54 | 346:54 | 94.7439 | 94.7439
16 | G.C.T.M | 1 | 1 | 0:05 | 59:00 | 4:50 | 0:20 | 5:10 | 141:35 | 5:15 | 5:15 | 99.3056 | 99.2944 | 200:35 | 200:35 | 97.8548 | 96.9609
17 | F.C.S.M | 2 | 2 | 2:40 | 109:35 | 4:10 | 0:05 | 4:15 | 123:05 | 6:55 | 3:27 | 99.7144 | 99.5352 | 232:40 | 116:20 | 99.0676 | 98.2374
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 1:20 | 1:00 | 2:20 | 102:03 | 2:20 | 2:20 | 99.6864 | 99.6864 | 102:03 | 102:03 | 98.4538 | 98.4538
19 | Hole-Alur | 1 | 1 | 3:00 | 93:10 | 5:15 | 0:20 | 5:35 | 109:40 | 8:35 | 8:35 | 99.2496 | 98.8463 | 202:50 | 202:50 | 98.3384 | 96.9268
20 | Savanur | 3 | 3 | 0:45 | 25:25 | 61:40 | 25:25 | 87:05 | 552:35 | 87:50 | 29:17 | 96.0984 | 96.0648 | 578:00 | 192:40 | 97.2092 | 97.0808
21 | Shiggaon | 4 | 4 | 2:50 | 24:55 | 17:50 | 11:40 | 29:30 | 522:45 | 32:20 | 8:05 | 98.0175 | 97.8271 | 547:40 | 136:55 | 96.0398 | 95.851
22 | Bankapur | 1 | 1 | 3:15 | 96:00 | 10:10 | 3:40 | 13:50 | 221:30 | 17:05 | 17:05 | 98.1407 | 97.7039 | 317:30 | 317:30 | 96.6439 | 95.1894
23 | Hangal | 2 | 2 | 16:40 | 100:40 | 11:25 | 2:00 | 13:25 | 441:10 | 30:05 | 15:03 | 99.0983 | 97.9783 | 541:50 | 270:55 | 96.6578 | 95.8952
24 | Ranebennur | 11 | 11 | 2:57 | 126:58 | 73:10 | 22:36 | 95:46 | 1814:14 | 98:43 | 8:58 | 98.8298 | 98.7938 | 1941:12 | 176:28 | 97.5011 | 97.3262
25 | Halageri | 1 | 1 | 5:55 | 218:20 | 1:40 | 0:00 | 1:40 | 433:40 | 7:35 | 7:35 | 99.776 | 98.9807 | 652:00 | 652:00 | 93.4293 | 90.1212
26 | Tuminakatti | 1 | 1 | 0:20 | 55:30 | 8:15 | 1:25 | 9:40 | 285:35 | 10:00 | 10:00 | 98.7007 | 98.6559 | 341:05 | 341:05 | 95.673 | 94.8321
27 | Kahanderayanahalli | 1 | 1 | 0:49 | 10:34 | 26:45 | 1:05 | 27:50 | 409:50 | 28:39 | 28:39 | 96.259 | 96.1492 | 420:24 | 420:24 | 93.7904 | 93.6303
28 | Rattihalli | 1 | 1 | 0:30 | 9:55 | 10:55 | 4:00 | 14:55 | 206:15 | 15:25 | 15:25 | 97.9951 | 97.9279 | 216:10 | 216:10 | 96.875 | 96.7247
29 | Hirekerur | 2 | 2 | 3:15 | 92:00 | 33:30 | 7:15 | 40:45 | 567:40 | 44:00 | 22:00 | 97.2614 | 97.043 | 659:40 | 329:50 | 95.6995 | 95.0025
30 | Byadagi | 6 | 6 | 12:15 | 232:10 | 32:45 | 60:20 | 93:05 | 1776:05 | 105:20 | 17:33 | 97.9148 | 97.6404 | 2008:15 | 334:42 | 95.5149 | 94.9287
31 | Sirsi | 6 | 6 | 9:00 | 123:15 | 77:30 | 6:25 | 83:55 | 787:32 | 92:55 | 15:29 | 98.1201 | 97.9185 | 910:47 | 151:48 | 98.0113 | 97.7
32 | Yellapur | 3 | 3 | 23:05 | 308:51 | 9:00 | 2:00 | 11:00 | 185:50 | 34:05 | 11:22 | 99.5072 | 98.473 | 494:41 | 164:54 | 99.0614 | 97.5016
33 | Mundagod | 2 | 2 | 1:20 | 40:38 | 2:45 | 1:50 | 4:35 | 555:31 | 5:55 | 2:58 | 99.692 | 99.6024 | 596:09 | 298:04 | 95.7915 | 95.4837
34 | Siddapur | 2 | 2 | 3:50 | 73:04 | 3:00 | 7:45 | 10:45 | 271:05 | 14:35 | 7:18 | 99.2776 | 99.0199 | 344:09 | 172:04 | 97.9463 | 97.3928
35 | Dandeli | 8 | 8 | 0:00 | 93:16 | 58:20 | 18:19 | 76:39 | 1254:39 | 76:39 | 9:35 | 98.7122 | 98.7122 | 1347:55 | 168:29 | 97.6238 | 97.4471
36 | Haliyal | 3 | 3 | 0:00 | 18:56 | 6:05 | 3:10 | 9:15 | 347:12 | 9:15 | 3:05 | 99.5856 | 99.5856 | 366:08 | 122:03 | 98.2465 | 98.1508
37 | Ankola | 3 | 3 | 9:48 | 249:03 | 10:06 | 12:50 | 22:56 | 322:48 | 32:44 | 10:55 | 98.9725 | 98.5335 | 571:51 | 190:37 | 98.3697 | 97.1119
38 | Kumta | 3 | 3 | 1:54 | 36:18 | 11:37 | 7:44 | 19:21 | 311:50 | 21:15 | 7:05 | 99.1331 | 99.0479 | 348:08 | 116:03 | 98.4251 | 98.2418
39 | Gokarna | 1 | 1 | 10:00 | 112:12 | 4:20 | 0:10 | 4:30 | 96:05 | 14:30 | 14:30 | 99.3952 | 98.0511 | 208:17 | 208:17 | 98.5442 | 96.8442
40 | Kasarkod | 1 | 1 | 20:02 | 225:15 | 3:45 | 1:30 | 5:15 | 166:33 | 25:17 | 25:17 | 99.2944 | 96.6017 | 391:48 | 391:48 | 97.4765 | 94.0636
41 | Honnavar | 3 | 3 | 1:51 | 71:39 | 10:55 | 3:03 | 13:58 | 458:27 | 15:49 | 5:16 | 99.3743 | 99.2914 | 530:06 | 176:42 | 97.6846 | 97.3227
42 | Murdeshwar | 4 | 4 | 2:28 | 104:08 | 25:34 | 10:31 | 36:05 | 759:24 | 38:33 | 9:38 | 98.7875 | 98.7046 | 863:32 | 215:53 | 97.1235 | 96.729
43 | Bhatkal | 3 | 3 | 6:12 | 247:59 | 11:43 | 4:52 | 16:35 | 320:16 | 22:47 | 7:36 | 99.257 | 98.9792 | 568:15 | 189:25 | 98.3825 | 97.1301
44 | Khanapur | 2 | 2 | 20:55 | 152:15 | 39:25 | 7:20 | 46:45 | 505:05 | 67:40 | 33:50 | 96.8582 | 95.4525 | 657:20 | 328:40 | 96.1736 | 95.0202
45 | Bailhongal | 3 | 3 | 0:03 | 67:52 | 26:50 | 5:35 | 32:25 | 1082:11 | 32:28 | 10:49 | 98.5476 | 98.5454 | 1150:03 | 383:21 | 94.5344 | 94.1917
46 | Soundatti | 3 | 3 | 3:34 | 85:38 | 13:22 | 1:50 | 15:12 | 532:12 | 18:46 | 6:15 | 99.319 | 99.1592 | 617:50 | 205:57 | 97.3121 | 96.8796
47 | Ramdurg | 2 | 2 | 5:18 | 81:38 | 13:20 | 1:10 | 14:30 | 268:59 | 19:48 | 9:54 | 99.0255 | 98.6694 | 350:37 | 175:18 | 97.9622 | 97.3438
48 | Gokak | 10 | 10 | 40:02 | 175:45 | 15:07 | 15:26 | 30:33 | 685:47 | 70:35 | 7:04 | 99.5894 | 99.0513 | 861:32 | 86:09 | 98.9609 | 98.6946
49 | Mudalagi | 2 | 2 | 2:20 | 37:25 | 17:10 | 1:10 | 18:20 | 333:00 | 20:40 | 10:20 | 98.7679 | 98.6111 | 370:25 | 185:12 | 97.4773 | 97.1938
50 | Konnur | 1 | 1 | 1:55 | 4:20 | 39:00 | 2:45 | 41:45 | 232:00 | 43:40 | 43:40 | 94.3884 | 94.1308 | 236:20 | 236:20 | 96.4848 | 96.4192
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 14:05 | 5:25 | 19:30 | 337:16 | 19:30 | 19:30 | 97.379 | 97.379 | 337:16 | 337:16 | 94.8899 | 94.8899
52 | Kudachi | 1 | 1 | 1:05 | 12:40 | 0:25 | 0:25 | 0:50 | 414:30 | 1:55 | 1:55 | 99.888 | 99.7424 | 427:10 | 427:10 | 93.7197 | 93.5278
53 | Athani | 7 | 7 | 22:00 | 246:41 | 64:37 | 26:28 | 91:05 | 1131:45 | 113:05 | 16:09 | 98.2511 | 97.8287 | 1378:26 | 196:55 | 97.5503 | 97.0164
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 17:55 | 1:25 | 19:20 | 194:50 | 19:20 | 9:40 | 98.7007 | 98.7007 | 194:50 | 97:25 | 98.524 | 98.524
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 71:40 | 10:50 | 82:30 | 836:43 | 82:30 | 16:30 | 97.7823 | 97.7823 | 836:43 | 167:21 | 97.4645 | 97.4645
56 | Sadalaga | 1 | 1 | 0:00 | 23:40 | 16:40 | 0:10 | 16:50 | 219:55 | 16:50 | 16:50 | 97.7375 | 97.7375 | 243:35 | 243:35 | 96.6679 | 96.3093
57 | Muddebihal | 2 | 2 | 0:55 | 74:05 | 30:40 | 5:30 | 36:10 | 590:30 | 37:05 | 18:33 | 97.5694 | 97.5078 | 664:35 | 332:18 | 95.5265 | 94.9653
58 | Talikoti | 1 | 1 | 25:15 | 59:00 | 15:05 | 4:10 | 19:15 | 179:45 | 44:30 | 44:30 | 97.4126 | 94.0188 | 238:45 | 238:45 | 97.2765 | 96.3826
59 | B.Bagewadi | 1 | 1 | 1:51 | 26:51 | 5:24 | 0:40 | 6:04 | 83:01 | 7:55 | 7:55 | 99.1846 | 98.9359 | 109:52 | 109:52 | 98.7422 | 98.3354
60 | Indi | 3 | 3 | 9:35 | 35:49 | 12:45 | 26:40 | 39:25 | 272:48 | 49:00 | 16:20 | 98.234 | 97.8047 | 308:37 | 102:52 | 98.6222 | 98.4413
61 | Sindagi | 2 | 2 | 6:50 | 116:10 | 13:30 | 2:35 | 16:05 | 341:00 | 22:55 | 11:28 | 98.9191 | 98.4599 | 457:10 | 228:35 | 97.4167 | 96.5366
62 | Guledgudda | 1 | 1 | 0:00 | 11:57 | 3:50 | 1:22 | 5:12 | 192:43 | 5:12 | 5:12 | 99.3011 | 99.3011 | 204:40 | 204:40 | 97.0801 | 96.899
63 | Ilkal | 8 | 8 | 4:45 | 241:38 | 40:07 | 38:25 | 78:32 | 2399:31 | 83:17 | 10:25 | 98.6806 | 98.6008 | 2641:09 | 330:09 | 95.4555 | 94.9978
64 | Kerur | 2 | 2 | 0:16 | 45:42 | 11:14 | 8:42 | 19:56 | 290:03 | 20:12 | 10:06 | 98.6604 | 98.6425 | 335:45 | 167:52 | 97.8027 | 97.4564
65 | Hungund | 4 | 4 | 4:02 | 124:14 | 38:11 | 16:18 | 54:29 | 821:22 | 58:31 | 14:38 | 98.1692 | 98.0337 | 945:36 | 236:24 | 96.8888 | 96.4182
66 | Gaddankeri | 3 | 3 | 2:18 | 90:49 | 26:06 | 7:48 | 33:54 | 643:31 | 36:12 | 12:04 | 98.4812 | 98.3781 | 734:20 | 244:47 | 96.7499 | 96.2912
67 | Rampur | 1 | 1 | 0:00 | 23:56 | 10:03 | 1:36 | 11:39 | 153:28 | 11:39 | 11:39 | 98.4341 | 98.4341 | 177:24 | 177:24 | 97.6747 | 97.3121
68 | Kaladagi | 2 | 2 | 0:18 | 43:51 | 7:36 | 5:21 | 12:57 | 359:18 | 13:15 | 6:37 | 99.1297 | 99.1095 | 403:09 | 201:34 | 97.278 | 96.9458
69 | Achanur | 1 | 1 | 0:00 | 16:03 | 7:03 | 2:54 | 9:57 | 370:05 | 9:57 | 9:57 | 98.6626 | 98.6626 | 386:08 | 386:08 | 94.3927 | 94.1495
70 | Shirur | 1 | 1 | 5:27 | 71:29 | 12:03 | 8:57 | 21:00 | 231:30 | 26:27 | 26:27 | 97.1774 | 96.4449 | 302:59 | 302:59 | 96.4924 | 95.4093
71 | Badami | 1 | 1 | 0:17 | 27:08 | 12:07 | 2:58 | 15:05 | 204:58 | 15:22 | 15:22 | 97.9727 | 97.9346 | 232:06 | 232:06 | 96.8944 | 96.4833
72 | Kulageri | 1 | 1 | 0:10 | 17:35 | 3:00 | 1:25 | 4:25 | 62:39 | 4:35 | 4:35 | 99.4064 | 99.384 | 80:14 | 80:14 | 99.0508 | 98.7843
73 | Jamkhandi | 6 | 6 | 0:25 | 157:35 | 44:25 | 3:40 | 48:05 | 844:50 | 48:30 | 8:05 | 98.9229 | 98.9135 | 1002:25 | 167:04 | 97.8666 | 97.4686
74 | Mahalingapur | 3 | 3 | 2:03 | 35:42 | 35:37 | 8:48 | 44:25 | 696:45 | 46:28 | 15:29 | 98.01 | 97.9182 | 732:27 | 244:09 | 96.4811 | 96.3008
75 | Rabakavi | 2 | 2 | 1:10 | 51:50 | 6:45 | 2:25 | 9:10 | 174:50 | 10:20 | 5:10 | 99.384 | 99.3056 | 226:40 | 113:20 | 98.6755 | 98.2828
76 | Banahatti | 2 | 2 | 0:35 | 24:01 | 6:50 | 0:05 | 6:55 | 196:10 | 7:30 | 3:45 | 99.5352 | 99.496 | 220:11 | 110:06 | 98.5139 | 98.3319
77 | Terdal | 2 | 2 | 0:00 | 40:30 | 17:05 | 3:05 | 20:10 | 498:55 | 20:10 | 10:05 | 98.6447 | 98.6447 | 539:25 | 269:43 | 96.2203 | 95.9135
78 | Mudhol | 4 | 4 | 2:14 | 41:48 | 24:34 | 9:22 | 33:56 | 561:09 | 36:10 | 9:02 | 98.8598 | 98.7847 | 602:57 | 150:44 | 97.8744 | 97.7161
79 | Bilagi | 1 | 1 | 4:20 | 37:25 | 8:15 | 0:00 | 8:15 | 158:18 | 12:35 | 12:35 | 98.8911 | 98.3087 | 195:43 | 195:43 | 97.6015 | 97.0346
80 | Lokapur | 2 | 2 | 0:00 | 12:20 | 42:40 | 6:05 | 48:45 | 586:40 | 48:45 | 24:22 | 96.7238 | 96.7238 | 599:00 | 299:30 | 95.5556 | 95.4621
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of February-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of February-2022 |  |  |  | Reliability for cumulative period from Apr-21 to February-2022
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 25:32 | 337:23 | 253:30 | 142:39 | 396:09 | 5224:52 | 421:41 | 5:20 | 99.2538 | 99.2057 | 5562:15 | 70:24 | 99.1749 | 99.1217
2 | Dharwad(R) | 14 | 14 | 1:40 | 364:42 | 353:44 | 26:22 | 380:06 | 3869:25 | 381:46 | 27:16 | 95.9598 | 95.9421 | 4234:07 | 302:26 | 96.5521 | 96.2271
3 | Kundagol | 1 | 1 | 3:55 | 143:35 | 2:30 | 0:20 | 2:50 | 148:15 | 6:45 | 6:45 | 99.5784 | 98.9955 | 291:50 | 291:50 | 98.1506 | 96.3594
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 12:18 | 4:14 | 16:32 | 146:24 | 16:32 | 16:32 | 97.5397 | 97.5397 | 146:24 | 146:24 | 98.1737 | 98.1737
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 4:00 | 2:15 | 6:15 | 161:12 | 6:15 | 6:15 | 99.0699 | 99.0699 | 161:12 | 161:12 | 97.989 | 97.989
6 | Kalghatagi | 2 | 2 | 0:00 | 188:15 | 15:10 | 15:20 | 30:30 | 563:39 | 30:30 | 15:15 | 97.7307 | 97.7307 | 751:54 | 375:57 | 96.4842 | 95.31
7 | Alnavar | 2 | 2 | 0:00 | 6:10 | 10:05 | 3:30 | 13:35 | 253:15 | 13:35 | 6:48 | 98.9893 | 98.9893 | 259:25 | 129:43 | 98.4203 | 98.3819
8 | Naragund | 2 | 2 | 8:10 | 92:00 | 11:40 | 6:00 | 17:40 | 354:55 | 25:50 | 12:55 | 98.6855 | 98.0779 | 446:55 | 223:28 | 97.7862 | 97.2123
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 17:37 | 12:35 | 30:12 | 832:52 | 30:12 | 7:33 | 98.8765 | 98.8765 | 832:52 | 208:13 | 97.4025 | 97.4025
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 22:02 | 15:00 | 37:02 | 771:32 | 37:02 | 9:16 | 98.6223 | 98.6223 | 771:32 | 192:53 | 97.5938 | 97.5938
11 | Naregal | 1 | 1 | 1:45 | 16:30 | 4:25 | 0:30 | 4:55 | 83:15 | 6:40 | 6:40 | 99.2684 | 99.0079 | 99:45 | 99:45 | 98.9615 | 98.7556
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 13:55 | 11:10 | 25:05 | 433:26 | 25:05 | 12:32 | 98.1337 | 98.1337 | 433:26 | 216:43 | 97.2964 | 97.2964
13 | Ron | 3 | 3 | 0:00 | 14:15 | 14:55 | 20:40 | 35:35 | 528:07 | 35:35 | 11:52 | 98.235 | 98.235 | 542:22 | 180:47 | 97.8039 | 97.7446
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 16:25 | 13:40 | 30:05 | 417:25 | 30:05 | 10:02 | 98.5078 | 98.5078 | 417:25 | 139:08 | 98.2642 | 98.2642
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 10:26 | 2:04 | 12:30 | 359:24 | 12:30 | 12:30 | 98.1399 | 98.1399 | 359:24 | 359:24 | 95.5165 | 95.5165
16 | G.C.T.M | 1 | 1 | 2:05 | 61:05 | 8:55 | 0:55 | 9:50 | 151:25 | 11:55 | 11:55 | 98.5367 | 98.2267 | 212:30 | 212:30 | 98.1111 | 97.3491
17 | F.C.S.M | 2 | 2 | 2:40 | 112:15 | 4:50 | 0:40 | 5:30 | 128:35 | 8:10 | 4:05 | 99.5908 | 99.3924 | 240:50 | 120:25 | 99.198 | 98.4978
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 4:05 | 0:25 | 4:30 | 106:33 | 4:30 | 4:30 | 99.3304 | 99.3304 | 106:33 | 106:33 | 98.6708 | 98.6708
19 | Hole-Alur | 1 | 1 | 12:25 | 105:35 | 3:15 | 0:30 | 3:45 | 113:25 | 16:10 | 16:10 | 99.442 | 97.5942 | 219:00 | 219:00 | 98.5851 | 97.268
20 | Savanur | 3 | 3 | 0:00 | 25:25 | 17:25 | 25:45 | 43:10 | 595:45 | 43:10 | 14:23 | 97.8588 | 97.8588 | 621:10 | 207:03 | 97.5227 | 97.417
21 | Shiggaon | 4 | 4 | 23:10 | 48:05 | 16:05 | 23:35 | 39:40 | 562:25 | 62:50 | 15:42 | 98.5243 | 97.6625 | 610:30 | 152:37 | 98.246 | 98.096
22 | Bankapur | 1 | 1 | 15:55 | 111:55 | 6:45 | 3:45 | 10:30 | 232:00 | 26:25 | 26:25 | 98.4375 | 96.0689 | 343:55 | 343:55 | 97.1058 | 95.7096
23 | Hangal | 2 | 2 | 0:50 | 101:30 | 29:55 | 6:30 | 36:25 | 477:35 | 37:15 | 18:38 | 97.2904 | 97.2284 | 579:05 | 289:32 | 97.0211 | 96.388
24 | Ranebennur | 11 | 11 | 6:26 | 133:24 | 22:25 | 11:40 | 34:05 | 1848:19 | 40:31 | 3:41 | 99.5389 | 99.4519 | 1981:43 | 180:09 | 97.9038 | 97.7525
25 | Halageri | 1 | 1 | 12:30 | 230:50 | 0:00 | 0:00 | 0:00 | 433:40 | 12:30 | 12:30 | 100 | 98.1399 | 664:30 | 664:30 | 94.59 | 91.7103
26 | Tuminakatti | 1 | 1 | 0:00 | 55:30 | 7:12 | 0:00 | 7:12 | 292:47 | 7:12 | 7:12 | 98.9286 | 98.9286 | 348:17 | 348:17 | 96.3475 | 95.6551
27 | Kahanderayanahalli | 1 | 1 | 5:15 | 15:49 | 3:20 | 2:00 | 5:20 | 415:10 | 10:35 | 10:35 | 99.2063 | 98.4251 | 430:59 | 430:59 | 94.8208 | 94.6235
28 | Rattihalli | 1 | 1 | 0:15 | 10:10 | 13:45 | 7:00 | 20:45 | 227:00 | 21:00 | 21:00 | 96.9122 | 96.875 | 237:10 | 237:10 | 97.1682 | 97.0413
29 | Hirekerur | 2 | 2 | 6:00 | 98:00 | 18:45 | 4:30 | 23:15 | 590:55 | 29:15 | 14:38 | 98.2701 | 97.8237 | 688:55 | 344:28 | 96.3141 | 95.7029
30 | Byadagi | 6 | 6 | 20:50 | 253:00 | 33:15 | 16:15 | 49:30 | 1825:35 | 70:20 | 11:43 | 98.7723 | 98.2556 | 2078:35 | 346:26 | 96.2043 | 95.6783
31 | Sirsi | 6 | 6 | 42:00 | 165:15 | 94:40 | 7:25 | 102:05 | 889:37 | 144:05 | 24:01 | 97.4682 | 96.4265 | 1054:52 | 175:49 | 98.1503 | 97.8067
32 | Yellapur | 3 | 3 | 8:00 | 316:51 | 8:05 | 1:45 | 9:50 | 195:40 | 17:50 | 5:57 | 99.5122 | 99.1154 | 512:31 | 170:50 | 99.1863 | 97.8688
33 | Mundagod | 2 | 2 | 0:40 | 41:18 | 10:50 | 2:05 | 12:55 | 568:26 | 13:35 | 6:48 | 99.0389 | 98.9893 | 609:44 | 304:52 | 96.4544 | 96.1968
34 | Siddapur | 2 | 2 | 37:10 | 110:14 | 15:35 | 9:25 | 25:00 | 296:05 | 62:10 | 31:05 | 98.1399 | 95.3745 | 406:19 | 203:10 | 98.1532 | 97.4656
35 | Dandeli | 8 | 8 | 1:24 | 94:40 | 16:14 | 45:29 | 61:43 | 1316:22 | 63:07 | 7:53 | 98.852 | 98.826 | 1411:02 | 176:23 | 97.9473 | 97.7997
36 | Haliyal | 3 | 3 | 0:00 | 18:56 | 10:25 | 1:53 | 12:18 | 359:30 | 12:18 | 4:06 | 99.3899 | 99.3899 | 378:26 | 126:09 | 98.5051 | 98.4263
37 | Ankola | 3 | 3 | 8:26 | 257:29 | 20:24 | 3:52 | 24:16 | 347:04 | 32:42 | 10:54 | 98.7963 | 98.378 | 604:33 | 201:31 | 98.5568 | 97.4861
38 | Kumta | 3 | 3 | 3:45 | 40:03 | 13:31 | 5:05 | 18:36 | 330:26 | 22:21 | 7:27 | 99.0774 | 98.8914 | 370:29 | 123:30 | 98.6259 | 98.4594
39 | Gokarna | 1 | 1 | 12:42 | 124:54 | 1:50 | 0:00 | 1:50 | 97:55 | 14:32 | 14:32 | 99.7272 | 97.8373 | 222:49 | 222:49 | 98.7785 | 97.2204
40 | Kasarkod | 1 | 1 | 16:28 | 241:43 | 2:49 | 2:56 | 5:45 | 172:18 | 22:13 | 22:13 | 99.1443 | 96.6939 | 414:01 | 414:01 | 97.8505 | 94.8351
41 | Honnavar | 3 | 3 | 3:45 | 75:24 | 15:33 | 3:18 | 18:51 | 477:18 | 22:36 | 7:32 | 99.065 | 98.879 | 552:42 | 184:14 | 98.0152 | 97.7017
42 | Murdeshwar | 4 | 4 | 22:44 | 126:52 | 18:41 | 1:58 | 20:39 | 780:03 | 43:23 | 10:51 | 99.2318 | 98.386 | 906:55 | 226:44 | 97.5672 | 97.1715
43 | Bhatkal | 3 | 3 | 28:15 | 276:14 | 12:03 | 2:02 | 14:05 | 334:21 | 42:20 | 14:07 | 99.3014 | 97.9001 | 610:35 | 203:32 | 98.6097 | 97.461
44 | Khanapur | 2 | 2 | 22:35 | 174:50 | 11:55 | 6:55 | 18:50 | 523:55 | 41:25 | 20:42 | 98.5987 | 96.9184 | 698:45 | 349:22 | 96.7321 | 95.6415
45 | Bailhongal | 3 | 3 | 0:00 | 67:52 | 49:50 | 9:30 | 59:20 | 1141:31 | 59:20 | 19:47 | 97.0569 | 97.0569 | 1209:23 | 403:08 | 95.2532 | 94.971
46 | Soundatti | 3 | 3 | 20:46 | 106:24 | 13:53 | 1:45 | 15:38 | 547:50 | 36:24 | 12:08 | 99.2245 | 98.1944 | 654:14 | 218:05 | 97.7219 | 97.2795
47 | Ramdurg | 2 | 2 | 6:58 | 88:36 | 9:42 | 2:10 | 11:52 | 280:51 | 18:50 | 9:25 | 99.1171 | 98.5987 | 369:27 | 184:43 | 98.2482 | 97.6955
48 | Gokak | 10 | 10 | 4:54 | 180:39 | 16:07 | 13:21 | 29:28 | 715:15 | 34:22 | 3:26 | 99.5615 | 99.4886 | 895:54 | 89:35 | 99.1077 | 98.8824
49 | Mudalagi | 2 | 2 | 0:00 | 37:25 | 21:55 | 0:40 | 22:35 | 355:35 | 22:35 | 11:18 | 98.3197 | 98.3197 | 393:00 | 196:30 | 97.782 | 97.5487
50 | Konnur | 1 | 1 | 0:00 | 4:20 | 8:30 | 3:20 | 11:50 | 243:50 | 11:50 | 11:50 | 98.2391 | 98.2391 | 248:10 | 248:10 | 96.9582 | 96.9041
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 16:35 | 4:25 | 21:00 | 358:16 | 21:00 | 21:00 | 96.875 | 96.875 | 358:16 | 358:16 | 95.5306 | 95.5306
52 | Kudachi | 1 | 1 | 0:00 | 12:40 | 6:10 | 1:15 | 7:25 | 421:55 | 7:25 | 7:25 | 98.8963 | 98.8963 | 434:35 | 434:35 | 94.7366 | 94.5786
53 | Athani | 7 | 7 | 25:11 | 271:52 | 61:48 | 25:43 | 87:31 | 1219:16 | 112:42 | 16:06 | 98.1395 | 97.6042 | 1491:08 | 213:01 | 97.8271 | 97.3426
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 2:35 | 4:35 | 7:10 | 202:00 | 7:10 | 3:35 | 99.4668 | 99.4668 | 202:00 | 101:00 | 98.74 | 98.74
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 26:05 | 68:35 | 94:40 | 931:23 | 94:40 | 18:56 | 97.1825 | 97.1825 | 931:23 | 186:17 | 97.6762 | 97.6762
56 | Sadalaga | 1 | 1 | 5:50 | 29:30 | 17:20 | 2:05 | 19:25 | 239:20 | 25:15 | 25:15 | 97.1106 | 96.2426 | 268:50 | 268:50 | 97.0143 | 96.6463
57 | Muddebihal | 2 | 2 | 0:00 | 74:05 | 20:45 | 4:15 | 25:00 | 615:30 | 25:00 | 12:30 | 98.1399 | 98.1399 | 689:35 | 344:48 | 96.1608 | 95.6987
58 | Talikoti | 1 | 1 | 1:20 | 60:20 | 19:00 | 2:25 | 21:25 | 201:10 | 22:45 | 22:45 | 96.813 | 96.6146 | 261:30 | 261:30 | 97.4904 | 96.7378
59 | B.Bagewadi | 1 | 1 | 1:44 | 28:35 | 4:42 | 0:37 | 5:19 | 88:20 | 7:03 | 7:03 | 99.2088 | 98.9509 | 116:55 | 116:55 | 98.898 | 98.5415
60 | Indi | 3 | 3 | 3:00 | 38:49 | 9:56 | 2:11 | 12:07 | 284:55 | 15:07 | 5:02 | 99.399 | 99.2502 | 323:44 | 107:55 | 98.8152 | 98.6538
61 | Sindagi | 2 | 2 | 11:50 | 128:00 | 18:25 | 2:30 | 20:55 | 361:55 | 32:45 | 16:23 | 98.4437 | 97.5632 | 489:55 | 244:57 | 97.7425 | 96.9441
62 | Guledgudda | 1 | 1 | 0:05 | 12:02 | 5:26 | 2:18 | 7:44 | 200:27 | 7:49 | 7:49 | 98.8492 | 98.8368 | 212:29 | 212:29 | 97.4994 | 97.3493
63 | Ilkal | 8 | 8 | 5:24 | 247:02 | 81:13 | 39:56 | 121:09 | 2520:40 | 126:33 | 15:49 | 97.7465 | 97.646 | 2767:42 | 345:58 | 96.0693 | 95.6841
64 | Kerur | 2 | 2 | 2:05 | 47:47 | 17:33 | 0:05 | 17:38 | 307:41 | 19:43 | 9:52 | 98.688 | 98.533 | 355:28 | 177:44 | 98.0808 | 97.7828
65 | Hungund | 4 | 4 | 4:08 | 128:22 | 23:14 | 14:02 | 37:16 | 858:38 | 41:24 | 10:21 | 98.6136 | 98.4598 | 987:00 | 246:45 | 97.3221 | 96.9218
66 | Gaddankeri | 3 | 3 | 3:08 | 93:57 | 28:50 | 9:40 | 38:30 | 682:01 | 41:38 | 13:53 | 98.0903 | 97.9349 | 775:58 | 258:39 | 97.1639 | 96.7733
67 | Rampur | 1 | 1 | 0:00 | 23:56 | 7:16 | 1:30 | 8:46 | 162:14 | 8:46 | 8:46 | 98.6954 | 98.6954 | 186:10 | 186:10 | 97.9761 | 97.6776
68 | Kaladagi | 2 | 2 | 0:36 | 44:27 | 8:21 | 6:42 | 15:03 | 374:21 | 15:39 | 7:50 | 98.8802 | 98.8356 | 418:48 | 209:24 | 97.665 | 97.3877
69 | Achanur | 1 | 1 | 0:00 | 16:03 | 38:30 | 4:00 | 42:30 | 412:35 | 42:30 | 42:30 | 93.6756 | 93.6756 | 428:38 | 428:38 | 94.853 | 94.6528
70 | Shirur | 1 | 1 | 4:06 | 75:35 | 0:24 | 2:00 | 2:24 | 233:54 | 6:30 | 6:30 | 99.6429 | 99.0327 | 309:29 | 309:29 | 97.0821 | 96.1392
71 | Badami | 1 | 1 | 1:56 | 29:04 | 4:07 | 3:15 | 7:22 | 212:20 | 9:18 | 9:18 | 98.9038 | 98.6161 | 241:24 | 241:24 | 97.3511 | 96.9885
72 | Kulageri | 1 | 1 | 0:55 | 18:30 | 3:20 | 1:05 | 4:25 | 67:04 | 5:20 | 5:20 | 99.3428 | 99.2063 | 85:34 | 85:34 | 99.1633 | 98.9326
73 | Jamkhandi | 6 | 6 | 2:30 | 160:05 | 93:55 | 8:00 | 101:55 | 946:45 | 104:25 | 17:24 | 97.4723 | 97.4103 | 1106:50 | 184:28 | 98.0315 | 97.6987
74 | Mahalingapur | 3 | 3 | 4:12 | 39:54 | 24:03 | 0:28 | 24:31 | 721:16 | 28:43 | 9:34 | 98.7839 | 98.5756 | 761:10 | 253:43 | 97.0007 | 96.8348
75 | Rabakavi | 2 | 2 | 2:40 | 54:30 | 6:35 | 2:10 | 8:45 | 183:35 | 11:25 | 5:42 | 99.349 | 99.1505 | 238:05 | 119:02 | 98.8549 | 98.5149
76 | Banahatti | 2 | 2 | 1:30 | 25:31 | 12:35 | 0:30 | 13:05 | 209:15 | 14:35 | 7:18 | 99.0265 | 98.9149 | 234:46 | 117:23 | 98.6948 | 98.5356
77 | Terdal | 2 | 2 | 3:00 | 43:30 | 11:50 | 3:20 | 15:10 | 514:05 | 18:10 | 9:05 | 98.8715 | 98.6483 | 557:35 | 278:48 | 96.7934 | 96.5221
78 | Mudhol | 4 | 4 | 4:10 | 45:58 | 34:12 | 0:53 | 35:05 | 596:14 | 39:15 | 9:49 | 98.6948 | 98.5398 | 642:12 | 160:33 | 98.1405 | 97.9971
79 | Bilagi | 1 | 1 | 2:45 | 40:10 | 4:50 | 1:25 | 6:15 | 164:33 | 9:00 | 9:00 | 99.0699 | 98.6607 | 204:43 | 204:43 | 97.9472 | 97.4461
80 | Lokapur | 2 | 2 | 0:00 | 12:20 | 34:35 | 4:30 | 39:05 | 625:45 | 39:05 | 19:32 | 97.092 | 97.092 | 638:05 | 319:02 | 96.0969 | 96.0199
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of March-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of March-2022 |  |  |  | Reliability for cumulative period from Apr-21 to March-2022
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 80 | 80 | 152:19 | 489:42 | 263:46 | 474:54 | 738:40 | 5963:32 | 890:59 | 11:08 | 98.759 | 98.5031 | 6453:14 | 80:40 | 99.149 | 99.0792
2 | Dharwad(R) | 14 | 14 | 0:00 | 364:42 | 153:34 | 151:10 | 304:44 | 4174:09 | 304:44 | 21:46 | 97.0744 | 97.0744 | 4538:51 | 324:12 | 96.5964 | 96.299
3 | Kundagol | 1 | 1 | 19:25 | 163:00 | 6:50 | 4:15 | 11:05 | 159:20 | 30:30 | 30:30 | 98.5103 | 95.9005 | 322:20 | 322:20 | 98.1811 | 96.3204
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 8:24 | 7:20 | 15:44 | 162:08 | 15:44 | 15:44 | 97.8853 | 97.8853 | 162:08 | 162:08 | 98.1492 | 98.1492
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 8:24 | 18:22 | 26:46 | 187:58 | 26:46 | 26:46 | 96.4023 | 96.4023 | 187:58 | 187:58 | 97.8543 | 97.8543
6 | Kalghatagi | 2 | 2 | 0:00 | 188:15 | 12:10 | 37:40 | 49:50 | 613:29 | 49:50 | 24:55 | 96.651 | 96.651 | 801:44 | 400:52 | 96.4984 | 95.4239
7 | Alnavar | 2 | 2 | 0:00 | 6:10 | 6:30 | 20:35 | 27:05 | 280:20 | 27:05 | 13:32 | 98.1799 | 98.1799 | 286:30 | 143:15 | 98.3999 | 98.3647
8 | Naragund | 2 | 2 | 6:40 | 98:40 | 22:35 | 9:00 | 31:35 | 386:30 | 38:15 | 19:08 | 97.8775 | 97.4294 | 485:10 | 242:35 | 97.7939 | 97.2308
9 | Shirahatti | 4 | 4 | 0:00 | 0:00 | 31:55 | 41:40 | 73:35 | 906:27 | 73:35 | 18:24 | 97.5274 | 97.5274 | 906:27 | 226:37 | 97.4131 | 97.4131
10 | Laxmeshwar | 4 | 4 | 0:00 | 0:00 | 43:02 | 17:12 | 60:14 | 831:46 | 60:14 | 15:03 | 97.976 | 97.976 | 831:46 | 207:56 | 97.6262 | 97.6262
11 | Naregal | 1 | 1 | 5:25 | 21:55 | 16:25 | 0:55 | 17:20 | 100:35 | 22:45 | 22:45 | 97.6703 | 96.9422 | 122:30 | 122:30 | 98.8518 | 98.6016
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 24:00 | 9:30 | 33:30 | 466:56 | 33:30 | 16:45 | 97.7487 | 97.7487 | 466:56 | 233:28 | 97.3349 | 97.3349
13 | Ron | 3 | 3 | 0:00 | 14:15 | 34:45 | 38:55 | 73:40 | 601:47 | 73:40 | 24:33 | 96.6995 | 96.6995 | 616:02 | 205:21 | 97.7101 | 97.6559
14 | Mundaragi | 3 | 3 | 0:00 | 0:00 | 41:15 | 18:00 | 59:15 | 476:40 | 59:15 | 19:45 | 97.3454 | 97.3454 | 476:40 | 158:53 | 98.1862 | 98.1862
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 26:29 | 10:06 | 36:35 | 395:59 | 36:35 | 36:35 | 95.0829 | 95.0829 | 395:59 | 395:59 | 95.4796 | 95.4796
16 | G.C.T.M | 1 | 1 | 12:20 | 73:25 | 4:35 | 1:50 | 6:25 | 157:50 | 18:45 | 18:45 | 99.1375 | 97.4798 | 231:15 | 231:15 | 98.1982 | 97.3602
17 | F.C.S.M | 2 | 2 | 21:10 | 133:25 | 5:50 | 1:00 | 6:50 | 135:25 | 28:00 | 14:00 | 99.5408 | 98.1183 | 268:50 | 134:25 | 99.2271 | 98.4656
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 25:00 | 2:40 | 27:40 | 134:13 | 27:40 | 27:40 | 96.2814 | 96.2814 | 134:13 | 134:13 | 98.4678 | 98.4678
19 | Hole-Alur | 1 | 1 | 5:05 | 110:40 | 2:20 | 0:15 | 2:35 | 116:00 | 7:40 | 7:40 | 99.6528 | 98.9695 | 226:40 | 226:40 | 98.6758 | 97.4125
20 | Savanur | 3 | 3 | 0:00 | 25:25 | 39:15 | 30:45 | 70:00 | 665:45 | 70:00 | 23:20 | 96.8638 | 96.8638 | 691:10 | 230:23 | 97.4667 | 97.37
21 | Shiggaon | 4 | 4 | 23:40 | 71:45 | 21:30 | 24:50 | 46:20 | 608:45 | 70:00 | 17:30 | 98.4431 | 97.6478 | 680:30 | 170:07 | 98.2627 | 98.0579
22 | Bankapur | 1 | 1 | 19:50 | 131:45 | 17:20 | 5:05 | 22:25 | 254:25 | 42:15 | 42:15 | 96.987 | 94.3212 | 386:10 | 386:10 | 97.0957 | 95.5917
23 | Hangal | 2 | 2 | 12:30 | 114:00 | 8:50 | 17:50 | 26:40 | 504:15 | 39:10 | 19:35 | 98.2079 | 97.3678 | 618:15 | 309:08 | 97.1219 | 96.4712
24 | Ranebennur | 12 | 12 | 15:09 | 148:33 | 86:59 | 29:32 | 116:31 | 1964:50 | 131:40 | 10:58 | 98.6949 | 98.5252 | 2113:23 | 176:07 | 98.1309 | 97.9896
25 | Halageri | 1 | 1 | 16:30 | 247:20 | 2:20 | 0:00 | 2:20 | 436:00 | 18:50 | 18:50 | 99.6864 | 97.4686 | 683:20 | 683:20 | 95.0228 | 92.1994
26 | Tuminakatti | 1 | 1 | 3:25 | 58:55 | 3:30 | 1:45 | 5:15 | 298:02 | 8:40 | 8:40 | 99.2944 | 98.8351 | 356:57 | 356:57 | 96.5978 | 95.9252
27 | Kahanderayanahalli | 1 | 1 | 7:20 | 23:09 | 8:05 | 6:20 | 14:25 | 429:35 | 21:45 | 21:45 | 98.0623 | 97.0766 | 452:44 | 452:44 | 95.0961 | 94.8318
28 | Rattihalli | 1 | 1 | 3:15 | 13:25 | 3:25 | 5:45 | 9:10 | 236:10 | 12:25 | 12:25 | 98.7679 | 98.3311 | 249:35 | 249:35 | 97.304 | 97.1509
29 | Hirekerur | 2 | 2 | 20:20 | 118:20 | 18:10 | 24:20 | 42:30 | 633:25 | 62:50 | 31:25 | 97.1438 | 95.7773 | 751:45 | 375:52 | 96.3846 | 95.7092
30 | Byadagi | 6 | 6 | 54:20 | 307:20 | 61:45 | 26:15 | 88:00 | 1913:35 | 142:20 | 23:43 | 98.0287 | 96.8115 | 2220:55 | 370:09 | 96.3592 | 95.7745
31 | Sirsi | 6 | 6 | 1:30 | 166:45 | 39:55 | 33:00 | 72:55 | 962:32 | 74:25 | 12:24 | 98.3666 | 98.333 | 1129:17 | 188:13 | 98.1687 | 97.8514
32 | Yellapur | 3 | 3 | 8:10 | 325:01 | 5:30 | 3:50 | 9:20 | 205:00 | 17:30 | 5:50 | 99.5818 | 99.2159 | 530:01 | 176:40 | 99.2199 | 97.9832
33 | Mundagod | 2 | 2 | 0:48 | 42:06 | 5:50 | 13:15 | 19:05 | 587:31 | 19:53 | 9:56 | 98.7175 | 98.6638 | 629:37 | 314:48 | 96.6466 | 96.4063
34 | Siddapur | 2 | 2 | 3:50 | 114:04 | 3:00 | 7:45 | 10:45 | 306:50 | 14:35 | 7:18 | 99.2776 | 99.0199 | 420:54 | 210:27 | 98.2487 | 97.5976
35 | Dandeli | 8 | 8 | 16:32 | 111:12 | 25:50 | 74:40 | 100:30 | 1416:52 | 117:02 | 14:38 | 98.3115 | 98.0337 | 1528:04 | 191:01 | 97.9782 | 97.8195
36 | Haliyal | 3 | 3 | 2:22 | 21:18 | 11:10 | 17:58 | 29:08 | 388:38 | 31:30 | 10:30 | 98.6947 | 98.5887 | 409:56 | 136:39 | 98.5212 | 98.4401
37 | Ankola | 3 | 3 | 19:14 | 276:43 | 6:45 | 3:53 | 10:38 | 357:42 | 29:52 | 9:57 | 99.5236 | 98.6619 | 634:25 | 211:28 | 98.6389 | 97.5859
38 | Kumta | 3 | 3 | 14:54 | 54:57 | 12:06 | 6:25 | 18:31 | 348:57 | 33:25 | 11:08 | 99.1704 | 98.5028 | 403:54 | 134:38 | 98.6722 | 98.4631
39 | Gokarna | 1 | 1 | 8:35 | 133:29 | 2:05 | 0:00 | 2:05 | 100:00 | 10:40 | 10:40 | 99.72 | 98.5663 | 233:29 | 233:29 | 98.8584 | 97.3347
40 | Kasarkod | 1 | 1 | 11:21 | 253:04 | 10:12 | 5:01 | 15:13 | 187:31 | 26:34 | 26:34 | 97.9547 | 96.4292 | 440:35 | 440:35 | 97.8594 | 94.9705
41 | Honnavar | 3 | 3 | 25:33 | 100:57 | 11:37 | 6:23 | 18:00 | 495:18 | 43:33 | 14:31 | 99.1935 | 98.0488 | 596:15 | 198:45 | 98.1153 | 97.7312
42 | Murdeshwar | 4 | 4 | 34:20 | 161:12 | 21:29 | 7:29 | 28:58 | 809:01 | 63:18 | 15:50 | 99.0267 | 97.873 | 970:13 | 242:33 | 97.6912 | 97.2311
43 | Bhatkal | 3 | 3 | 14:09 | 290:23 | 16:42 | 9:04 | 25:46 | 360:07 | 39:55 | 13:18 | 98.8456 | 98.2116 | 650:30 | 216:50 | 98.6297 | 97.5247
44 | Khanapur | 2 | 2 | 17:10 | 192:00 | 11:20 | 8:25 | 19:45 | 543:40 | 36:55 | 18:28 | 98.6727 | 97.519 | 735:40 | 367:50 | 96.8969 | 95.801
45 | Bailhongal | 3 | 3 | 15:00 | 82:52 | 64:45 | 21:10 | 85:55 | 1227:26 | 100:55 | 33:38 | 96.1507 | 95.4786 | 1310:18 | 436:46 | 95.3294 | 95.0141
46 | Soundatti | 3 | 3 | 5:38 | 112:02 | 13:33 | 5:45 | 19:18 | 567:08 | 24:56 | 8:19 | 99.1353 | 98.8829 | 679:10 | 226:23 | 97.842 | 97.4157
47 | Ramdurg | 2 | 2 | 11:08 | 99:44 | 22:26 | 5:04 | 27:30 | 308:21 | 38:38 | 19:19 | 98.1519 | 97.4037 | 408:05 | 204:02 | 98.24 | 97.6708
48 | Gokak | 10 | 10 | 27:27 | 208:06 | 5:26 | 14:08 | 19:34 | 734:49 | 47:01 | 4:42 | 99.737 | 99.3681 | 942:55 | 94:18 | 99.1612 | 98.9236
49 | Mudalagi | 2 | 2 | 7:20 | 44:45 | 49:25 | 9:40 | 59:05 | 414:40 | 66:25 | 33:12 | 96.0293 | 95.5365 | 459:25 | 229:42 | 97.6332 | 97.3778
50 | Konnur | 1 | 1 | 1:20 | 5:40 | 11:35 | 1:25 | 13:00 | 256:50 | 14:20 | 14:20 | 98.2527 | 98.0735 | 262:30 | 262:30 | 97.0681 | 97.0034
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 28:00 | 6:15 | 34:15 | 392:31 | 34:15 | 34:15 | 95.3965 | 95.3965 | 392:31 | 392:31 | 95.5192 | 95.5192
52 | Kudachi | 1 | 1 | 1:50 | 14:30 | 27:20 | 2:05 | 29:25 | 451:20 | 31:15 | 31:15 | 96.0461 | 95.7997 | 465:50 | 465:50 | 94.8478 | 94.6823
53 | Athani | 7 | 7 | 0:00 | 271:52 | 117:29 | 35:02 | 152:31 | 1371:47 | 152:31 | 21:47 | 97.0715 | 97.0715 | 1643:39 | 234:48 | 97.7629 | 97.3196
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 22:20 | 20:10 | 42:30 | 244:30 | 42:30 | 21:15 | 97.1438 | 97.1438 | 244:30 | 122:15 | 98.6045 | 98.6045
55 | Nippani | 5 | 5 | 0:00 | 0:00 | 58:45 | 40:25 | 99:10 | 1030:33 | 99:10 | 19:50 | 97.3342 | 97.3342 | 1030:33 | 206:07 | 97.6471 | 97.6471
56 | Sadalaga | 1 | 1 | 1:35 | 31:05 | 8:50 | 2:50 | 11:40 | 251:00 | 13:15 | 13:15 | 98.4319 | 98.2191 | 282:05 | 282:05 | 97.1347 | 96.7799
57 | Muddebihal | 2 | 2 | 0:15 | 74:20 | 51:25 | 4:25 | 55:50 | 671:20 | 56:05 | 28:02 | 96.2478 | 96.231 | 745:40 | 372:50 | 96.1682 | 95.7439
58 | Talikoti | 1 | 1 | 3:00 | 63:20 | 29:25 | 5:40 | 35:05 | 236:15 | 38:05 | 38:05 | 95.2845 | 94.8813 | 299:35 | 299:35 | 97.3031 | 96.5801
59 | B.Bagewadi | 1 | 1 | 1:58 | 30:33 | 5:10 | 4:47 | 9:57 | 98:17 | 11:55 | 11:55 | 98.6626 | 98.3983 | 128:50 | 128:50 | 98.878 | 98.5293
60 | Indi | 3 | 3 | 0:04 | 38:53 | 30:23 | 2:14 | 32:37 | 317:32 | 32:41 | 10:54 | 98.5387 | 98.5357 | 356:25 | 118:48 | 98.7917 | 98.6438
61 | Sindagi | 2 | 2 | 1:00 | 129:00 | 17:40 | 3:50 | 21:30 | 383:25 | 22:30 | 11:15 | 98.5551 | 98.4879 | 512:25 | 256:12 | 97.8115 | 97.0752
62 | Guledgudda | 1 | 1 | 1:20 | 13:22 | 11:35 | 4:25 | 16:00 | 216:27 | 17:20 | 17:20 | 97.8495 | 97.6703 | 229:49 | 229:49 | 97.5291 | 97.3765
63 | Ilkal | 8 | 8 | 27:25 | 274:27 | 41:11 | 58:50 | 100:01 | 2620:41 | 127:26 | 15:56 | 98.3196 | 97.859 | 2895:08 | 361:54 | 96.2604 | 95.8688
64 | Kerur | 2 | 2 | 0:00 | 47:47 | 32:33 | 12:31 | 45:04 | 352:45 | 45:04 | 22:32 | 96.9713 | 96.9713 | 400:32 | 200:16 | 97.9866 | 97.7139
65 | Hungund | 4 | 4 | 13:44 | 142:06 | 67:15 | 39:18 | 106:33 | 965:11 | 120:17 | 30:04 | 96.4197 | 95.9582 | 1107:17 | 276:49 | 97.2455 | 96.8399
66 | Gaddankeri | 3 | 3 | 31:27 | 125:24 | 25:59 | 3:59 | 29:58 | 711:59 | 61:25 | 20:28 | 98.6574 | 97.2484 | 837:23 | 279:08 | 97.2908 | 96.8136
67 | Rampur | 1 | 1 | 3:27 | 27:23 | 7:15 | 3:12 | 10:27 | 172:41 | 13:54 | 13:54 | 98.5954 | 98.1317 | 200:04 | 200:04 | 98.0287 | 97.7161
68 | Kaladagi | 2 | 2 | 35:09 | 79:36 | 16:42 | 19:42 | 36:24 | 410:45 | 71:33 | 35:46 | 97.5538 | 95.1915 | 490:21 | 245:10 | 97.6555 | 97.2012
69 | Achanur | 1 | 1 | 10:18 | 26:21 | 12:03 | 5:06 | 17:09 | 429:44 | 27:27 | 27:27 | 97.6949 | 96.3105 | 456:05 | 456:05 | 95.0944 | 94.7936
70 | Shirur | 1 | 1 | 11:30 | 87:05 | 2:30 | 4:46 | 7:16 | 241:10 | 18:46 | 18:46 | 99.0233 | 97.4776 | 328:15 | 328:15 | 97.247 | 96.2529
71 | Badami | 1 | 1 | 4:20 | 33:24 | 13:56 | 5:38 | 19:34 | 231:54 | 23:54 | 23:54 | 97.3701 | 96.7876 | 265:18 | 265:18 | 97.3527 | 96.9715
72 | Kulageri | 1 | 1 | 0:35 | 19:05 | 5:45 | 2:15 | 8:00 | 75:04 | 8:35 | 8:35 | 98.9247 | 98.8463 | 94:09 | 94:09 | 99.1431 | 98.9252
73 | Jamkhandi | 6 | 6 | 7:30 | 167:35 | 34:20 | 9:30 | 43:50 | 990:35 | 51:20 | 8:33 | 99.0181 | 98.8501 | 1158:10 | 193:02 | 98.1153 | 97.7965
74 | Mahalingapur | 3 | 3 | 4:50 | 44:44 | 43:41 | 7:32 | 51:13 | 772:29 | 56:03 | 18:41 | 97.7053 | 97.4888 | 817:13 | 272:24 | 97.0606 | 96.8903
75 | Rabakavi | 2 | 2 | 4:50 | 59:20 | 8:20 | 3:15 | 11:35 | 195:10 | 16:25 | 8:12 | 99.2216 | 98.8967 | 254:30 | 127:15 | 98.886 | 98.5474
76 | Banahatti | 2 | 2 | 3:10 | 28:41 | 6:45 | 1:10 | 7:55 | 217:10 | 11:05 | 5:32 | 99.468 | 99.2552 | 245:51 | 122:56 | 98.7605 | 98.5967
77 | Terdal | 2 | 2 | 4:15 | 47:45 | 48:00 | 2:40 | 50:40 | 564:45 | 54:55 | 27:28 | 96.595 | 96.3094 | 612:30 | 306:15 | 96.7765 | 96.504
78 | Mudhol | 4 | 4 | 7:07 | 53:05 | 43:29 | 5:32 | 49:01 | 645:15 | 56:08 | 14:02 | 98.3529 | 98.1138 | 698:20 | 174:35 | 98.1585 | 98.007
79 | Bilagi | 1 | 1 | 4:25 | 44:35 | 4:05 | 1:05 | 5:10 | 169:43 | 9:35 | 9:35 | 99.3056 | 98.7119 | 214:18 | 214:18 | 98.0626 | 97.5537
80 | Lokapur | 2 | 2 | 0:15 | 12:35 | 49:00 | 13:25 | 62:25 | 688:10 | 62:40 | 31:20 | 95.8053 | 95.7885 | 700:45 | 350:22 | 96.0721 | 96.0003
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]

## RURAL (Incl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2021 |  |  |  | Reliability for cumulative period from Apr-21 to Apr-21
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 585:45 | 585:45 | 5554:28 | 1642:49 | 7197:17 | 7197:17 | 7783:02 | 172:57 | 77.7862 | 75.9783 | 7783:02 | 172:57 | 77.7862 | 75.9783
2 | Dharwad Rural | 82 | 82 | 317:48 | 317:48 | 15560:04 | 3818:42 | 19378:46 | 19378:46 | 19696:34 | 240:12 | 67.1769 | 66.6386 | 19696:34 | 240:12 | 67.1769 | 66.6386
3 | Gadag | 94 | 94 | 64:50 | 64:50 | 18787:09 | 2671:07 | 21458:16 | 21458:16 | 21523:06 | 228:58 | 68.2945 | 68.1987 | 21523:06 | 228:58 | 68.2945 | 68.1987
4 | Ron | 53 | 53 | 326:45 | 326:45 | 12741:16 | 1064:51 | 13806:07 | 13806:07 | 14132:52 | 266:39 | 63.8204 | 62.9642 | 14132:52 | 266:39 | 63.8204 | 62.9642
5 | Haveri | 197 | 197 | 2306:56 | 2306:56 | 2377.6236 | 8476:46 | 2730.8222 | 2730.8222 | 2826.9444 | 344:24 | 53.7932 | 52.1668 | 2826.9444 | 344:24 | 53.7932 | 52.1668
6 | Ranebennur | 182 | 182 | 1162:15 | 1162:15 | 2360.775 | 6907:59 | 2648.6076 | 2648.6076 | 2697.0347 | 355:39 | 51.4907 | 50.6038 | 2697.0347 | 355:39 | 51.4907 | 50.6038
7 | Sirsi | 53 | 53 | 368:08 | 368:08 | 643:19 | 2016:24 | 2659:43 | 2659:43 | 3027:51 | 57:08 | 93.0301 | 92.0654 | 3027:51 | 57:08 | 93.0301 | 92.0654
8 | Dandeli | 22 | 22 | 87:36 | 87:36 | 291:20 | 437:31 | 728:51 | 728:51 | 816:27 | 37:07 | 95.3987 | 94.8456 | 816:27 | 37:07 | 95.3987 | 94.8456
9 | Karwar | 30 | 30 | 437:29 | 437:29 | 352:54 | 1336:01 | 1688:55 | 1688:55 | 2126:24 | 70:53 | 92.1809 | 90.1556 | 2126:24 | 70:53 | 92.1809 | 90.1556
10 | Honnavar | 40 | 40 | 373:59 | 373:59 | 416:55 | 558:15 | 975:10 | 975:10 | 1349:09 | 33:44 | 96.614 | 95.3155 | 1349:09 | 33:44 | 96.614 | 95.3155
11 | Belagavi | 138 | 138 | 379:44 | 379:44 | 1043.2799 | 2574:19 | 1150.5431 | 1150.5431 | 1166.3653 | 202:51 | 72.2091 | 71.8269 | 1166.3653 | 202:51 | 72.2091 | 71.8269
12 | Bailhongal | 191 | 191 | 2479:50 | 2479:50 | 1745.8528 | 3473:45 | 1890.5924 | 1890.5924 | 1993.9187 | 250:33 | 67.0054 | 65.2021 | 1993.9187 | 250:33 | 67.0054 | 65.2021
13 | Ramdurg | 76 | 76 | 682:35 | 682:35 | 23073:23 | 2266:12 | 1055.816 | 1055.816 | 1084.2569 | 342:24 | 53.6923 | 52.4449 | 1084.2569 | 342:24 | 53.6923 | 52.4449
14 | Ghataprabha | 160 | 160 | 248:53 | 248:53 | 1858.7028 | 1742:10 | 1931.2931 | 1931.2931 | 1941.6632 | 291:15 | 59.7647 | 59.5487 | 1941.6632 | 291:15 | 59.7647 | 59.5487
15 | Raibag | 169 | 169 | 548:16 | 548:16 | 2090.8139 | 1392:55 | 2148.8521 | 2148.8521 | 2171.6965 | 308:24 | 57.6163 | 57.1657 | 2171.6965 | 308:24 | 57.6163 | 57.1657
16 | Athani | 192 | 192 | 408:19 | 408:19 | 1745.2937 | 1745:05 | 1818.0056 | 1818.0056 | 1835.0187 | 229:23 | 68.4374 | 68.142 | 1835.0187 | 229:23 | 68.4374 | 68.142
17 | Chikkodi | 189 | 189 | 409:48 | 409:48 | 2203.7743 | 2237:39 | 2297.0097 | 2297.0097 | 2314.0847 | 293:51 | 59.4884 | 59.1872 | 2314.0847 | 293:51 | 59.4884 | 59.1872
18 | Vijayapur | 159 | 159 | 285:24 | 285:24 | 1990.0132 | 2504:08 | 2094.3521 | 2094.3521 | 2106.2438 | 317:55 | 56.0932 | 55.8439 | 2106.2438 | 317:55 | 56.0932 | 55.8439
19 | Indi | 249 | 249 | 1627:38 | 1627:38 | 3035.5813 | 4511:14 | 3223.5493 | 3223.5493 | 3291.3674 | 317:14 | 56.8467 | 55.9389 | 3291.3674 | 317:14 | 56.8467 | 55.9389
20 | B.Bagewadi | 138 | 138 | 696:55 | 696:55 | 1512.1236 | 2122:09 | 1600.5465 | 1600.5465 | 1629.5847 | 283:24 | 61.3395 | 60.6381 | 1629.5847 | 283:24 | 61.3395 | 60.6381
21 | Bagalkot | 185 | 185 | 926:37 | 926:37 | 2085.0819 | 3887:48 | 2247.0736 | 2247.0736 | 2285.6826 | 296:31 | 59.5122 | 58.8165 | 2285.6826 | 296:31 | 59.5122 | 58.8165
22 | Jamkhandi | 207 | 207 | 539:52 | 539:52 | 2697.3861 | 1261:30 | 2749.9486 | 2749.9486 | 2772.4431 | 321:27 | 55.7174 | 55.3552 | 2772.4431 | 321:27 | 55.7174 | 55.3552
23 | Mudhol | 192 | 192 | 599:35 | 599:35 | 2547.4257 | 1858:22 | 2624.8576 | 2624.8576 | 2649.8403 | 331:14 | 54.4296 | 53.9958 | 2649.8403 | 331:14 | 54.4296 | 53.9958
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2021 |  |  |  | Reliability for cumulative period from Apr-21 to May-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 345:25 | 931:10 | 4495:33 | 2416:31 | 6912:04 | 14109:21 | 7257:29 | 161:17 | 79.3546 | 78.3229 | 15040:31 | 334:14 | 78.5833 | 77.1698
2 | Dharwad Rural | 82 | 82 | 332:05 | 649:53 | 14567:51 | 5334:33 | 19902:24 | 1636.7153 | 20234:29 | 246:46 | 67.3774 | 66.8331 | 1663.7937 | 486:58 | 67.2788 | 66.7374
3 | Gadag | 96 | 96 | 209:06 | 273:56 | 17489:40 | 4432:54 | 21922:34 | 1807.5347 | 22131:40 | 230:32 | 69.3064 | 69.0137 | 1818.9486 | 454:44 | 69.1336 | 68.9387
4 | Ron | 54 | 54 | 194:07 | 520:52 | 12999:57 | 1905:37 | 14905:34 | 1196.3201 | 15099:41 | 279:37 | 62.8993 | 62.4162 | 1218.0229 | 541:21 | 63.6818 | 63.023
5 | Haveri | 197 | 197 | 2616:54 | 4923:50 | 2242.8437 | 17554:29 | 2974.2806 | 5705.1028 | 3083.3181 | 375:38 | 51.2972 | 49.5117 | 5910.2625 | 720:02 | 52.5247 | 50.8175
6 | Ranebennur | 182 | 182 | 1564:24 | 2726:39 | 2300.1451 | 12856:57 | 2835.8514 | 5484.459 | 2901.0347 | 382:33 | 49.7368 | 48.5814 | 5598.0694 | 738:12 | 50.5994 | 49.576
7 | Sirsi | 54 | 54 | 823:35 | 1191:43 | 785:34 | 3103:34 | 3889:08 | 6548:51 | 4712:43 | 87:16 | 90.3198 | 88.2698 | 7740:34 | 143:21 | 91.7162 | 90.2088
8 | Dandeli | 22 | 22 | 89:01 | 176:37 | 217:38 | 512:45 | 730:23 | 1459:14 | 819:24 | 37:15 | 95.5377 | 94.9939 | 1635:51 | 74:21 | 95.4693 | 94.921
9 | Karwar | 30 | 30 | 591:52 | 1029:21 | 819:00 | 1479:16 | 2298:16 | 3987:11 | 2890:08 | 96:20 | 89.7031 | 87.0514 | 5016:32 | 167:13 | 90.9217 | 88.578
10 | Honnavar | 40 | 40 | 904:45 | 1278:44 | 753:35 | 1417:50 | 2171:25 | 3146:35 | 3076:10 | 76:54 | 92.7036 | 89.6634 | 4425:19 | 110:38 | 94.6267 | 92.4431
11 | Belagavi | 139 | 139 | 537:31 | 917:15 | 19091:54 | 4483:06 | 23575:00 | 2132.8347 | 1004.6882 | 173:28 | 77.2037 | 76.684 | 2171.0535 | 374:51 | 74.8457 | 74.3949
12 | Bailhongal | 192 | 192 | 1911:22 | 4391:12 | 1722.1674 | 9036:49 | 2098.7014 | 3989.2937 | 2178.3417 | 272:18 | 64.7396 | 63.4015 | 4172.2604 | 521:32 | 65.9384 | 64.3762
13 | Ramdurg | 76 | 76 | 296:09 | 978:44 | 23346:07 | 3163:15 | 1104.5569 | 2160.3729 | 1116.8965 | 352:42 | 53.1173 | 52.5935 | 2201.1535 | 695:06 | 53.4001 | 52.5204
14 | Ghataprabha | 161 | 161 | 234:39 | 483:32 | 1762.6014 | 3548:34 | 1910.4583 | 3841.7514 | 1920.2354 | 286:15 | 61.7219 | 61.526 | 3861.8986 | 575:41 | 60.8823 | 60.6771
15 | Raibag | 176 | 176 | 403:40 | 951:56 | 1833.3431 | 2628:37 | 1942.8687 | 4091.7208 | 1959.6882 | 267:14 | 64.3902 | 64.082 | 4131.3847 | 563:22 | 61.8878 | 61.5184
16 | Athani | 194 | 194 | 1060:50 | 1469:09 | 1646.6417 | 2769:08 | 1762.0222 | 3580.0278 | 1806.2236 | 223:27 | 70.7013 | 69.9664 | 3641.2424 | 450:28 | 69.7479 | 69.2307
17 | Chikkodi | 190 | 190 | 860:20 | 1270:08 | 2109.0063 | 3240:56 | 2244.0451 | 4541.0549 | 2279.8924 | 287:59 | 61.9008 | 61.2922 | 4593.9771 | 580:18 | 60.8192 | 60.3626
18 | Vijayapur | 159 | 159 | 193:43 | 479:07 | 1817.5951 | 4837:01 | 2019.1375 | 4113.4896 | 2027.209 | 306:00 | 59.0356 | 58.8718 | 4133.4528 | 623:55 | 57.5885 | 57.3827
19 | Indi | 254 | 254 | 1265:07 | 2892:45 | 3059.1694 | 6792:26 | 3342.1875 | 6565.7368 | 3394.9007 | 320:47 | 57.5541 | 56.8847 | 6686.2681 | 631:46 | 57.624 | 56.8461
20 | B.Bagewadi | 138 | 138 | 408:09 | 1105:04 | 1519.2889 | 4411:40 | 1703.1083 | 3303.6549 | 1720.1146 | 299:09 | 60.1891 | 59.7916 | 3349.6993 | 582:33 | 60.7549 | 60.2079
21 | Bagalkot | 185 | 185 | 975:40 | 1902:17 | 1884.8472 | 8155:52 | 2224.675 | 4471.7486 | 2265.3278 | 293:53 | 61.2088 | 60.5 | 4551.0104 | 590:24 | 60.3744 | 59.672
22 | Jamkhandi | 207 | 207 | 321:57 | 861:49 | 2552.1354 | 2202:10 | 2643.8924 | 5393.841 | 2657.3069 | 308:06 | 58.7986 | 58.5896 | 5429.75 | 629:32 | 57.2833 | 56.9989
23 | Mudhol | 192 | 192 | 320:55 | 920:30 | 2673.3382 | 2845:01 | 2791.8806 | 5416.7382 | 2805.2521 | 350:39 | 53.0934 | 52.8687 | 5455.0924 | 681:53 | 53.7505 | 53.4231
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2021 |  |  |  | Reliability for cumulative period from Apr-21 to June-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 95:05 | 1026:15 | 4752:01 | 2152:30 | 6904:31 | 21013:52 | 6999:36 | 155:33 | 78.6898 | 78.3963 | 22040:07 | 489:47 | 78.6184 | 77.5742
2 | Dharwad Rural | 81 | 81 | 110:32 | 760:25 | 14638:41 | 3486:55 | 18125:36 | 2391.9486 | 18236:08 | 225:08 | 68.9204 | 68.7309 | 2423.6326 | 718:07 | 67.5492 | 67.1194
3 | Gadag | 98 | 98 | 52:25 | 326:21 | 15756:50 | 3470:18 | 19227:08 | 2608.6653 | 19279:33 | 196:44 | 72.7507 | 72.6764 | 2622.2632 | 642:11 | 70.7483 | 70.5958
4 | Ron | 54 | 54 | 293:05 | 813:57 | 11230:45 | 1140:30 | 12371:15 | 1711.7889 | 12664:20 | 234:31 | 68.1809 | 67.4271 | 1745.7035 | 775:52 | 65.1651 | 64.4749
5 | Haveri | 196 | 196 | 1351:53 | 6275:43 | 2094.0514 | 17410:54 | 2819.5056 | 8524.6083 | 2875.834 | 352:09 | 52.0492 | 51.0913 | 8786.0965 | 1075:51 | 52.2056 | 50.7395
6 | Ranebennur | 182 | 182 | 542:50 | 3269:29 | 2274.1194 | 10194:56 | 2698.9083 | 8183.3674 | 2721.5264 | 358:53 | 50.5694 | 50.1552 | 8319.5958 | 1097:05 | 50.5895 | 49.767
7 | Sirsi | 54 | 54 | 737:16 | 1928:59 | 1026:00 | 3492:24 | 4518:24 | 11067:15 | 5255:40 | 97:20 | 88.3786 | 86.4823 | 12996:14 | 240:40 | 90.6159 | 88.9803
8 | Dandeli | 22 | 22 | 345:38 | 522:15 | 282:41 | 645:37 | 928:18 | 2387:32 | 1273:56 | 57:54 | 94.1395 | 91.9575 | 2909:47 | 132:16 | 95.0309 | 93.944
9 | Karwar | 30 | 30 | 474:58 | 1504:19 | 468:19 | 633:22 | 1101:41 | 5088:52 | 1576:39 | 52:33 | 94.8996 | 92.7007 | 6593:11 | 219:46 | 92.2331 | 89.9371
10 | Honnavar | 40 | 40 | 524:11 | 1802:55 | 817:25 | 1357:17 | 2174:42 | 5321:17 | 2698:53 | 67:28 | 92.449 | 90.6289 | 7124:12 | 178:06 | 93.9088 | 91.845
11 | Belagavi | 139 | 139 | 254:31 | 1171:46 | 14899:51 | 3390:10 | 18290:01 | 2894.9187 | 18544:32 | 133:25 | 81.7246 | 81.4703 | 2943.7424 | 508:16 | 77.1135 | 76.7275
12 | Bailhongal | 192 | 192 | 1335:25 | 5726:37 | 1589.4125 | 7985:52 | 1922.1569 | 5911.4507 | 1977.7993 | 247:13 | 66.6292 | 65.6632 | 6150.0597 | 768:45 | 66.1661 | 64.8005
13 | Ramdurg | 76 | 76 | 359:00 | 1337:44 | 22255:56 | 3460:44 | 1071.5278 | 3231.9007 | 1086.4861 | 343:06 | 53.0032 | 52.3471 | 3287.6396 | 1038:12 | 53.2692 | 52.4633
14 | Ghataprabha | 161 | 161 | 173:24 | 656:56 | 1558.9778 | 2700:41 | 1671.5063 | 5513.2576 | 1678.7313 | 250:15 | 65.3932 | 65.2437 | 5540.6299 | 825:56 | 62.3694 | 62.1826
15 | Raibag | 176 | 176 | 289:54 | 1241:50 | 1599.2944 | 1692:24 | 1669.8111 | 5761.5319 | 1681.8903 | 229:21 | 68.3748 | 68.146 | 5813.275 | 792:43 | 64.0264 | 63.7033
16 | Athani | 194 | 194 | 667:32 | 2136:41 | 1438.5007 | 1890:56 | 1517.2896 | 5097.3174 | 1545.1035 | 191:09 | 73.9297 | 73.4518 | 5186.3458 | 641:37 | 71.1266 | 70.6223
17 | Chikkodi | 190 | 190 | 266:35 | 1536:43 | 1888.2528 | 2326:00 | 1985.1694 | 6526.2243 | 1996.2771 | 252:10 | 65.1725 | 64.9776 | 6590.2542 | 832:27 | 62.2543 | 61.884
18 | Vijayapur | 166 | 166 | 354:16 | 833:23 | 1600.4437 | 6059:39 | 1852.9292 | 5966.4187 | 1867.6903 | 270:02 | 62.7926 | 62.4962 | 6001.1431 | 867:38 | 60.503 | 60.2731
19 | Indi | 254 | 254 | 1118:39 | 4011:24 | 2558.0139 | 9719:14 | 2962.9819 | 9528.7188 | 3009.5924 | 284:22 | 61.1157 | 60.504 | 9695.8604 | 916:09 | 58.7751 | 58.052
20 | B.Bagewadi | 139 | 139 | 1367:18 | 2472:22 | 1387.7729 | 4805:03 | 1587.9833 | 4891.6382 | 1644.9542 | 284:01 | 61.9189 | 60.5527 | 4994.6535 | 862:23 | 61.3279 | 60.5135
21 | Bagalkot | 185 | 185 | 899:28 | 2801:45 | 1626.9167 | 8262:16 | 1971.1778 | 6442.9264 | 2008.6556 | 260:35 | 64.4833 | 63.808 | 6559.666 | 850:59 | 61.729 | 61.0355
22 | Jamkhandi | 207 | 207 | 450:58 | 1312:47 | 2321.2146 | 1826:03 | 2397.3 | 7791.141 | 2416.0903 | 280:08 | 61.3961 | 61.0936 | 7845.8403 | 909:40 | 58.6392 | 58.3488
23 | Mudhol | 192 | 192 | 210:43 | 1131:13 | 2585.6097 | 3526:57 | 2732.566 | 8149.3042 | 2741.3458 | 342:40 | 52.5596 | 52.4072 | 8196.4382 | 1024:33 | 53.3579 | 53.0882
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of July-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2021 |  |  |  | Reliability for cumulative period from Apr-21 to July-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 93:25 | 1119:40 | 4649:28 | 2251:22 | 6900:50 | 1163.1125 | 6994:15 | 155:26 | 79.3882 | 79.1092 | 1209.7653 | 645:12 | 78.814 | 77.9642
2 | Dharwad Rural | 81 | 81 | 95:04 | 855:29 | 15371:04 | 3664:06 | 19035:10 | 3185.0806 | 19130:14 | 236:11 | 68.4137 | 68.256 | 3220.7257 | 954:17 | 67.7689 | 67.4082
3 | Gadag | 98 | 98 | 83:10 | 409:31 | 16048:33 | 3181:16 | 19229:49 | 3409.9076 | 19312:59 | 197:04 | 73.626 | 73.5119 | 3426.9708 | 839:15 | 71.4795 | 71.3368
4 | Ron | 54 | 54 | 259:27 | 1073:24 | 10915:35 | 1173:26 | 12089:01 | 2215.4979 | 12348:28 | 228:41 | 69.9099 | 69.2641 | 2260.2229 | 1004:33 | 66.3707 | 65.6918
5 | Haveri | 198 | 198 | 671:52 | 6947:35 | 2262.9097 | 14591:25 | 2870.8854 | 11395.4937 | 2898.8799 | 351:23 | 53.2277 | 52.7716 | 11684.9764 | 1416:22 | 52.8254 | 51.627
6 | Ranebennur | 182 | 182 | 692:10 | 3961:39 | 2404.4972 | 9817:44 | 2813.5694 | 10996.9368 | 2842.4097 | 374:49 | 50.1317 | 49.6205 | 11162.0056 | 1471:55 | 50.4732 | 49.7298
7 | Sirsi | 54 | 54 | 362:05 | 2291:04 | 577:24 | 2910:38 | 3488:02 | 14555:17 | 3850:07 | 71:18 | 91.3181 | 90.4169 | 16846:21 | 311:58 | 90.7943 | 89.3453
8 | Dandeli | 22 | 22 | 129:20 | 651:35 | 364:49 | 837:17 | 1202:06 | 3589:38 | 1331:26 | 60:31 | 92.6558 | 91.8656 | 4241:13 | 192:47 | 94.4274 | 93.4159
9 | Karwar | 30 | 30 | 244:50 | 1749:09 | 586:47 | 1200:18 | 1787:05 | 6875:57 | 2031:55 | 67:44 | 91.9934 | 90.8964 | 8625:06 | 287:30 | 92.1722 | 90.1809
10 | Honnavar | 40 | 40 | 469:23 | 2272:18 | 528:23 | 873:42 | 1402:05 | 6723:22 | 1871:28 | 46:47 | 95.2887 | 93.7115 | 8995:40 | 224:54 | 94.2594 | 92.3193
11 | Belagavi | 142 | 142 | 780:43 | 1952:29 | 14502:52 | 3047:18 | 17550:10 | 3626.1757 | 18330:53 | 129:05 | 83.3881 | 82.6491 | 3707.5292 | 626:37 | 79.0685 | 78.5989
12 | Bailhongal | 192 | 192 | 1281:34 | 7008:11 | 1600.1437 | 6136:38 | 1855.8368 | 7767.2875 | 1909.2354 | 238:39 | 68.8199 | 67.9228 | 8059.2951 | 1007:25 | 66.8405 | 65.5939
13 | Ramdurg | 76 | 76 | 292:22 | 1630:06 | 23937:30 | 3155:42 | 1128.8833 | 4360.784 | 1141.0653 | 360:20 | 52.0847 | 51.5677 | 4428.7049 | 1398:32 | 52.9682 | 52.2357
14 | Ghataprabha | 162 | 162 | 249:00 | 905:56 | 1613.9292 | 3234:54 | 1748.7167 | 7261.9743 | 1759.0917 | 260:36 | 65.1789 | 64.9723 | 7299.7215 | 1081:26 | 63.2566 | 63.0656
15 | Raibag | 176 | 176 | 702:00 | 1943:50 | 1711.8062 | 2407:49 | 1812.1319 | 7573.6639 | 1841.3819 | 251:06 | 66.7864 | 66.2503 | 7654.6569 | 1043:49 | 64.7277 | 64.3505
16 | Athani | 194 | 194 | 732:04 | 2868:45 | 1578.5889 | 2082:07 | 1665.3438 | 6762.6611 | 1695.8465 | 209:48 | 72.3089 | 71.8017 | 6882.1924 | 851:24 | 71.427 | 70.922
17 | Chikkodi | 190 | 190 | 335:15 | 1871:58 | 1980.2694 | 3039:43 | 2106.9243 | 8633.1486 | 2120.8931 | 267:54 | 64.2288 | 63.9916 | 8711.1472 | 1100:21 | 62.756 | 62.4196
18 | Vijayapur | 166 | 166 | 380:45 | 1214:08 | 1631.1208 | 5489:01 | 1859.8299 | 7826.2486 | 1875.6944 | 271:11 | 63.8587 | 63.5504 | 7876.8375 | 1138:49 | 61.3557 | 61.1059
19 | Indi | 254 | 254 | 1330:55 | 5342:19 | 2718.5597 | 8312:16 | 3064.9042 | 12593.6229 | 3120.359 | 294:50 | 61.0756 | 60.3714 | 12816.2194 | 1210:59 | 59.3597 | 58.6413
20 | B.Bagewadi | 142 | 142 | 681:10 | 3153:32 | 1505.8104 | 4588:20 | 1696.991 | 6588.6292 | 1725.3729 | 291:37 | 61.4495 | 60.8048 | 6720.0264 | 1135:47 | 61.9682 | 61.2097
21 | Bagalkot | 185 | 185 | 800:22 | 3602:07 | 1594.8924 | 6917:28 | 1883.1201 | 8326.0465 | 1916.4688 | 248:37 | 67.1644 | 66.5829 | 8476.1347 | 1099:36 | 63.1101 | 62.4451
22 | Jamkhandi | 208 | 208 | 668:40 | 1981:27 | 2347.759 | 1916:40 | 2427.6201 | 10218.7611 | 2455.4812 | 283:19 | 62.3508 | 61.9187 | 10301.3215 | 1188:37 | 59.7306 | 59.4053
23 | Mudhol | 192 | 192 | 435:57 | 1567:10 | 2692.8653 | 3015:20 | 2818.5042 | 10967.8083 | 2836.6688 | 354:35 | 52.6461 | 52.3409 | 11033.1069 | 1379:08 | 53.177 | 52.8983
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of August-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of August-2021 |  |  |  | Reliability for cumulative period from Apr-21 to August-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 71:35 | 1191:15 | 5195:06 | 1847:37 | 7042:43 | 1456.559 | 7114:18 | 158:06 | 78.9644 | 78.7506 | 1506.1944 | 803:18 | 78.8445 | 78.1235
2 | Dharwad Rural | 81 | 81 | 56:46 | 912:15 | 15664:30 | 1759:04 | 17423:34 | 3911.0625 | 17480:20 | 215:48 | 71.0879 | 70.9937 | 3949.0729 | 1170:06 | 68.4414 | 68.1346
3 | Gadag | 98 | 98 | 46:20 | 455:51 | 19375:33 | 2243:19 | 21618:52 | 4310.6938 | 21665:12 | 221:04 | 70.3494 | 70.2858 | 4329.6875 | 1060:20 | 71.2505 | 71.1239
4 | Ron | 54 | 54 | 61:25 | 1134:49 | 8238:15 | 501:20 | 8739:35 | 2579.6472 | 8801:00 | 162:59 | 78.2468 | 78.0939 | 2626.9313 | 1167:32 | 68.777 | 68.2047
5 | Haveri | 197 | 197 | 800:48 | 7748:23 | 2392.2924 | 8576:39 | 2749.6528 | 14145.1465 | 2783.0194 | 339:03 | 54.9754 | 54.429 | 14467.9958 | 1762:36 | 53.0701 | 51.999
6 | Ranebennur | 182 | 182 | 507:24 | 4469:03 | 2495.6 | 5217:06 | 2712.9792 | 13709.916 | 2734.1208 | 360:33 | 51.9146 | 51.5399 | 13896.1264 | 1832:27 | 50.7652 | 50.0965
7 | Sirsi | 54 | 54 | 271:19 | 2562:23 | 533:51 | 1378:00 | 1911:51 | 16467:08 | 2183:10 | 40:26 | 95.2413 | 94.566 | 19029:31 | 352:24 | 91.6953 | 90.4031
8 | Dandeli | 22 | 22 | 69:56 | 721:31 | 254:16 | 463:36 | 717:52 | 4307:30 | 787:48 | 35:49 | 95.6142 | 95.187 | 5029:01 | 228:36 | 94.6679 | 93.7747
9 | Karwar | 30 | 30 | 265:47 | 2014:56 | 326:02 | 480:36 | 806:38 | 7682:35 | 1072:25 | 35:45 | 96.3861 | 95.1953 | 9697:31 | 323:15 | 93.026 | 91.1969
10 | Honnavar | 40 | 40 | 285:02 | 2557:20 | 569:25 | 526:02 | 1095:27 | 7818:49 | 1380:29 | 34:31 | 96.3191 | 95.3613 | 10376:09 | 259:24 | 94.6767 | 92.9356
11 | Belagavi | 142 | 142 | 391:31 | 2344:00 | 22082:29 | 1673:22 | 23755:51 | 4616.0028 | 1006.1403 | 170:03 | 77.5142 | 77.1436 | 4713.6694 | 796:41 | 78.7536 | 78.304
12 | Bailhongal | 192 | 192 | 965:33 | 7973:44 | 1829.8507 | 3026:37 | 1955.9597 | 9723.2472 | 1996.191 | 249:31 | 67.1378 | 66.4618 | 10055.4861 | 1256:56 | 66.9007 | 65.7697
13 | Ramdurg | 78 | 78 | 386:55 | 2017:01 | 1023.4715 | 2282:11 | 1118.5625 | 5479.3465 | 1134.684 | 349:08 | 53.7402 | 53.0734 | 5563.3889 | 1711:49 | 54.0863 | 53.382
14 | Ghataprabha | 162 | 162 | 182:12 | 1088:08 | 1838.4778 | 1250:35 | 1890.5854 | 9152.5597 | 1898.1771 | 281:13 | 62.3539 | 62.2028 | 9197.8986 | 1362:39 | 63.0737 | 62.8908
15 | Raibag | 176 | 176 | 374:49 | 2318:39 | 1677.8417 | 1179:54 | 1727.0042 | 9300.6681 | 1742.6215 | 237:38 | 68.3467 | 68.0605 | 9397.2785 | 1281:27 | 65.461 | 65.1022
16 | Athani | 197 | 197 | 728:11 | 3596:56 | 1602.6042 | 1419:21 | 1661.7438 | 8424.4049 | 1692.0847 | 206:09 | 72.7895 | 72.2927 | 8574.2771 | 1044:35 | 72.05 | 71.5528
17 | Chikkodi | 190 | 190 | 142:40 | 2014:38 | 1703.4687 | 892:44 | 1740.666 | 10373.8146 | 1746.6104 | 220:37 | 70.4471 | 70.3462 | 10457.7576 | 1320:59 | 64.3144 | 64.0256
18 | Vijayapur | 173 | 173 | 416:33 | 1630:41 | 1920.3292 | 5390:02 | 2144.9139 | 9971.1625 | 2162.2701 | 299:58 | 60.0053 | 59.6817 | 10039.1076 | 1392:43 | 62.3289 | 62.0722
19 | Indi | 254 | 254 | 524:50 | 5867:09 | 2816.7715 | 7258:48 | 3119.2215 | 15712.8444 | 3141.0896 | 296:48 | 60.3858 | 60.1081 | 15957.309 | 1507:47 | 59.5676 | 58.9385
20 | B.Bagewadi | 142 | 142 | 284:18 | 3437:50 | 1533.3076 | 2983:21 | 1657.6139 | 8246.2431 | 1669.4597 | 282:10 | 62.3441 | 62.075 | 8389.4861 | 1417:56 | 62.0444 | 61.385
21 | Bagalkot | 187 | 187 | 462:46 | 4064:53 | 1685.9424 | 4885:10 | 1889.491 | 10215.5375 | 1908.7729 | 244:59 | 67.4057 | 67.0731 | 10384.9076 | 1332:49 | 64.2951 | 63.7031
22 | Jamkhandi | 210 | 210 | 792:19 | 2773:46 | 2329.3014 | 1436:09 | 2389.141 | 12607.9021 | 2422.1542 | 276:49 | 63.3004 | 62.7933 | 12723.4757 | 1454:07 | 60.7597 | 60.4
23 | Mudhol | 192 | 192 | 176:02 | 1743:12 | 2644.666 | 2264:56 | 2739.0382 | 13706.8465 | 2746.3729 | 343:18 | 53.9812 | 53.858 | 13779.4799 | 1722:26 | 53.34 | 53.0927
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of September-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of September-2021 |  |  |  | Reliability for cumulative period from Apr-21 to September-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 55:40 | 1246:55 | 5261:21 | 1309:49 | 6571:10 | 1730.3576 | 6626:50 | 147:16 | 79.7186 | 79.5468 | 1782.3125 | 950:34 | 78.9878 | 78.3569
2 | Dharwad Rural | 81 | 81 | 361:25 | 1273:40 | 15888:09 | 2271:11 | 18159:20 | 4667.7014 | 18520:45 | 228:39 | 68.8626 | 68.2429 | 4720.7708 | 1398:45 | 68.5104 | 68.1524
3 | Gadag | 99 | 99 | 72:45 | 528:36 | 17077:34 | 1753:39 | 18831:13 | 5095.3278 | 18903:58 | 190:57 | 73.5813 | 73.4793 | 5117.3528 | 1240:34 | 71.8754 | 71.7539
4 | Ron | 54 | 54 | 25:50 | 1160:39 | 12293:15 | 640:30 | 12933:45 | 3118.5535 | 12959:35 | 240:00 | 66.7342 | 66.6677 | 3166.9139 | 1407:31 | 68.4421 | 67.9527
5 | Haveri | 197 | 197 | 1020:28 | 8768:51 | 2253.5708 | 8174:44 | 2594.1847 | 16739.3312 | 2636.7042 | 321:13 | 56.1052 | 55.3857 | 17104.7 | 2083:49 | 53.5676 | 52.5542
6 | Ranebennur | 182 | 182 | 600:34 | 5069:37 | 2499.75 | 4214:10 | 2675.3403 | 16385.2562 | 2700.3639 | 356:06 | 51.0011 | 50.5428 | 16596.4903 | 2188:33 | 50.8039 | 50.1697
7 | Sirsi | 54 | 54 | 252:43 | 2815:06 | 479:31 | 1456:23 | 1935:54 | 18403:02 | 2188:37 | 40:32 | 95.0208 | 94.3708 | 21218:08 | 392:56 | 92.2405 | 91.0535
8 | Dandeli | 22 | 22 | 28:05 | 749:36 | 235:15 | 510:17 | 745:32 | 5053:02 | 773:37 | 35:10 | 95.2934 | 95.1161 | 5802:38 | 263:45 | 94.7704 | 93.9946
9 | Karwar | 30 | 30 | 313:06 | 2328:02 | 270:51 | 491:58 | 762:49 | 8445:24 | 1075:55 | 35:52 | 96.4684 | 95.0189 | 10773:26 | 359:07 | 93.5903 | 91.8234
10 | Honnavar | 40 | 40 | 318:38 | 2875:58 | 444:37 | 599:35 | 1044:12 | 8863:01 | 1362:50 | 34:04 | 96.3743 | 95.2679 | 11738:59 | 293:28 | 94.955 | 93.318
11 | Belagavi | 142 | 142 | 834:49 | 3178:49 | 18432:18 | 1711:29 | 20143:47 | 5455.3271 | 20978:36 | 147:44 | 80.2976 | 79.481 | 5587.7778 | 944:25 | 79.0067 | 78.497
12 | Bailhongal | 192 | 192 | 1363:22 | 9337:06 | 1758.6035 | 2804:20 | 1875.4507 | 11598.6979 | 1932.2576 | 241:32 | 67.4401 | 66.4539 | 11987.7437 | 1498:28 | 66.9891 | 65.8819
13 | Ramdurg | 79 | 79 | 396:20 | 2413:21 | 1024.2833 | 1676:33 | 1094.1396 | 6573.4861 | 1110.6535 | 337:25 | 53.8338 | 53.137 | 6674.0424 | 2027:33 | 54.5308 | 53.8352
14 | Ghataprabha | 162 | 162 | 437:26 | 1525:34 | 1523.3146 | 1047:51 | 1566.975 | 10719.5347 | 1585.2014 | 234:51 | 67.7577 | 67.3827 | 10783.1 | 1597:30 | 63.8415 | 63.6271
15 | Raibag | 175 | 175 | 494:17 | 2812:56 | 1639.1931 | 888:26 | 1676.2111 | 10976.8792 | 1696.8063 | 232:42 | 68.0722 | 67.6799 | 11094.0847 | 1521:28 | 65.724 | 65.358
16 | Athani | 197 | 197 | 671:12 | 4268:08 | 1460.0319 | 1316:02 | 1514.8667 | 9939.2715 | 1542.8333 | 187:58 | 74.3677 | 73.8945 | 10117.1104 | 1232:32 | 72.43 | 71.9367
17 | Chikkodi | 191 | 191 | 278:30 | 2293:08 | 1861.2757 | 1269:13 | 1914.1597 | 12287.9743 | 1925.7639 | 241:59 | 66.5941 | 66.3916 | 12383.5215 | 1556:03 | 64.8443 | 64.5709
18 | Vijayapur | 173 | 173 | 249:29 | 1880:10 | 1550.9986 | 5499:51 | 1780.159 | 11751.3215 | 1790.5542 | 248:24 | 65.7002 | 65.4999 | 11829.6618 | 1641:07 | 62.8816 | 62.6341
19 | Indi | 254 | 254 | 1768:59 | 7636:08 | 2394.0236 | 8749:58 | 2758.6056 | 18471.45 | 2832.3132 | 267:37 | 63.7978 | 62.8305 | 18789.6222 | 1775:24 | 60.2611 | 59.5766
20 | B.Bagewadi | 142 | 142 | 331:39 | 3769:29 | 1445.9188 | 2887:53 | 1566.2472 | 9812.4903 | 1580.066 | 267:03 | 63.2336 | 62.9092 | 9969.5521 | 1685:00 | 62.2393 | 61.6349
21 | Bagalkot | 187 | 187 | 1009:47 | 5074:40 | 1558.6243 | 5345:38 | 1781.359 | 11996.8965 | 1823.4333 | 234:01 | 68.2467 | 67.4967 | 12208.341 | 1566:51 | 64.9429 | 64.325
22 | Jamkhandi | 210 | 210 | 481:10 | 3254:56 | 2262.2104 | 1324:47 | 2317.4097 | 14925.3118 | 2337.4583 | 267:08 | 63.2157 | 62.8975 | 15060.934 | 1721:15 | 61.1623 | 60.8094
23 | Mudhol | 193 | 193 | 209:37 | 1952:49 | 2560.2875 | 1818:47 | 2636.0701 | 16342.9167 | 2644.8042 | 328:53 | 54.472 | 54.3212 | 16424.284 | 2042:24 | 53.7277 | 53.4973
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of October-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of October-2021 |  |  |  | Reliability for cumulative period from Apr-21 to October-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 165:55 | 1412:50 | 5473:20 | 1859:29 | 7332:49 | 2035.8917 | 7498:44 | 166:38 | 78.0979 | 77.6023 | 2094.7597 | 1117:12 | 78.8589 | 78.2476
2 | Dharwad Rural | 85 | 85 | 1600:07 | 2873:47 | 11710:04 | 1782:31 | 13492:35 | 5229.8924 | 15092:42 | 177:34 | 78.6645 | 76.1343 | 5349.6333 | 1510:29 | 71.2485 | 70.5903
3 | Gadag | 99 | 99 | 104:55 | 633:31 | 15741:25 | 3233:15 | 18974:40 | 5885.9389 | 19079:35 | 192:43 | 74.2388 | 74.0964 | 5912.3354 | 1433:18 | 72.2178 | 72.0932
4 | Ron | 54 | 54 | 238:42 | 1399:21 | 12615:35 | 680:46 | 13296:21 | 3672.5681 | 13535:03 | 250:39 | 66.9047 | 66.3106 | 3730.8743 | 1658:10 | 68.2194 | 67.7148
5 | Haveri | 197 | 197 | 1391:05 | 10159:56 | 2227.684 | 13305:50 | 2782.0937 | 19521.425 | 2840.0556 | 346:00 | 54.4442 | 53.4951 | 19944.7556 | 2429:49 | 53.6946 | 52.6905
6 | Ranebennur | 182 | 182 | 819:44 | 5889:21 | 2373.9493 | 12226:10 | 2883.3729 | 19268.6292 | 2917.5285 | 384:44 | 48.8945 | 48.2891 | 19514.0188 | 2573:17 | 50.5273 | 49.8973
7 | Sirsi | 54 | 54 | 404:59 | 3220:05 | 602:09 | 1818:12 | 2420:21 | 20823:23 | 2825:20 | 52:19 | 93.9756 | 92.9676 | 1001.8111 | 445:15 | 92.4919 | 91.3308
8 | Dandeli | 22 | 22 | 32:17 | 781:53 | 286:31 | 536:48 | 823:19 | 5876:21 | 855:36 | 38:53 | 94.97 | 94.7727 | 6658:14 | 302:39 | 94.7993 | 94.1073
9 | Karwar | 30 | 30 | 280:16 | 2608:18 | 177:50 | 469:55 | 647:45 | 9093:09 | 928:01 | 30:56 | 97.0979 | 95.8422 | 11701:27 | 390:03 | 94.0984 | 92.4056
10 | Honnavar | 40 | 40 | 304:25 | 3180:23 | 344:23 | 437:27 | 781:50 | 9644:51 | 1086:15 | 27:09 | 97.3729 | 96.35 | 12825:14 | 320:38 | 95.3053 | 93.7572
11 | Belagavi | 142 | 142 | 823:16 | 4002:05 | 14312:28 | 3748:03 | 18060:31 | 6207.8486 | 18883:47 | 132:59 | 82.905 | 82.1258 | 6374.6021 | 1077:24 | 79.5714 | 79.0226
12 | Bailhongal | 192 | 192 | 1284:55 | 10622:01 | 1782.1181 | 4850:07 | 1984.2063 | 13582.9042 | 2037.7444 | 254:43 | 66.6632 | 65.7637 | 14025.4882 | 1753:11 | 66.9419 | 65.8648
13 | Ramdurg | 80 | 80 | 282:56 | 2696:17 | 1061.6208 | 2076:57 | 1148.1604 | 7721.6465 | 1159.9493 | 347:59 | 53.7032 | 53.2279 | 7833.9917 | 2350:12 | 54.8969 | 54.2407
14 | Ghataprabha | 162 | 162 | 736:07 | 2261:41 | 1574.0146 | 2297:26 | 1669.741 | 12389.2757 | 1700.4125 | 251:55 | 66.7515 | 66.1407 | 12483.5125 | 1849:25 | 64.2631 | 63.9913
15 | Raibag | 174 | 174 | 672:17 | 3485:13 | 1660.1604 | 2453:51 | 1762.4042 | 12739.2833 | 1790.416 | 246:57 | 67.3266 | 66.8073 | 12884.5007 | 1777:10 | 65.7877 | 65.3977
16 | Athani | 197 | 197 | 843:24 | 5111:32 | 1525.4403 | 1788:22 | 1599.9556 | 11539.2271 | 1635.0972 | 199:12 | 73.8013 | 73.2259 | 11752.2076 | 1431:44 | 72.6286 | 72.1234
17 | Chikkodi | 192 | 192 | 868:55 | 3162:03 | 1948.2299 | 1686:53 | 2018.5167 | 14306.491 | 2054.7215 | 256:50 | 66.0867 | 65.4785 | 14438.2431 | 1804:47 | 65.1809 | 64.8602
18 | Vijayapur | 173 | 173 | 593:36 | 2473:46 | 1599.134 | 3128:01 | 1729.4681 | 13480.7896 | 1754.2014 | 243:21 | 67.7519 | 67.2907 | 13583.8632 | 1884:28 | 63.5871 | 63.3087
19 | Indi | 254 | 254 | 726:11 | 8362:19 | 2552.4556 | 5469:11 | 2780.3382 | 21251.7882 | 2810.5958 | 265:34 | 64.6896 | 64.3054 | 21600.2181 | 2040:58 | 60.9026 | 60.2616
20 | B.Bagewadi | 142 | 142 | 404:36 | 4174:05 | 1475.309 | 2921:05 | 1597.0208 | 11409.5111 | 1613.8792 | 272:46 | 63.7206 | 63.3376 | 11583.4312 | 1957:46 | 62.4539 | 61.8816
21 | Bagalkot | 188 | 188 | 428:49 | 5503:29 | 1745.1354 | 4051:53 | 1913.9639 | 13910.8604 | 1931.8312 | 246:37 | 67.1592 | 66.8526 | 14140.1722 | 1805:08 | 65.4234 | 64.8534
22 | Jamkhandi | 211 | 211 | 611:07 | 3866:03 | 2348.4264 | 1558:46 | 2413.375 | 17338.6868 | 2438.8382 | 277:24 | 63.1039 | 62.7146 | 17499.7722 | 1990:30 | 61.601 | 61.2442
23 | Mudhol | 193 | 193 | 210:51 | 2163:40 | 2669.8792 | 2139:25 | 2759.0215 | 19101.9382 | 2767.8069 | 344:11 | 53.8857 | 53.7388 | 19192.091 | 2386:35 | 53.7506 | 53.5323
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of November-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of November-2021 |  |  |  | Reliability for cumulative period from Apr-21 to November-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 344:00 | 1756:50 | 5161:19 | 1561:24 | 6722:43 | 2316.0049 | 7066:43 | 157:02 | 79.2509 | 78.1891 | 2389.2062 | 1274:15 | 78.9071 | 78.2404
2 | Dharwad Rural | 90 | 90 | 467:26 | 3341:13 | 15103:48 | 3079:14 | 18183:02 | 5987.5188 | 18650:28 | 207:14 | 71.9398 | 71.2184 | 6126.7361 | 1633:48 | 72.7344 | 72.1005
3 | Gadag | 99 | 99 | 96:30 | 730:01 | 13835:42 | 3626:51 | 17462:33 | 6613.5451 | 17559:03 | 177:22 | 75.5015 | 75.3661 | 6643.9625 | 1610:39 | 72.6215 | 72.4956
4 | Ron | 54 | 54 | 85:45 | 1485:06 | 11230:35 | 792:55 | 12023:30 | 4173.5472 | 12109:15 | 224:15 | 69.0754 | 68.8548 | 4235.4264 | 1882:25 | 68.3246 | 67.855
5 | Haveri | 196 | 196 | 1370:17 | 11530:13 | 2214.7007 | 13666:28 | 2784.1368 | 22305.5618 | 2841.2319 | 347:54 | 52.6507 | 51.6797 | 22785.9875 | 2790:07 | 53.3591 | 52.3545
6 | Ranebennur | 191 | 191 | 481:48 | 6371:09 | 2364.284 | 11084:12 | 2826.1257 | 22094.7549 | 2846.2007 | 357:38 | 50.6784 | 50.3281 | 22360.2194 | 2809:40 | 52.5904 | 52.0208
7 | Sirsi | 55 | 55 | 410:24 | 3630:29 | 577:16 | 1834:22 | 2411:38 | 23235:01 | 2822:02 | 51:19 | 93.91 | 92.8737 | 1119.3958 | 488:28 | 92.7859 | 91.6587
8 | Dandeli | 22 | 22 | 103:05 | 884:58 | 193:23 | 418:15 | 611:38 | 6487:59 | 714:43 | 32:29 | 96.1387 | 95.4879 | 7372:57 | 335:08 | 94.964 | 94.2771
9 | Karwar | 30 | 30 | 105:22 | 2713:40 | 246:26 | 447:01 | 693:27 | 9786:36 | 798:49 | 26:38 | 96.7896 | 96.3018 | 12500:16 | 416:41 | 94.4293 | 92.8846
10 | Honnavar | 40 | 40 | 275:36 | 3455:59 | 585:02 | 624:12 | 1209:14 | 10854:05 | 1484:50 | 37:07 | 95.8013 | 94.8443 | 14310:04 | 357:45 | 95.3663 | 93.8909
11 | Belagavi | 142 | 142 | 871:19 | 4873:24 | 13198:57 | 3744:20 | 16943:17 | 6913.8188 | 17814:36 | 125:27 | 83.4279 | 82.5757 | 7116.8771 | 1202:51 | 80.0455 | 79.4595
12 | Bailhongal | 192 | 192 | 1751:16 | 12373:17 | 1613.4465 | 5778:34 | 1854.2201 | 15437.1243 | 1927.1896 | 240:54 | 67.8087 | 66.5418 | 15952.6778 | 1994:05 | 67.0485 | 65.948
13 | Ramdurg | 83 | 83 | 435:13 | 3131:30 | 1044.0764 | 2508:33 | 1148.5993 | 8870.2458 | 1166.7333 | 337:22 | 53.8715 | 53.1432 | 9000.725 | 2602:37 | 56.2006 | 55.5564
14 | Ghataprabha | 162 | 162 | 169:44 | 2431:25 | 1482.2451 | 2300:31 | 1578.1 | 13967.3757 | 1585.1722 | 234:50 | 67.5288 | 67.3833 | 14068.6847 | 2084:15 | 64.6646 | 64.4083
15 | Raibag | 174 | 174 | 258:41 | 3743:54 | 1551.5875 | 1704:55 | 1622.6257 | 14361.909 | 1633.4042 | 225:18 | 68.9152 | 68.7087 | 14517.9049 | 2002:28 | 66.1723 | 65.8048
16 | Athani | 197 | 197 | 641:23 | 5752:55 | 1454.1424 | 2335:32 | 1551.4563 | 13090.6833 | 1578.1806 | 192:16 | 73.7486 | 73.2964 | 13330.3882 | 1624:00 | 72.7663 | 72.2676
17 | Chikkodi | 192 | 192 | 135:50 | 3297:53 | 1863.1333 | 1585:43 | 1929.2049 | 16235.6958 | 1934.8646 | 241:51 | 66.5069 | 66.4086 | 16373.1076 | 2046:38 | 65.3439 | 65.0506
18 | Vijayapur | 173 | 173 | 414:30 | 2888:16 | 1587.0444 | 3984:46 | 1753.0764 | 15233.866 | 1770.3472 | 245:36 | 66.222 | 65.8893 | 15354.2104 | 2130:04 | 63.9111 | 63.626
19 | Indi | 255 | 255 | 810:10 | 9172:29 | 2436.0806 | 6386:56 | 2702.2028 | 23953.991 | 2735.9597 | 257:30 | 64.6771 | 64.2358 | 24336.1778 | 2290:28 | 61.5011 | 60.8869
20 | B.Bagewadi | 142 | 142 | 442:01 | 4616:06 | 1419.841 | 2921:52 | 1541.5854 | 12951.0965 | 1560.0028 | 263:40 | 63.8125 | 63.3802 | 13143.434 | 2221:26 | 62.6209 | 62.0658
21 | Bagalkot | 187 | 187 | 726:07 | 6229:36 | 1577.275 | 4616:27 | 1769.6271 | 15680.4875 | 1799.8819 | 231:00 | 68.4558 | 67.9165 | 15940.0542 | 2045:47 | 65.6341 | 65.0652
22 | Jamkhandi | 212 | 212 | 337:48 | 4203:51 | 2173.0438 | 1643:20 | 2241.516 | 19580.2028 | 2255.591 | 255:21 | 64.756 | 64.5347 | 19755.3632 | 2236:27 | 62.1478 | 61.8091
23 | Mudhol | 194 | 194 | 381:30 | 2545:10 | 2585.1035 | 2238:54 | 2678.391 | 21780.3292 | 2694.2868 | 333:19 | 53.9795 | 53.7064 | 21886.3778 | 2707:36 | 53.9878 | 53.7638
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of December-2021
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of December-2021 |  |  |  | Reliability for cumulative period from Apr-21 to December-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 100:20 | 1857:10 | 6489:59 | 473:58 | 6963:57 | 2606.1694 | 7064:17 | 153:34 | 79.6519 | 79.3587 | 2683.5514 | 1400:07 | 79.3979 | 78.7862
2 | Dharwad Rural | 90 | 90 | 328:03 | 3669:16 | 16072:28 | 1530:20 | 17602:48 | 6720.9688 | 17930:51 | 199:14 | 73.7115 | 73.2216 | 6873.8549 | 1833:02 | 72.8446 | 72.2268
3 | Gadag | 99 | 99 | 135:35 | 865:36 | 16532:30 | 1693:13 | 18225:43 | 7372.95 | 18361:18 | 185:28 | 75.2556 | 75.0715 | 7409.0167 | 1796:08 | 72.9185 | 72.786
4 | Ron | 54 | 54 | 63:53 | 1548:59 | 12794:14 | 339:48 | 13134:02 | 4720.7986 | 13197:55 | 244:24 | 67.3088 | 67.1497 | 4785.3396 | 2126:49 | 68.2101 | 67.7755
5 | Haveri | 197 | 197 | 1371:14 | 12901:27 | 2511.5771 | 5428:53 | 2737.7806 | 25043.3424 | 2794.9153 | 340:30 | 55.1698 | 54.2342 | 25580.9028 | 3116:27 | 53.7732 | 52.781
6 | Ranebennur | 191 | 191 | 757:35 | 7128:44 | 2613.0507 | 2792:49 | 2729.4181 | 24824.1729 | 2760.984 | 346:56 | 53.9028 | 53.3696 | 25121.2035 | 3156:35 | 52.7384 | 52.1729
7 | Sirsi | 55 | 55 | 356:23 | 3986:52 | 736:04 | 1022:31 | 1758:35 | 1041.4 | 2114:58 | 38:27 | 95.7024 | 94.8315 | 1207.5194 | 526:55 | 93.1147 | 92.0164
8 | Dandeli | 22 | 22 | 228:26 | 1113:24 | 165:31 | 284:28 | 449:59 | 6937:58 | 678:25 | 30:50 | 97.2508 | 95.8552 | 8051:22 | 365:58 | 95.2218 | 94.455
9 | Karwar | 30 | 30 | 188:15 | 2901:55 | 329:14 | 234:51 | 564:05 | 10350:41 | 752:20 | 25:05 | 97.4727 | 96.6293 | 13252:36 | 441:45 | 94.7724 | 93.3068
10 | Honnavar | 40 | 40 | 364:08 | 3820:07 | 437:37 | 304:39 | 742:16 | 11596:21 | 1106:24 | 27:40 | 97.5058 | 96.2823 | 15416:28 | 385:25 | 95.6074 | 94.1604
11 | Belagavi | 142 | 142 | 844:41 | 5718:05 | 12900:49 | 1972:50 | 14873:39 | 7533.5542 | 15718:20 | 110:42 | 85.9215 | 85.122 | 7771.8076 | 1313:33 | 80.7079 | 80.0978
12 | Bailhongal | 192 | 192 | 767:33 | 13140:50 | 1770.8375 | 2362:21 | 1869.2688 | 17306.3931 | 1901.25 | 237:39 | 68.5943 | 68.057 | 17853.9278 | 2231:44 | 67.2227 | 66.1857
13 | Ramdurg | 84 | 84 | 318:40 | 3450:10 | 1122.9389 | 1072:26 | 1167.6236 | 10037.8694 | 1180.9014 | 337:24 | 55.1604 | 54.6505 | 10181.6264 | 2909:02 | 56.546 | 55.9237
14 | Ghataprabha | 162 | 162 | 222:42 | 2654:07 | 1555.275 | 736:07 | 1585.9465 | 15553.3222 | 1595.2257 | 236:20 | 68.42 | 68.2353 | 15663.9104 | 2320:35 | 65.0879 | 64.8397
15 | Raibag | 174 | 174 | 442:52 | 4186:46 | 1619.65 | 967:51 | 1659.9771 | 16021.8861 | 1678.4299 | 231:30 | 69.2255 | 68.8834 | 16196.3347 | 2233:59 | 66.5164 | 66.1519
16 | Athani | 197 | 197 | 365:10 | 6118:05 | 1487.816 | 805:21 | 1521.3722 | 14612.0556 | 1536.5875 | 187:12 | 75.0881 | 74.8389 | 14866.9757 | 1811:12 | 73.028 | 72.5575
17 | Chikkodi | 192 | 192 | 528:55 | 3826:48 | 1909.0285 | 917:53 | 1947.2736 | 18182.9694 | 1969.3118 | 246:10 | 67.2837 | 66.9134 | 18342.4194 | 2292:48 | 65.5626 | 65.2606
18 | Vijayapur | 173 | 173 | 161:09 | 3049:25 | 1607.0125 | 2158:12 | 1696.9375 | 16930.8035 | 1703.6521 | 236:21 | 68.3584 | 68.2332 | 17057.8625 | 2366:25 | 64.4124 | 64.1453
19 | Indi | 255 | 255 | 837:32 | 10010:01 | 2394.1847 | 4523:36 | 2582.6681 | 26536.659 | 2617.5653 | 246:22 | 67.3287 | 66.8872 | 26953.7431 | 2536:49 | 62.1581 | 61.5633
20 | B.Bagewadi | 142 | 142 | 175:07 | 4791:13 | 1359.1854 | 1522:17 | 1422.6139 | 14373.7104 | 1429.9104 | 241:40 | 67.6826 | 67.5168 | 14573.3444 | 2463:06 | 63.1915 | 62.6803
21 | Bagalkot | 187 | 187 | 378:35 | 6608:11 | 1714.8347 | 2399:00 | 1814.7931 | 17495.2806 | 1830.5674 | 234:56 | 68.6943 | 68.4222 | 17770.6215 | 2280:43 | 65.979 | 65.4436
22 | Jamkhandi | 212 | 212 | 396:10 | 4600:01 | 2216.9007 | 1050:56 | 2260.6896 | 21840.8924 | 2277.1965 | 257:48 | 65.6012 | 65.35 | 22032.5597 | 2494:15 | 62.5371 | 62.2083
23 | Mudhol | 194 | 194 | 215:27 | 2760:37 | 2654.3222 | 1283:52 | 2707.8167 | 24488.1458 | 2716.7938 | 336:06 | 54.9748 | 54.8255 | 24603.1715 | 3043:41 | 54.0991 | 53.8835
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of January-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of January-2022 |  |  |  | Reliability for cumulative period from Apr-21 to Jan-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 63:00 | 1920:10 | 6776:43 | 363:15 | 7139:58 | 2903.6681 | 7202:58 | 156:35 | 79.1375 | 78.9535 | 2983.675 | 1556:42 | 77.0461 | 76.4136
2 | Dharwad Rural | 90 | 90 | 441:41 | 4110:57 | 17335:56 | 744:09 | 18080:05 | 7474.3056 | 18521:46 | 205:48 | 72.9987 | 72.3391 | 7645.5951 | 2038:50 | 69.8008 | 69.1087
3 | Gadag | 101 | 101 | 18:10 | 883:46 | 21353:38 | 484:14 | 21837:52 | 8282.8611 | 21856:02 | 216:24 | 70.3515 | 70.3269 | 8319.6847 | 1976:57 | 69.5763 | 69.441
4 | Ron | 54 | 54 | 104:17 | 1653:16 | 14816:42 | 196:44 | 15013:26 | 5346.3583 | 15117:43 | 279:57 | 62.6308 | 62.3713 | 5415.2444 | 2406:47 | 63.9976 | 63.5337
5 | Haveri | 197 | 197 | 1183:08 | 14084:35 | 2685.2285 | 1978:00 | 2767.6451 | 27810.9875 | 2816.9424 | 343:11 | 54.6808 | 53.8735 | 28397.8451 | 3459:38 | 48.6645 | 47.5813
6 | Ranebennur | 192 | 192 | 450:19 | 7579:03 | 2731.0944 | 1902:39 | 2810.3715 | 27634.5444 | 2829.1347 | 353:39 | 52.5355 | 52.2186 | 27950.3382 | 3493:48 | 47.3878 | 46.7866
7 | Sirsi | 56 | 56 | 313:12 | 4300:04 | 516:13 | 848:28 | 1364:41 | 1098.2618 | 1677:53 | 29:58 | 96.665 | 95.8996 | 1277.4312 | 547:28 | 92.7388 | 91.5542
8 | Dandeli | 22 | 22 | 11:06 | 1124:30 | 161:48 | 184:43 | 346:31 | 7284:29 | 357:37 | 16:15 | 97.883 | 97.8151 | 8408:59 | 382:14 | 94.9831 | 94.2087
9 | Karwar | 29 | 29 | 89:55 | 2991:50 | 295:13 | 134:31 | 429:44 | 10780:25 | 519:39 | 17:55 | 98.0747 | 97.6718 | 13772:15 | 474:54 | 94.5553 | 93.0443
10 | Honnavar | 40 | 40 | 249:24 | 4069:31 | 372:45 | 242:47 | 615:32 | 12211:53 | 864:56 | 21:37 | 97.9317 | 97.0936 | 16281:24 | 407:02 | 95.3743 | 93.8328
11 | Belagavi | 149 | 149 | 612:43 | 6330:48 | 13194:22 | 1308:01 | 14502:23 | 8137.8201 | 15115:06 | 101:27 | 86.2729 | 85.693 | 8401.6035 | 1353:17 | 79.1605 | 78.485
12 | Bailhongal | 192 | 192 | 1253:34 | 14394:24 | 1945.7375 | 1267:18 | 1998.5417 | 19304.9347 | 2050.7736 | 256:21 | 66.4224 | 65.5448 | 19904.7014 | 2488:05 | 63.4376 | 62.3017
13 | Ramdurg | 85 | 85 | 280:48 | 3730:58 | 1151.3785 | 566:42 | 1174.991 | 11212.8604 | 1186.691 | 335:04 | 54.8775 | 54.4282 | 11368.3174 | 3209:53 | 51.4595 | 50.7865
14 | Ghataprabha | 162 | 162 | 291:41 | 2945:48 | 1563.8799 | 583:52 | 1588.2076 | 17141.5299 | 1600.3611 | 237:05 | 68.375 | 68.133 | 17264.2715 | 2557:40 | 61.5229 | 61.2474
15 | Raibag | 175 | 175 | 281:17 | 4468:03 | 1701.0347 | 762:24 | 1732.8014 | 17754.6875 | 1744.5215 | 239:15 | 67.8754 | 67.6581 | 17940.8562 | 2460:28 | 62.8951 | 62.506
16 | Athani | 197 | 197 | 221:18 | 6339:23 | 1514.9076 | 534:08 | 1537.1632 | 16149.2188 | 1546.384 | 188:24 | 74.8295 | 74.6785 | 16413.3597 | 1999:36 | 70.1906 | 69.7031
17 | Chikkodi | 192 | 192 | 278:45 | 4105:33 | 1954.2535 | 679:57 | 1982.5847 | 20165.5542 | 1994.1993 | 249:16 | 66.6904 | 66.4953 | 20336.6187 | 2542:05 | 61.8077 | 61.4837
18 | Vijayapur | 174 | 174 | 393:19 | 3442:44 | 1785.1778 | 875:43 | 1821.666 | 18752.4694 | 1838.0542 | 253:31 | 66.0327 | 65.7271 | 18895.9167 | 2606:20 | 60.5834 | 60.2818
19 | Indi | 255 | 255 | 1160:34 | 11170:35 | 2550.0111 | 2849:23 | 2668.7354 | 29205.3944 | 2717.0924 | 255:44 | 66.2399 | 65.6282 | 29670.8354 | 2792:33 | 58.3524 | 57.6886
20 | B.Bagewadi | 142 | 142 | 507:24 | 5298:37 | 1499.2465 | 788:16 | 1532.091 | 15905.8014 | 1553.2326 | 262:31 | 65.1956 | 64.7153 | 16126.5771 | 2725:37 | 59.2681 | 58.7027
21 | Bagalkot | 187 | 187 | 341:50 | 6950:01 | 2155.6507 | 1395:08 | 2213.7812 | 19709.0618 | 2228.0243 | 285:57 | 61.8116 | 61.5659 | 19998.6458 | 2566:40 | 61.6742 | 61.111
22 | Jamkhandi | 212 | 212 | 307:20 | 4907:21 | 2353.2646 | 521:38 | 2374.9993 | 24215.8917 | 2387.8049 | 270:19 | 63.8618 | 63.667 | 24420.3646 | 2764:34 | 58.4633 | 58.1126
23 | Mudhol | 194 | 194 | 311:50 | 3072:27 | 2698.9729 | 759:50 | 2730.6326 | 27218.7785 | 2743.6257 | 339:25 | 54.5954 | 54.3794 | 27346.7972 | 3383:07 | 48.9807 | 48.7408
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of February-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of February-2022 |  |  |  | Reliability for cumulative period from Apr-21 to February-2022
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 51:00 | 1971:10 | 6172:13 | 280:32 | 6452:45 | 3172.5326 | 6503:45 | 141:23 | 79.1254 | 78.9604 | 3254.6646 | 1698:05 | 79.3509 | 78.8163
2 | Dharwad Rural | 90 | 90 | 60:35 | 4171:32 | 16904:04 | 780:53 | 17684:57 | 8211.1785 | 17745:32 | 197:10 | 70.759 | 70.6588 | 8384.9924 | 2236:00 | 72.684 | 72.1058
3 | Gadag | 101 | 101 | 15:05 | 898:51 | 20846:54 | 381:18 | 21228:12 | 9167.3694 | 21243:17 | 210:20 | 68.7232 | 68.701 | 9204.8215 | 2187:17 | 72.8245 | 72.7135
4 | Ron | 54 | 54 | 155:01 | 1808:17 | 12939:29 | 509:46 | 13449:15 | 5906.7438 | 13604:16 | 251:56 | 62.9375 | 62.5103 | 5982.0889 | 2658:42 | 67.2503 | 66.8325
5 | Haveri | 199 | 199 | 758:03 | 14842:38 | 2478.0924 | 1490:59 | 2540.2167 | 30351.2042 | 2571.8021 | 310:10 | 54.411 | 53.8442 | 30969.6472 | 3735:02 | 54.3357 | 53.4053
6 | Ranebennur | 192 | 192 | 824:07 | 8403:10 | 2345.3472 | 1610:01 | 2412.4313 | 30046.9757 | 2446.7694 | 305:51 | 55.1259 | 54.4872 | 30397.1076 | 3799:38 | 53.1453 | 52.5993
7 | Sirsi | 56 | 56 | 392:29 | 4692:33 | 755:03 | 796:36 | 1551:39 | 1162.9139 | 1944:08 | 34:43 | 95.8768 | 94.8338 | 1358.4368 | 582:11 | 93.7825 | 92.7372
8 | Dandeli | 22 | 22 | 41:11 | 1165:41 | 193:34 | 208:41 | 402:15 | 7686:44 | 443:26 | 20:09 | 97.2792 | 97.0006 | 8852:25 | 402:23 | 95.6413 | 94.9803
9 | Karwar | 29 | 29 | 120:42 | 3112:32 | 472:25 | 514:05 | 986:30 | 11766:55 | 1107:12 | 38:11 | 94.9379 | 94.3186 | 14879:27 | 513:05 | 94.9382 | 93.5992
10 | Honnavar | 40 | 40 | 291:33 | 4361:04 | 327:57 | 208:12 | 536:09 | 12748:02 | 827:42 | 20:42 | 98.0054 | 96.9208 | 17109:06 | 427:44 | 96.0242 | 94.6641
11 | Belagavi | 149 | 149 | 294:22 | 6625:10 | 12794:57 | 925:08 | 13720:05 | 8709.4903 | 14014:27 | 94:03 | 86.2975 | 86.0035 | 8985.5389 | 1447:20 | 82.4991 | 81.9444
12 | Bailhongal | 192 | 192 | 1146:51 | 15541:15 | 1793.6139 | 1001:08 | 1835.3278 | 21140.2625 | 1883.1132 | 235:23 | 65.8607 | 64.9719 | 21787.8146 | 2723:29 | 67.0343 | 66.0245
13 | Ramdurg | 85 | 85 | 204:09 | 3935:07 | 1072.3382 | 481:07 | 1092.3847 | 12305.2451 | 1100.891 | 310:50 | 54.1015 | 53.7441 | 12469.2083 | 3520:43 | 56.6564 | 56.0789
14 | Ghataprabha | 162 | 162 | 82:28 | 3028:16 | 1369.2729 | 487:59 | 1389.6056 | 18531.1354 | 1393.0417 | 206:23 | 69.365 | 69.2892 | 18657.3132 | 2764:03 | 65.7516 | 65.5184
15 | Raibag | 175 | 175 | 133:52 | 4601:55 | 1521.0049 | 632:52 | 1547.3743 | 19302.0618 | 1552.9521 | 212:59 | 68.4209 | 68.3071 | 19493.8083 | 2673:26 | 66.9768 | 66.6487
16 | Athani | 200 | 200 | 280:55 | 6620:18 | 1295.3833 | 429:21 | 1313.2729 | 17462.4917 | 1324.9778 | 159:00 | 76.5487 | 76.3397 | 17738.3375 | 2128:36 | 73.8585 | 73.4456
17 | Chikkodi | 192 | 192 | 280:55 | 4386:28 | 1731.1889 | 676:59 | 1759.3965 | 21924.9507 | 1771.1014 | 221:23 | 67.2731 | 67.0554 | 22107.7201 | 2763:28 | 65.8106 | 65.5256
18 | Vijayapur | 184 | 184 | 108:41 | 3551:25 | 1741.4847 | 916:21 | 1779.666 | 20532.1354 | 1784.1944 | 232:43 | 65.4568 | 65.3689 | 20680.1111 | 2697:24 | 66.5905 | 66.3497
19 | Indi | 256 | 256 | 725:02 | 11895:37 | 2266.3042 | 3425:14 | 2409.0222 | 31614.4167 | 2439.2319 | 228:41 | 66.392 | 65.9705 | 32110.0674 | 3010:19 | 63.0258 | 62.4461
20 | B.Bagewadi | 142 | 142 | 150:55 | 5449:32 | 1371.4049 | 419:12 | 1388.8715 | 17294.6729 | 1395.1597 | 235:48 | 65.0686 | 64.9105 | 17521.7368 | 2961:25 | 63.5349 | 63.0561
21 | Bagalkot | 187 | 187 | 323:35 | 7273:36 | 2033.3722 | 1090:48 | 2078.8222 | 21787.884 | 2092.3049 | 268:32 | 60.2975 | 60.04 | 22090.9507 | 2835:12 | 65.1159 | 64.6307
22 | Jamkhandi | 212 | 212 | 372:43 | 5280:04 | 2120.791 | 459:48 | 2139.9493 | 26355.841 | 2155.4792 | 244:01 | 63.9496 | 63.688 | 26575.8438 | 3008:35 | 62.7784 | 62.4677
23 | Mudhol | 194 | 194 | 169:49 | 3242:16 | 2426.5028 | 528:28 | 2448.5222 | 29667.3007 | 2455.5979 | 303:47 | 54.9241 | 54.7939 | 29802.3951 | 3686:54 | 54.2143 | 54.0058
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of March-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of March-2022 |  |  |  | Reliability for cumulative period from Apr-21 to March-2022
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 233:00 | 2204:10 | 6342:39 | 1120:24 | 7463:03 | 3483.4931 | 7696:03 | 167:18 | 78.1935 | 77.5127 | 3575.3333 | 1865:23 | 79.2526 | 78.7056
2 | Dharwad Rural | 91 | 91 | 24:05 | 4195:37 | 17938:35 | 3757:10 | 21695:45 | 9115.1681 | 21719:50 | 238:41 | 67.955 | 67.9194 | 9289.9854 | 2450:06 | 72.5571 | 72.0308
3 | Gadag | 101 | 101 | 125:15 | 1024:06 | 1010.5993 | 800:32 | 1043.9549 | 10211.3243 | 1049.1736 | 249:19 | 66.6575 | 66.4908 | 10253.9951 | 2436:36 | 72.3008 | 72.185
4 | Ron | 57 | 57 | 144:05 | 1952:22 | 14896:25 | 628:19 | 15524:44 | 6553.6076 | 15668:49 | 274:53 | 63.392 | 63.0522 | 6634.9563 | 2793:40 | 68.4998 | 68.1088
5 | Haveri | 199 | 199 | 1887:40 | 16730:18 | 2619.7507 | 4589:50 | 2810.9938 | 33162.1979 | 2889.6465 | 348:30 | 54.4336 | 53.1586 | 33859.2937 | 4083:32 | 54.3441 | 53.3843
6 | Ranebennur | 193 | 193 | 1097:15 | 9500:25 | 2609.3007 | 2932:58 | 2731.5076 | 32778.4833 | 2777.2264 | 345:21 | 54.3455 | 53.5814 | 33174.334 | 4125:18 | 53.4694 | 52.9075
7 | Sirsi | 59 | 59 | 368:20 | 5060:53 | 593:14 | 1246:42 | 1839:56 | 1239.5778 | 2208:16 | 37:26 | 95.8084 | 94.9693 | 1450.4479 | 590:01 | 94.2439 | 93.2647
8 | Dandeli | 22 | 22 | 81:51 | 1247:32 | 310:58 | 387:07 | 698:05 | 8384:49 | 779:56 | 35:27 | 95.7351 | 95.235 | 9632:21 | 437:50 | 95.6492 | 95.0019
9 | Karwar | 32 | 32 | 268:57 | 3381:29 | 248:56 | 214:25 | 463:21 | 12230:16 | 732:18 | 22:53 | 98.0538 | 96.9241 | 15611:45 | 487:52 | 95.637 | 94.4307
10 | Honnavar | 40 | 40 | 353:50 | 4714:54 | 362:52 | 330:19 | 693:11 | 13441:13 | 1047:01 | 26:11 | 97.6708 | 96.4818 | 18156:07 | 453:54 | 96.164 | 94.8185
11 | Belagavi | 149 | 149 | 707:39 | 7332:49 | 15716:04 | 2118:51 | 17834:55 | 9452.6118 | 18542:34 | 124:27 | 83.9116 | 83.2733 | 9758.1458 | 1571:47 | 82.6191 | 82.0573
12 | Bailhongal | 194 | 194 | 1652:19 | 17193:34 | 1991.566 | 2139:30 | 2080.7118 | 23220.9743 | 2149.5583 | 265:55 | 65.4022 | 64.2574 | 23937.3729 | 2961:19 | 67.2066 | 66.1949
13 | Ramdurg | 87 | 87 | 808:37 | 4743:44 | 1170.2938 | 1631:17 | 1238.2639 | 13543.509 | 1271.9563 | 350:53 | 54.0874 | 52.8381 | 13741.1646 | 3790:40 | 57.35 | 56.7276
14 | Ghataprabha | 163 | 163 | 674:53 | 3703:09 | 1527.2611 | 1017:27 | 1569.6549 | 20100.7903 | 1597.775 | 235:15 | 68.9362 | 68.3797 | 20255.0882 | 2982:21 | 66.2143 | 65.955
15 | Raibag | 175 | 175 | 553:55 | 5155:50 | 1699.7187 | 908:17 | 1737.5639 | 21039.6257 | 1760.6437 | 241:28 | 67.9712 | 67.5457 | 21254.4521 | 2914:54 | 67.0613 | 66.7249
16 | Athani | 200 | 200 | 866:06 | 7486:24 | 1609.7014 | 1074:50 | 1654.4861 | 19116.9778 | 1690.5736 | 202:52 | 73.3147 | 72.7327 | 19428.9111 | 2331:28 | 73.8124 | 73.3851
17 | Chikkodi | 192 | 192 | 700:30 | 5086:58 | 1927.9326 | 1564:14 | 1993.109 | 23918.0597 | 2022.2965 | 252:47 | 66.5136 | 66.0232 | 24130.0167 | 3016:15 | 65.8703 | 65.5679
18 | Vijayapur | 184 | 184 | 188:55 | 3740:20 | 1894.1306 | 1475:26 | 1955.6069 | 22487.7424 | 1963.4785 | 256:06 | 65.7152 | 65.5772 | 22643.5896 | 2953:31 | 66.5162 | 66.2841
19 | Indi | 265 | 265 | 386:11 | 12281:48 | 2856.4951 | 1829:45 | 2932.7347 | 34547.1514 | 2948.8257 | 267:04 | 64.3002 | 64.1044 | 35058.8931 | 3175:09 | 64.2831 | 63.7541
20 | B.Bagewadi | 142 | 142 | 404:55 | 5854:27 | 1497.4056 | 942:12 | 1536.6639 | 18831.3368 | 1553.5354 | 262:34 | 65.0917 | 64.7084 | 19075.2722 | 3223:59 | 63.6671 | 63.1965
21 | Bagalkot | 187 | 187 | 1290:33 | 8564:09 | 2238.6049 | 2280:17 | 2333.6167 | 24121.5007 | 2387.3896 | 306:24 | 59.7444 | 58.8168 | 24478.3403 | 3141:36 | 64.6597 | 64.1369
22 | Jamkhandi | 213 | 213 | 380:29 | 5660:33 | 2416.0375 | 846:57 | 2451.3271 | 28807.1681 | 2467.1806 | 278:00 | 62.8756 | 62.6355 | 29043.0243 | 3272:27 | 62.9466 | 62.6432
23 | Mudhol | 194 | 194 | 523:35 | 3765:51 | 2722.9472 | 959:58 | 2762.9458 | 32430.2465 | 2784.7618 | 344:30 | 54.0581 | 53.6953 | 32587.1569 | 4031:24 | 54.201 | 53.9794
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]

## RURAL(Excl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of April-2021 |  |  |  | Reliability for cumulative period from Apr-21 to Apr-21
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 584:55 | 584:55 | 956:02 | 1642:49 | 2598:51 | 2598:51 | 3183:46 | 70:45 | 91.9789 | 90.1736 | 3183:46 | 70:45 | 91.9789 | 90.1736
2 | Dharwad Rural | 82 | 82 | 317:48 | 317:48 | 1961:00 | 3818:42 | 5779:42 | 5779:42 | 6097:30 | 74:22 | 90.2105 | 89.6723 | 6097:30 | 74:22 | 90.2105 | 89.6723
3 | Gadag | 94 | 94 | 64:50 | 64:50 | 1351:44 | 2671:07 | 4022:51 | 4022:51 | 4087:41 | 43:29 | 94.0561 | 93.9603 | 4087:41 | 43:29 | 94.0561 | 93.9603
4 | Ron | 53 | 53 | 326:45 | 326:45 | 727:51 | 1064:51 | 1792:42 | 1792:42 | 2119:27 | 39:59 | 95.3021 | 94.4459 | 2119:27 | 39:59 | 95.3021 | 94.4459
5 | Haveri | 197 | 197 | 2306:56 | 2306:56 | 2873:41 | 8476:46 | 11350:27 | 11350:27 | 13657:23 | 69:20 | 91.9977 | 90.3713 | 13657:23 | 69:20 | 91.9977 | 90.3713
6 | Ranebennur | 182 | 182 | 1162:15 | 1162:15 | 4092:13 | 6907:59 | 11000:12 | 11000:12 | 12162:27 | 66:50 | 91.6055 | 90.7185 | 12162:27 | 66:50 | 91.6055 | 90.7185
7 | Sirsi | 53 | 53 | 368:08 | 368:08 | 643:19 | 2016:24 | 2659:43 | 2659:43 | 3027:51 | 57:08 | 93.0301 | 92.0654 | 3027:51 | 57:08 | 93.0301 | 92.0654
8 | Dandeli | 22 | 22 | 87:36 | 87:36 | 291:20 | 437:31 | 728:51 | 728:51 | 816:27 | 37:07 | 95.3987 | 94.8456 | 816:27 | 37:07 | 95.3987 | 94.8456
9 | Karwar | 30 | 30 | 437:29 | 437:29 | 352:54 | 1336:01 | 1688:55 | 1688:55 | 2126:24 | 70:53 | 92.1809 | 90.1556 | 2126:24 | 70:53 | 92.1809 | 90.1556
10 | Honnavar | 40 | 40 | 373:59 | 373:59 | 416:55 | 558:15 | 975:10 | 975:10 | 1349:09 | 33:44 | 96.614 | 95.3155 | 1349:09 | 33:44 | 96.614 | 95.3155
11 | Belagavi | 138 | 138 | 379:44 | 379:44 | 3301:53 | 2574:19 | 5876:12 | 5876:12 | 6255:56 | 45:20 | 94.086 | 93.7038 | 6255:56 | 45:20 | 94.086 | 93.7038
12 | Bailhongal | 191 | 191 | 2479:50 | 2479:50 | 2456:45 | 3473:45 | 5930:30 | 5930:30 | 8410:20 | 44:02 | 95.6875 | 93.8843 | 8410:20 | 44:02 | 95.6875 | 93.8843
13 | Ramdurg | 76 | 76 | 682:35 | 682:35 | 1419:58 | 2266:12 | 3686:10 | 3686:10 | 4368:45 | 57:29 | 93.2636 | 92.0162 | 4368:45 | 57:29 | 93.2636 | 92.0162
14 | Ghataprabha | 160 | 160 | 248:53 | 248:53 | 1406:32 | 1742:10 | 3148:42 | 3148:42 | 3397:35 | 21:14 | 97.2668 | 97.0507 | 3397:35 | 21:14 | 97.2668 | 97.0507
15 | Raibag | 169 | 169 | 548:16 | 548:16 | 4626:08 | 1392:55 | 6019:03 | 6019:03 | 6567:19 | 38:52 | 95.0534 | 94.6028 | 6567:19 | 38:52 | 95.0534 | 94.6028
16 | Athani | 192 | 192 | 408:19 | 408:19 | 3000:23 | 1745:05 | 4745:28 | 4745:28 | 5153:47 | 26:51 | 96.5672 | 96.2719 | 5153:47 | 26:51 | 96.5672 | 96.2719
17 | Chikkodi | 189 | 189 | 409:48 | 409:48 | 1710:27 | 2237:39 | 3948:06 | 3948:06 | 4357:54 | 23:03 | 97.0987 | 96.7975 | 4357:54 | 23:03 | 97.0987 | 96.7975
18 | Vijayapur | 159 | 159 | 285:24 | 285:24 | 1273:54 | 2504:08 | 3778:02 | 3778:02 | 4063:26 | 25:33 | 96.6998 | 96.4505 | 4063:26 | 25:33 | 96.6998 | 96.4505
19 | Indi | 249 | 249 | 1627:38 | 1627:38 | 3647:50 | 4511:14 | 8159:04 | 8159:04 | 9786:42 | 39:18 | 95.449 | 94.5411 | 9786:42 | 39:18 | 95.449 | 94.5411
20 | B.Bagewadi | 138 | 138 | 696:55 | 696:55 | 1732:23 | 2122:09 | 3854:32 | 3854:32 | 4551:27 | 32:59 | 96.1206 | 95.4192 | 4551:27 | 32:59 | 96.1206 | 95.4192
21 | Bagalkot | 185 | 185 | 926:37 | 926:37 | 3165:28 | 3887:48 | 7053:16 | 7053:16 | 7979:53 | 43:08 | 94.7048 | 94.0091 | 7979:53 | 43:08 | 94.7048 | 94.0091
22 | Jamkhandi | 207 | 207 | 539:52 | 539:52 | 2082:33 | 1261:30 | 3344:03 | 3344:03 | 3883:55 | 18:46 | 97.7563 | 97.394 | 3883:55 | 18:46 | 97.7563 | 97.394
23 | Mudhol | 192 | 192 | 599:35 | 599:35 | 1788:03 | 1858:22 | 3646:25 | 3646:25 | 4246:00 | 22:07 | 97.3623 | 96.9285 | 4246:00 | 22:07 | 97.3623 | 96.9285
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of May-2021 |  |  |  | Reliability for cumulative period from Apr-21 to May-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 345:25 | 930:20 | 857:21 | 2416:31 | 3273:52 | 5872:43 | 3619:17 | 80:26 | 90.2214 | 89.1897 | 6803:03 | 151:11 | 91.0857 | 89.6736
2 | Dharwad Rural | 82 | 82 | 332:05 | 649:53 | 2072:33 | 5334:33 | 7407:06 | 13186:48 | 7739:11 | 94:23 | 87.8588 | 87.3145 | 13836:41 | 168:44 | 89.0154 | 88.474
3 | Gadag | 96 | 96 | 209:06 | 273:56 | 1659:27 | 4432:54 | 6092:21 | 10115:12 | 6301:27 | 65:38 | 91.4702 | 91.1774 | 10389:08 | 108:13 | 92.8028 | 92.6079
4 | Ron | 54 | 54 | 194:07 | 520:52 | 1007:12 | 1905:37 | 2912:49 | 4705:31 | 3106:56 | 57:32 | 92.7499 | 92.2667 | 5226:23 | 96:47 | 94.0479 | 93.389
5 | Haveri | 197 | 197 | 2616:54 | 4923:50 | 4744:23 | 17554:29 | 22298:52 | 1402.0549 | 1038.1569 | 126:29 | 84.786 | 83.0005 | 1607.2146 | 195:48 | 88.3327 | 86.6255
6 | Ranebennur | 182 | 182 | 1564:24 | 2726:39 | 5561:13 | 12856:57 | 18418:10 | 1225.7653 | 19982:34 | 109:48 | 86.398 | 85.2427 | 1339.3757 | 176:37 | 88.9591 | 87.9357
7 | Sirsi | 54 | 54 | 823:35 | 1191:43 | 785:34 | 3103:34 | 3889:08 | 6548:51 | 4712:43 | 87:16 | 90.3198 | 88.2698 | 7740:34 | 143:21 | 91.7162 | 90.2088
8 | Dandeli | 22 | 22 | 89:01 | 176:37 | 215:38 | 512:45 | 728:23 | 1457:14 | 817:24 | 37:09 | 95.55 | 95.0061 | 1633:51 | 74:16 | 95.4756 | 94.9272
9 | Karwar | 30 | 30 | 591:52 | 1029:21 | 819:00 | 1479:16 | 2298:16 | 3987:11 | 2890:08 | 96:20 | 89.7031 | 87.0514 | 5016:32 | 167:13 | 90.9217 | 88.578
10 | Honnavar | 40 | 40 | 904:45 | 1278:44 | 753:35 | 1417:50 | 2171:25 | 3146:35 | 3076:10 | 76:54 | 92.7036 | 89.6634 | 4425:19 | 110:38 | 94.6267 | 92.4431
11 | Belagavi | 139 | 139 | 537:31 | 917:15 | 2947:42 | 4483:06 | 7430:48 | 13307:00 | 7968:19 | 57:20 | 92.8147 | 92.2949 | 14224:15 | 102:20 | 93.4608 | 93.0101
12 | Bailhongal | 192 | 192 | 1911:22 | 4391:12 | 2935:07 | 9036:49 | 11971:56 | 17902:26 | 13883:18 | 72:19 | 91.6191 | 90.2811 | 22293:38 | 116:07 | 93.631 | 92.0688
13 | Ramdurg | 76 | 76 | 296:09 | 978:44 | 1660:19 | 3163:15 | 4823:34 | 8509:44 | 5119:43 | 67:22 | 91.4694 | 90.9456 | 9488:28 | 124:51 | 92.3518 | 91.4721
14 | Ghataprabha | 161 | 161 | 234:39 | 483:32 | 1640:33 | 3548:34 | 5189:07 | 8337:49 | 5423:46 | 33:41 | 95.6679 | 95.472 | 8821:21 | 54:47 | 96.4626 | 96.2574
15 | Raibag | 176 | 176 | 403:40 | 951:56 | 5242:50 | 2628:37 | 7871:27 | 13890:30 | 8275:07 | 47:01 | 93.9887 | 93.6804 | 14842:26 | 84:20 | 94.6091 | 94.2396
16 | Athani | 194 | 194 | 1060:50 | 1469:09 | 3284:57 | 2769:08 | 6054:05 | 10799:33 | 7114:55 | 36:40 | 95.8056 | 95.0706 | 12268:42 | 63:14 | 96.1976 | 95.6803
17 | Chikkodi | 190 | 190 | 860:20 | 1270:08 | 2242:22 | 3240:56 | 5483:18 | 9431:24 | 6343:38 | 33:23 | 96.121 | 95.5124 | 10701:32 | 56:19 | 96.6094 | 96.1527
18 | Vijayapur | 159 | 159 | 193:43 | 479:07 | 1843:46 | 4837:01 | 6680:47 | 10458:49 | 6874:30 | 43:14 | 94.3525 | 94.1887 | 10937:56 | 68:48 | 95.5069 | 95.3011
19 | Indi | 254 | 254 | 1265:07 | 2892:45 | 3532:05 | 6792:26 | 10324:31 | 18483:35 | 11589:38 | 45:38 | 94.5366 | 93.8671 | 21376:20 | 84:10 | 95.0294 | 94.2514
20 | B.Bagewadi | 138 | 138 | 408:09 | 1105:04 | 2471:21 | 4411:40 | 6883:01 | 10737:33 | 7291:10 | 52:50 | 93.2961 | 92.8986 | 11842:37 | 85:49 | 94.6852 | 94.1382
21 | Bagalkot | 185 | 185 | 975:40 | 1902:17 | 4408:55 | 8155:52 | 12564:47 | 19618:03 | 13540:27 | 73:11 | 90.8713 | 90.1624 | 21520:20 | 116:20 | 92.7566 | 92.0542
22 | Jamkhandi | 207 | 207 | 321:57 | 861:49 | 2086:05 | 2202:10 | 4288:15 | 7632:18 | 4610:12 | 22:16 | 97.2156 | 97.0065 | 8494:07 | 41:02 | 97.4815 | 97.1971
23 | Mudhol | 192 | 192 | 320:55 | 920:30 | 2027:13 | 2845:01 | 4872:14 | 8518:39 | 5193:09 | 27:03 | 96.5892 | 96.3646 | 9439:09 | 49:10 | 96.9694 | 96.6419
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of June-2021 |  |  |  | Reliability for cumulative period from Apr-21 to June-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 95:05 | 1025:25 | 1251:29 | 2152:30 | 3403:59 | 9276:42 | 3499:04 | 77:45 | 89.4939 | 89.2004 | 10302:07 | 228:56 | 90.5609 | 89.5176
2 | Dharwad Rural | 81 | 81 | 110:32 | 760:25 | 1841:45 | 3486:55 | 5328:40 | 18515:28 | 5439:12 | 67:09 | 90.8631 | 90.6735 | 19275:53 | 237:58 | 89.5336 | 89.1038
3 | Gadag | 98 | 98 | 52:25 | 326:21 | 2425:07 | 3470:18 | 5895:25 | 16010:37 | 5947:50 | 60:42 | 91.6448 | 91.5705 | 16336:58 | 166:42 | 92.5195 | 92.367
4 | Ron | 54 | 54 | 293:05 | 813:57 | 830:25 | 1140:30 | 1970:55 | 6676:26 | 2264:00 | 41:56 | 94.9308 | 94.177 | 7490:23 | 138:43 | 94.3389 | 93.6488
5 | Haveri | 196 | 196 | 1351:53 | 6275:43 | 3361:49 | 17410:54 | 20772:43 | 2267.5847 | 22124:36 | 112:53 | 85.2801 | 84.3221 | 2529.0729 | 309:41 | 87.2865 | 85.8204
6 | Ranebennur | 182 | 182 | 542:50 | 3269:29 | 4781:39 | 10194:56 | 14976:35 | 1849.7896 | 15519:25 | 85:16 | 88.571 | 88.1567 | 1986.0181 | 261:54 | 88.8311 | 88.0086
7 | Sirsi | 54 | 54 | 737:16 | 1928:59 | 1026:00 | 3492:24 | 4518:24 | 11067:15 | 5255:40 | 97:20 | 88.3786 | 86.4823 | 12996:14 | 240:40 | 90.6159 | 88.9803
8 | Dandeli | 22 | 22 | 345:38 | 522:15 | 282:41 | 645:37 | 928:18 | 2385:32 | 1273:56 | 57:54 | 94.1395 | 91.9575 | 2907:47 | 132:10 | 95.0351 | 93.9482
9 | Karwar | 30 | 30 | 474:58 | 1504:19 | 468:19 | 633:22 | 1101:41 | 5088:52 | 1576:39 | 52:33 | 94.8996 | 92.7007 | 6593:11 | 219:46 | 92.2331 | 89.9371
10 | Honnavar | 40 | 40 | 524:11 | 1802:55 | 817:25 | 1357:17 | 2174:42 | 5321:17 | 2698:53 | 67:28 | 92.449 | 90.6289 | 7124:12 | 178:06 | 93.9088 | 91.845
11 | Belagavi | 139 | 139 | 254:31 | 1171:46 | 2929:35 | 3390:10 | 6319:45 | 19626:45 | 6574:16 | 47:18 | 93.6853 | 93.431 | 20798:31 | 149:38 | 93.5348 | 93.1488
12 | Bailhongal | 192 | 192 | 1335:25 | 5726:37 | 3566:16 | 7985:52 | 11552:08 | 1227.2736 | 12887:33 | 67:07 | 91.6434 | 90.6774 | 1465.8826 | 183:14 | 92.9758 | 91.6101
13 | Ramdurg | 76 | 76 | 359:00 | 1337:44 | 1456:51 | 3460:44 | 4917:35 | 13427:19 | 5276:35 | 69:26 | 91.0132 | 90.3571 | 14765:03 | 194:17 | 91.9105 | 91.1045
14 | Ghataprabha | 161 | 161 | 173:24 | 656:56 | 1422:15 | 2700:41 | 4122:56 | 12460:45 | 4296:20 | 26:41 | 96.4433 | 96.2937 | 13117:41 | 81:29 | 96.4562 | 96.2694
15 | Raibag | 176 | 176 | 289:54 | 1241:50 | 4980:59 | 1692:24 | 6673:23 | 20563:53 | 6963:17 | 39:34 | 94.7338 | 94.505 | 21805:43 | 123:54 | 94.6502 | 94.3271
16 | Athani | 194 | 194 | 667:32 | 2136:41 | 3211:25 | 1890:56 | 5102:21 | 15901:54 | 5769:53 | 29:44 | 96.3471 | 95.8692 | 18038:35 | 92:59 | 96.2469 | 95.7426
17 | Chikkodi | 190 | 190 | 266:35 | 1536:43 | 1769:35 | 2326:00 | 4095:35 | 13526:59 | 4362:10 | 22:58 | 97.0062 | 96.8113 | 15063:42 | 79:17 | 96.7402 | 96.3698
18 | Vijayapur | 166 | 166 | 354:16 | 833:23 | 2637:35 | 6059:39 | 8697:14 | 19156:03 | 9051:30 | 54:32 | 92.7232 | 92.4268 | 19989:26 | 120:25 | 94.7162 | 94.4863
19 | Indi | 254 | 254 | 1118:39 | 4011:24 | 4127:09 | 9719:14 | 13846:23 | 1347.0819 | 14965:02 | 58:55 | 92.4287 | 91.817 | 1514.2236 | 143:05 | 94.172 | 93.4489
20 | B.Bagewadi | 139 | 139 | 1367:18 | 2472:22 | 2516:08 | 4805:03 | 7321:11 | 18058:44 | 8688:29 | 62:30 | 92.6847 | 91.3185 | 20531:06 | 147:42 | 94.0513 | 93.2369
21 | Bagalkot | 185 | 185 | 899:28 | 2801:45 | 4764:24 | 8262:16 | 13026:40 | 1360.1965 | 13926:08 | 75:17 | 90.2202 | 89.5449 | 1476.9361 | 191:36 | 91.9204 | 91.227
22 | Jamkhandi | 207 | 207 | 450:58 | 1312:47 | 2123:00 | 1826:03 | 3949:03 | 11581:21 | 4400:01 | 21:15 | 97.3503 | 97.0478 | 12894:08 | 62:17 | 97.4383 | 97.1479
23 | Mudhol | 192 | 192 | 210:43 | 1131:13 | 2707:54 | 3526:57 | 6234:51 | 14753:30 | 6445:34 | 33:34 | 95.4898 | 95.3374 | 15884:43 | 82:44 | 96.4816 | 96.2119
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of July-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of July-2021 |  |  |  | Reliability for cumulative period from Apr-21 to July-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 93:25 | 1118:50 | 813:25 | 2251:22 | 3064:47 | 12341:29 | 3158:12 | 70:11 | 90.8459 | 90.5669 | 13460:19 | 299:07 | 90.6334 | 89.7842
2 | Dharwad Rural | 81 | 81 | 95:04 | 855:29 | 1822:48 | 3664:06 | 5486:54 | 1000.0986 | 5581:58 | 68:55 | 90.8952 | 90.7375 | 1035.7437 | 306:53 | 89.8796 | 89.5189
3 | Gadag | 98 | 98 | 83:10 | 409:31 | 1737:37 | 3181:16 | 4918:53 | 20929:30 | 5002:03 | 51:02 | 93.2537 | 93.1396 | 21339:01 | 217:45 | 92.7061 | 92.5634
4 | Ron | 54 | 54 | 259:27 | 1073:24 | 962:05 | 1173:26 | 2135:31 | 8811:57 | 2394:58 | 44:21 | 94.6846 | 94.0388 | 9885:21 | 183:04 | 94.4268 | 93.7479
5 | Haveri | 198 | 198 | 671:52 | 6947:35 | 3060:03 | 14591:25 | 17651:28 | 3003.0625 | 18323:20 | 92:33 | 88.0176 | 87.5615 | 3292.5451 | 399:06 | 87.568 | 86.3697
6 | Ranebennur | 182 | 182 | 692:10 | 3961:39 | 3978:32 | 9817:44 | 13796:16 | 2424.634 | 14488:26 | 79:36 | 89.8113 | 89.3002 | 2589.7028 | 341:30 | 89.0802 | 88.3368
7 | Sirsi | 54 | 54 | 362:05 | 2291:04 | 577:24 | 2910:38 | 3488:02 | 14555:17 | 3850:07 | 71:18 | 91.3181 | 90.4169 | 16846:21 | 311:58 | 90.7943 | 89.3453
8 | Dandeli | 22 | 22 | 129:20 | 651:35 | 364:49 | 837:17 | 1202:06 | 3587:38 | 1331:26 | 60:31 | 92.6558 | 91.8656 | 4239:13 | 192:42 | 94.4305 | 93.419
9 | Karwar | 30 | 30 | 244:50 | 1749:09 | 586:47 | 1200:18 | 1787:05 | 6875:57 | 2031:55 | 67:44 | 91.9934 | 90.8964 | 8625:06 | 287:30 | 92.1722 | 90.1809
10 | Honnavar | 40 | 40 | 469:23 | 2272:18 | 528:23 | 873:42 | 1402:05 | 6723:22 | 1871:28 | 46:47 | 95.2887 | 93.7115 | 8995:40 | 224:54 | 94.2594 | 92.3193
11 | Belagavi | 142 | 142 | 780:43 | 1952:29 | 4002:23 | 3047:18 | 7049:41 | 1111.5181 | 7830:24 | 55:09 | 93.3272 | 92.5882 | 1192.8715 | 201:37 | 93.5839 | 93.1143
12 | Bailhongal | 192 | 192 | 1281:34 | 7008:11 | 3902:24 | 6136:38 | 10039:02 | 1645.5667 | 11320:36 | 58:58 | 92.9722 | 92.0751 | 1937.5743 | 242:12 | 92.9749 | 91.7283
13 | Ramdurg | 76 | 76 | 292:22 | 1630:06 | 1775:39 | 3155:42 | 4931:21 | 18358:40 | 5223:43 | 68:44 | 91.2787 | 90.7617 | 19988:46 | 263:01 | 91.75 | 91.0174
14 | Ghataprabha | 162 | 162 | 249:00 | 905:56 | 1607:50 | 3234:54 | 4842:44 | 17303:29 | 5091:44 | 31:26 | 95.9821 | 95.7755 | 18209:25 | 112:24 | 96.3521 | 96.1611
15 | Raibag | 176 | 176 | 702:00 | 1943:50 | 5220:46 | 2407:49 | 7628:35 | 1174.6861 | 8330:35 | 47:20 | 94.1742 | 93.6381 | 1255.6792 | 171:14 | 94.5292 | 94.152
16 | Athani | 194 | 194 | 732:04 | 2868:45 | 3485:49 | 2082:07 | 5567:56 | 21469:50 | 6300:00 | 32:28 | 96.1424 | 95.6352 | 1014.1076 | 125:27 | 96.2203 | 95.7153
17 | Chikkodi | 190 | 190 | 335:15 | 1871:58 | 2092:33 | 3039:43 | 5132:16 | 18659:15 | 5467:31 | 28:47 | 96.3694 | 96.1322 | 20531:13 | 108:04 | 96.646 | 96.3095
18 | Vijayapur | 166 | 166 | 380:45 | 1214:08 | 3032:25 | 5489:01 | 8521:26 | 1153.2285 | 8902:11 | 53:38 | 93.1003 | 92.792 | 1203.8174 | 174:03 | 94.3056 | 94.0558
19 | Indi | 254 | 254 | 1330:55 | 5342:19 | 5025:15 | 8312:16 | 13337:31 | 1902.8118 | 14668:26 | 57:45 | 92.9422 | 92.2379 | 2125.4083 | 200:50 | 93.8595 | 93.1412
20 | B.Bagewadi | 142 | 142 | 681:10 | 3153:32 | 3424:31 | 4588:20 | 8012:51 | 1086.316 | 8694:01 | 61:14 | 92.4155 | 91.7708 | 1217.7132 | 205:49 | 93.7294 | 92.9709
21 | Bagalkot | 185 | 185 | 800:22 | 3602:07 | 3805:08 | 6917:28 | 10722:36 | 1806.9715 | 11522:58 | 62:17 | 92.2097 | 91.6282 | 1957.0597 | 253:53 | 91.9939 | 91.3289
22 | Jamkhandi | 208 | 208 | 668:40 | 1981:27 | 2531:25 | 1916:40 | 4448:05 | 16029:26 | 5116:45 | 24:36 | 97.1257 | 96.6936 | 18010:53 | 86:35 | 97.368 | 97.0427
23 | Mudhol | 192 | 192 | 435:57 | 1567:10 | 2419:01 | 3015:20 | 5434:21 | 20187:51 | 5870:18 | 30:34 | 96.1957 | 95.8905 | 21755:01 | 113:18 | 96.409 | 96.1302
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of August-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of August-2021 |  |  |  | Reliability for cumulative period from Apr-21 to August-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 71:35 | 1190:25 | 966:38 | 1847:37 | 2814:15 | 15155:44 | 2885:50 | 64:08 | 91.5942 | 91.3804 | 16346:09 | 363:15 | 90.828 | 90.1076
2 | Dharwad Rural | 81 | 81 | 56:46 | 912:15 | 1208:22 | 1759:04 | 2967:26 | 1123.7417 | 3024:12 | 37:20 | 95.0759 | 94.9817 | 1161.7521 | 344:13 | 90.9324 | 90.6257
3 | Gadag | 98 | 98 | 46:20 | 455:51 | 1224:53 | 2243:19 | 3468:12 | 1016.5708 | 3514:32 | 35:52 | 95.2433 | 95.1798 | 1035.5646 | 253:36 | 93.2201 | 93.0935
4 | Ron | 54 | 54 | 61:25 | 1134:49 | 444:45 | 501:20 | 946:05 | 9758:02 | 1007:30 | 18:39 | 97.6452 | 97.4923 | 10892:51 | 201:43 | 95.0789 | 94.5066
5 | Haveri | 197 | 197 | 800:48 | 7748:23 | 2080:08 | 8576:39 | 10656:47 | 3447.0951 | 11457:35 | 58:10 | 92.7291 | 92.1828 | 3769.9444 | 459:17 | 88.5634 | 87.4923
6 | Ranebennur | 182 | 182 | 507:24 | 4469:03 | 2926:17 | 5217:06 | 8143:23 | 2763.9417 | 8650:47 | 47:32 | 93.986 | 93.6113 | 2950.1521 | 389:02 | 90.0742 | 89.4055
7 | Sirsi | 54 | 54 | 271:19 | 2562:23 | 533:51 | 1378:00 | 1911:51 | 16467:08 | 2183:10 | 40:26 | 95.2413 | 94.566 | 19029:31 | 352:24 | 91.6953 | 90.4031
8 | Dandeli | 22 | 22 | 69:56 | 721:31 | 215:09 | 463:36 | 678:45 | 4266:23 | 748:41 | 34:02 | 95.8532 | 95.4259 | 4987:54 | 226:43 | 94.7188 | 93.8256
9 | Karwar | 30 | 30 | 265:47 | 2014:56 | 326:02 | 480:36 | 806:38 | 7682:35 | 1072:25 | 35:45 | 96.3861 | 95.1953 | 9697:31 | 323:15 | 93.026 | 91.1969
10 | Honnavar | 40 | 40 | 285:02 | 2557:20 | 569:25 | 526:02 | 1095:27 | 7818:49 | 1380:29 | 34:31 | 96.3191 | 95.3613 | 10376:09 | 259:24 | 94.6767 | 92.9356
11 | Belagavi | 142 | 142 | 391:31 | 2344:00 | 2638:35 | 1673:22 | 4311:57 | 1291.1826 | 4703:28 | 33:07 | 95.9186 | 95.548 | 1388.8493 | 234:44 | 94.057 | 93.6074
12 | Bailhongal | 192 | 192 | 965:33 | 7973:44 | 3175:14 | 3026:37 | 6201:51 | 1903.9771 | 7167:24 | 37:20 | 95.6584 | 94.9825 | 2236.216 | 279:32 | 93.5186 | 92.3876
13 | Ramdurg | 78 | 78 | 386:55 | 2017:01 | 1506:52 | 2282:11 | 3789:03 | 22147:43 | 4175:58 | 53:32 | 93.4708 | 92.804 | 1006.8639 | 309:48 | 92.2673 | 91.5631
14 | Ghataprabha | 162 | 162 | 182:12 | 1088:08 | 1519:29 | 1250:35 | 2770:04 | 20073:33 | 2952:16 | 18:13 | 97.7017 | 97.5506 | 21161:41 | 130:38 | 96.6255 | 96.4426
15 | Raibag | 176 | 176 | 374:49 | 2318:39 | 5352:00 | 1179:54 | 6531:54 | 1446.8486 | 6906:43 | 39:15 | 95.0117 | 94.7254 | 1543.459 | 210:28 | 94.627 | 94.2682
16 | Athani | 197 | 197 | 728:11 | 3596:56 | 4244:31 | 1419:21 | 5663:52 | 1130.5708 | 6392:03 | 32:27 | 96.1357 | 95.6389 | 1280.4431 | 156:00 | 96.2491 | 95.7518
17 | Chikkodi | 190 | 190 | 142:40 | 2014:38 | 1750:05 | 892:44 | 2642:49 | 21302:04 | 2785:29 | 14:40 | 98.1304 | 98.0295 | 23316:42 | 122:43 | 96.9467 | 96.658
18 | Vijayapur | 173 | 173 | 416:33 | 1630:41 | 1904:16 | 5390:02 | 7294:18 | 1457.1576 | 7710:51 | 44:34 | 94.3329 | 94.0092 | 1525.1028 | 211:34 | 94.4949 | 94.2382
19 | Indi | 254 | 254 | 524:50 | 5867:09 | 3612:25 | 7258:48 | 10871:13 | 2355.7792 | 11396:03 | 44:52 | 94.2473 | 93.9696 | 2600.2437 | 245:42 | 93.9381 | 93.309
20 | B.Bagewadi | 142 | 142 | 284:18 | 3437:50 | 1870:58 | 2983:21 | 4854:19 | 1288.5792 | 5138:37 | 36:11 | 95.4052 | 95.1361 | 1431.8222 | 242:00 | 94.069 | 93.4096
21 | Bagalkot | 187 | 187 | 462:46 | 4064:53 | 2882:47 | 4885:10 | 7767:57 | 2130.6361 | 8230:43 | 44:01 | 94.4167 | 94.0841 | 2300.0062 | 295:11 | 92.5531 | 91.9611
22 | Jamkhandi | 210 | 210 | 792:19 | 2773:46 | 2158:06 | 1436:09 | 3594:15 | 19623:41 | 4386:34 | 20:53 | 97.6995 | 97.1924 | 22397:27 | 106:39 | 97.4552 | 97.0955
23 | Mudhol | 192 | 192 | 176:02 | 1743:12 | 2566:55 | 2264:56 | 4831:51 | 1042.4875 | 5007:53 | 26:05 | 96.6175 | 96.4943 | 1115.1208 | 139:23 | 96.4512 | 96.204
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of September-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of September-2021 |  |  |  | Reliability for cumulative period from Apr-21 to September-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 55:40 | 1246:05 | 589:48 | 1309:49 | 1899:37 | 17055:21 | 1955:17 | 43:27 | 94.137 | 93.9652 | 18301:26 | 406:42 | 91.3705 | 90.74
2 | Dharwad Rural | 81 | 81 | 361:25 | 1273:40 | 1765:45 | 2271:11 | 4036:56 | 1291.9472 | 4398:21 | 54:18 | 93.078 | 92.4582 | 1345.0167 | 398:31 | 91.2842 | 90.9262
3 | Gadag | 99 | 99 | 72:45 | 528:36 | 1295:27 | 1753:39 | 3049:06 | 1143.6167 | 3121:51 | 31:32 | 95.7224 | 95.6203 | 1165.6417 | 282:35 | 93.6876 | 93.566
4 | Ron | 54 | 54 | 25:50 | 1160:39 | 649:15 | 640:30 | 1289:45 | 11047:47 | 1315:35 | 24:22 | 96.6827 | 96.6163 | 12208:26 | 226:05 | 95.3418 | 94.8524
5 | Haveri | 197 | 197 | 1020:28 | 8768:51 | 1974:41 | 8174:44 | 10149:25 | 3869.9875 | 11169:53 | 56:42 | 92.8445 | 92.125 | 4235.3562 | 515:59 | 89.2652 | 88.2518
6 | Ranebennur | 182 | 182 | 600:34 | 5069:37 | 2557:33 | 4214:10 | 6771:43 | 3046.0965 | 7372:17 | 40:30 | 94.8323 | 94.374 | 3257.3306 | 429:32 | 90.8542 | 90.22
7 | Sirsi | 54 | 54 | 252:43 | 2815:06 | 479:31 | 1456:23 | 1935:54 | 18403:02 | 2188:37 | 40:32 | 95.0208 | 94.3708 | 21218:08 | 392:56 | 92.2405 | 91.0535
8 | Dandeli | 22 | 22 | 28:05 | 749:36 | 184:30 | 510:17 | 694:47 | 4961:10 | 722:52 | 32:51 | 95.6137 | 95.4364 | 5710:46 | 259:35 | 94.8655 | 94.0897
9 | Karwar | 30 | 30 | 313:06 | 2328:02 | 270:51 | 491:58 | 762:49 | 8445:24 | 1075:55 | 35:52 | 96.4684 | 95.0189 | 10773:26 | 359:07 | 93.5903 | 91.8234
10 | Honnavar | 40 | 40 | 318:38 | 2875:58 | 444:37 | 599:35 | 1044:12 | 8863:01 | 1362:50 | 34:04 | 96.3743 | 95.2679 | 11738:59 | 293:28 | 94.955 | 93.318
11 | Belagavi | 142 | 142 | 834:49 | 3178:49 | 2616:15 | 1711:29 | 4327:44 | 1471.5049 | 5162:33 | 36:21 | 95.7671 | 94.9506 | 1603.9556 | 271:05 | 94.3373 | 93.8276
12 | Bailhongal | 192 | 192 | 1363:22 | 9337:06 | 2683:22 | 2804:20 | 5487:42 | 2132.6312 | 6851:04 | 35:41 | 96.0303 | 95.0441 | 2521.6771 | 315:13 | 93.9304 | 92.8231
13 | Ramdurg | 79 | 79 | 396:20 | 2413:21 | 1196:45 | 1676:33 | 2873:18 | 1042.5424 | 3269:38 | 41:23 | 94.9485 | 94.2517 | 1143.0986 | 347:16 | 92.7887 | 92.0931
14 | Ghataprabha | 162 | 162 | 437:26 | 1525:34 | 1555:28 | 1047:51 | 2603:19 | 22676:52 | 3040:45 | 18:46 | 97.7681 | 97.393 | 1008.4347 | 149:24 | 96.8128 | 96.5984
15 | Raibag | 175 | 175 | 494:17 | 2812:56 | 5766:56 | 888:26 | 6655:22 | 1724.1556 | 7149:39 | 40:51 | 94.718 | 94.3257 | 1841.3611 | 252:32 | 94.6162 | 94.2502
16 | Athani | 197 | 197 | 671:12 | 4268:08 | 3325:11 | 1316:02 | 4641:13 | 1323.9549 | 5312:25 | 26:58 | 96.7279 | 96.2546 | 1501.7937 | 182:58 | 96.3276 | 95.8343
17 | Chikkodi | 191 | 191 | 278:30 | 2293:08 | 1726:10 | 1269:13 | 2995:23 | 1012.3937 | 3273:53 | 17:08 | 97.8219 | 97.6193 | 1107.941 | 139:13 | 97.1036 | 96.8302
18 | Vijayapur | 173 | 173 | 249:29 | 1880:10 | 1755:07 | 5499:51 | 7254:58 | 1759.4479 | 7504:27 | 43:23 | 94.1755 | 93.9752 | 1837.7882 | 254:57 | 94.4425 | 94.1951
19 | Indi | 254 | 254 | 1768:59 | 7636:08 | 3435:12 | 8749:58 | 12185:10 | 2863.4944 | 13954:09 | 54:56 | 93.3371 | 92.3698 | 3181.6667 | 300:38 | 93.8396 | 93.1551
20 | B.Bagewadi | 142 | 142 | 331:39 | 3769:29 | 1917:14 | 2887:53 | 4805:07 | 1488.7924 | 5136:46 | 36:10 | 95.3002 | 94.9758 | 1645.8542 | 278:10 | 94.2708 | 93.6664
21 | Bagalkot | 187 | 187 | 1009:47 | 5074:40 | 2848:23 | 5345:38 | 8194:01 | 2472.0535 | 9203:48 | 49:13 | 93.9141 | 93.1641 | 2683.4979 | 344:24 | 92.7762 | 92.1583
22 | Jamkhandi | 210 | 210 | 481:10 | 3254:56 | 1983:01 | 1324:47 | 3307:48 | 22931:29 | 3788:58 | 18:03 | 97.8123 | 97.4941 | 1091.1007 | 124:42 | 97.5137 | 97.1608
23 | Mudhol | 193 | 193 | 209:37 | 1952:49 | 2298:50 | 1818:47 | 4117:37 | 1214.0549 | 4327:14 | 22:25 | 97.0368 | 96.886 | 1295.4222 | 161:05 | 96.5626 | 96.3322
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of October-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of October-2021 |  |  |  | Reliability for cumulative period from Apr-21 to October-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 165:55 | 1412:00 | 778:41 | 1859:29 | 2638:10 | 19693:31 | 2804:05 | 62:19 | 92.1202 | 91.6246 | 21105:31 | 469:01 | 91.4791 | 90.8682
2 | Dharwad Rural | 85 | 85 | 1600:07 | 2873:47 | 1299:33 | 1782:31 | 3082:04 | 1420.3667 | 4682:11 | 55:05 | 95.1264 | 92.5962 | 1540.1076 | 434:51 | 92.1915 | 91.5332
3 | Gadag | 99 | 99 | 104:55 | 633:31 | 1294:02 | 3233:15 | 4527:17 | 1332.2535 | 4632:12 | 46:47 | 93.8535 | 93.711 | 1358.65 | 329:22 | 93.7116 | 93.587
4 | Ron | 54 | 54 | 238:42 | 1399:21 | 512:10 | 680:46 | 1192:56 | 12240:43 | 1431:38 | 26:31 | 97.0307 | 96.4366 | 13640:04 | 252:36 | 95.5864 | 95.0819
5 | Haveri | 197 | 197 | 1391:05 | 10159:56 | 2352:54 | 13305:50 | 15658:44 | 4522.4347 | 17049:49 | 86:33 | 89.3164 | 88.3673 | 4945.7653 | 602:32 | 89.2727 | 88.2685
6 | Ranebennur | 182 | 182 | 819:44 | 5889:21 | 2774:58 | 12226:10 | 15001:08 | 3671.1437 | 15820:52 | 86:56 | 88.9215 | 88.3162 | 3916.5333 | 516:28 | 90.5742 | 89.9442
7 | Sirsi | 54 | 54 | 404:59 | 3220:05 | 602:09 | 1818:12 | 2420:21 | 20823:23 | 2825:20 | 52:19 | 93.9756 | 92.9676 | 1001.8111 | 445:15 | 92.4919 | 91.3308
8 | Dandeli | 22 | 22 | 32:17 | 781:53 | 273:31 | 536:48 | 810:19 | 5771:29 | 842:36 | 38:18 | 95.0494 | 94.8522 | 6553:22 | 297:53 | 94.8921 | 94.2001
9 | Karwar | 30 | 30 | 280:16 | 2608:18 | 177:50 | 469:55 | 647:45 | 9093:09 | 928:01 | 30:56 | 97.0979 | 95.8422 | 11701:27 | 390:03 | 94.0984 | 92.4056
10 | Honnavar | 40 | 40 | 304:25 | 3180:23 | 344:23 | 437:27 | 781:50 | 9644:51 | 1086:15 | 27:09 | 97.3729 | 96.35 | 12825:14 | 320:38 | 95.3053 | 93.7572
11 | Belagavi | 142 | 142 | 823:16 | 4002:05 | 2566:29 | 3748:03 | 6314:32 | 1734.6104 | 7137:48 | 50:16 | 94.023 | 93.2438 | 1901.3639 | 321:21 | 94.2918 | 93.743
12 | Bailhongal | 192 | 192 | 1284:55 | 10622:01 | 3175:11 | 4850:07 | 8025:18 | 2467.0187 | 9310:13 | 48:29 | 94.3819 | 93.4824 | 2909.6028 | 363:42 | 93.9958 | 92.9186
13 | Ramdurg | 80 | 80 | 282:56 | 2696:17 | 1335:49 | 2076:57 | 3412:46 | 1184.741 | 3695:42 | 46:12 | 94.2662 | 93.7908 | 1297.0861 | 389:08 | 93.0798 | 92.4236
14 | Ghataprabha | 162 | 162 | 736:07 | 2261:41 | 1261:04 | 2297:26 | 3558:30 | 1093.1403 | 4294:37 | 26:31 | 97.0476 | 96.4368 | 1187.3771 | 175:54 | 96.8468 | 96.575
15 | Raibag | 174 | 174 | 672:17 | 3485:13 | 5814:16 | 2453:51 | 8268:07 | 2068.6604 | 8940:24 | 51:23 | 93.6132 | 93.0939 | 2213.8778 | 305:22 | 94.4445 | 94.0545
16 | Athani | 197 | 197 | 843:24 | 5111:32 | 3247:52 | 1788:22 | 5036:14 | 1533.7979 | 5879:38 | 29:51 | 96.5639 | 95.9885 | 1746.7785 | 212:48 | 96.3618 | 95.8566
17 | Chikkodi | 192 | 192 | 868:55 | 3162:03 | 1762:31 | 1686:53 | 3449:24 | 1156.1187 | 4318:19 | 22:29 | 97.5853 | 96.977 | 1287.8708 | 160:59 | 97.1862 | 96.8656
18 | Vijayapur | 173 | 173 | 593:36 | 2473:46 | 1282:36 | 3128:01 | 4410:37 | 1943.2236 | 5004:13 | 28:56 | 96.5733 | 96.1121 | 2046.2972 | 283:53 | 94.7512 | 94.4728
19 | Indi | 254 | 254 | 726:11 | 8362:19 | 2993:30 | 5469:11 | 8462:41 | 3216.1062 | 9188:52 | 36:11 | 95.5218 | 95.1375 | 3564.5361 | 336:48 | 94.0833 | 93.4422
20 | B.Bagewadi | 142 | 142 | 404:36 | 4174:05 | 1704:01 | 2921:05 | 4625:06 | 1681.5049 | 5029:42 | 35:25 | 95.6222 | 95.2392 | 1855.425 | 313:36 | 94.4665 | 93.8942
21 | Bagalkot | 188 | 188 | 428:49 | 5503:29 | 2972:13 | 4051:53 | 7024:06 | 2764.7243 | 7452:55 | 39:39 | 94.9782 | 94.6716 | 2994.0361 | 382:13 | 93.128 | 92.5581
22 | Jamkhandi | 211 | 211 | 611:07 | 3866:03 | 3851:35 | 1558:46 | 5410:21 | 1180.9097 | 6021:28 | 28:32 | 96.5536 | 96.1643 | 1341.9951 | 152:39 | 97.3847 | 97.028
23 | Mudhol | 193 | 193 | 210:51 | 2163:40 | 1750:51 | 2139:25 | 3890:16 | 1376.1493 | 4101:07 | 21:15 | 97.2907 | 97.1439 | 1466.3021 | 182:20 | 96.6681 | 96.4498
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of November-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of November-2021 |  |  |  | Reliability for cumulative period from Apr-21 to November-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 45 | 45 | 344:00 | 1756:00 | 874:15 | 1561:24 | 2435:39 | 22129:10 | 2779:39 | 61:46 | 92.4826 | 91.4208 | 23885:10 | 530:47 | 91.6025 | 90.9361
2 | Dharwad Rural | 90 | 90 | 467:26 | 3341:13 | 1976:56 | 3079:14 | 5056:10 | 1631.0403 | 5523:36 | 61:22 | 92.1973 | 91.4759 | 1770.2576 | 472:04 | 92.5727 | 91.9387
3 | Gadag | 99 | 99 | 96:30 | 730:01 | 1165:40 | 3626:51 | 4792:31 | 1531.9417 | 4889:01 | 49:23 | 93.2765 | 93.1411 | 1562.359 | 378:45 | 93.6581 | 93.5322
4 | Ron | 54 | 54 | 85:45 | 1485:06 | 398:55 | 792:55 | 1191:50 | 13432:33 | 1277:35 | 23:40 | 96.9346 | 96.714 | 14917:39 | 276:15 | 95.7522 | 95.2826
5 | Haveri | 196 | 196 | 1370:17 | 11530:13 | 2409:24 | 13666:28 | 16075:52 | 5192.2625 | 17446:09 | 89:01 | 88.6084 | 87.6374 | 5672.6882 | 694:37 | 89.143 | 88.1384
6 | Ranebennur | 191 | 191 | 481:48 | 6371:09 | 3555:24 | 11084:12 | 14639:36 | 4281.1271 | 15121:24 | 79:10 | 89.3546 | 89.0042 | 4546.5917 | 571:18 | 90.8138 | 90.2442
7 | Sirsi | 55 | 55 | 410:24 | 3630:29 | 577:16 | 1834:22 | 2411:38 | 23235:01 | 2822:02 | 51:19 | 93.91 | 92.8737 | 1119.3958 | 488:28 | 92.7859 | 91.6587
8 | Dandeli | 22 | 22 | 103:05 | 884:58 | 193:23 | 418:15 | 611:38 | 6383:07 | 714:43 | 32:29 | 96.1387 | 95.4879 | 7268:05 | 330:22 | 95.0454 | 94.3585
9 | Karwar | 30 | 30 | 105:22 | 2713:40 | 244:21 | 447:01 | 691:22 | 9784:31 | 796:44 | 26:33 | 96.7992 | 96.3114 | 12498:11 | 416:36 | 94.4305 | 92.8858
10 | Honnavar | 40 | 40 | 275:36 | 3455:59 | 585:02 | 624:12 | 1209:14 | 10854:05 | 1484:50 | 37:07 | 95.8013 | 94.8443 | 14310:04 | 357:45 | 95.3663 | 93.8909
11 | Belagavi | 142 | 142 | 871:19 | 4873:24 | 2537:15 | 3744:20 | 6281:35 | 1996.3431 | 7152:54 | 50:22 | 93.856 | 93.0038 | 2199.4014 | 371:44 | 94.2382 | 93.6522
12 | Bailhongal | 192 | 192 | 1751:16 | 12373:17 | 2493:15 | 5778:34 | 8271:49 | 2811.6778 | 10023:05 | 52:12 | 94.0163 | 92.7495 | 3327.2313 | 415:54 | 93.9983 | 92.8978
13 | Ramdurg | 83 | 83 | 435:13 | 3131:30 | 1246:27 | 2508:33 | 3755:00 | 1341.1993 | 4190:13 | 50:29 | 93.7165 | 92.9883 | 1471.6785 | 425:33 | 93.3774 | 92.7332
14 | Ghataprabha | 162 | 162 | 169:44 | 2431:25 | 998:40 | 2300:31 | 3299:11 | 1230.6063 | 3468:55 | 21:25 | 97.1715 | 97.026 | 1331.9153 | 197:19 | 96.8867 | 96.6305
15 | Raibag | 174 | 174 | 258:41 | 3743:54 | 4639:27 | 1704:55 | 6344:22 | 2333.009 | 6603:03 | 37:57 | 94.9359 | 94.7294 | 2489.0049 | 343:19 | 94.5049 | 94.1374
16 | Athani | 197 | 197 | 641:23 | 5752:55 | 2510:48 | 2335:32 | 4846:20 | 1735.7285 | 5487:43 | 27:51 | 96.5832 | 96.1311 | 1975.4333 | 240:40 | 96.389 | 95.8903
17 | Chikkodi | 192 | 192 | 135:50 | 3297:53 | 1372:22 | 1585:43 | 2958:05 | 1279.3722 | 3093:55 | 16:07 | 97.8602 | 97.7619 | 1416.784 | 177:06 | 97.2691 | 96.9758
18 | Vijayapur | 173 | 173 | 414:30 | 2888:16 | 1511:51 | 3984:46 | 5496:37 | 2172.2493 | 5911:07 | 34:10 | 95.5872 | 95.2544 | 2292.5937 | 318:03 | 94.854 | 94.5689
19 | Indi | 255 | 255 | 810:10 | 9172:29 | 2887:45 | 6386:56 | 9274:41 | 3602.5514 | 10084:51 | 39:33 | 94.9484 | 94.5072 | 3984.7382 | 375:02 | 94.21 | 93.5957
20 | B.Bagewadi | 142 | 142 | 442:01 | 4616:06 | 1753:06 | 2921:52 | 4674:58 | 1876.2951 | 5116:59 | 36:02 | 95.4275 | 94.9951 | 2068.6326 | 349:38 | 94.5847 | 94.0296
21 | Bagalkot | 187 | 187 | 726:07 | 6229:36 | 2756:10 | 4616:27 | 7372:37 | 3071.9167 | 8098:44 | 43:19 | 94.5242 | 93.9849 | 3331.4833 | 427:34 | 93.2675 | 92.6986
22 | Jamkhandi | 212 | 212 | 337:48 | 4203:51 | 2008:21 | 1643:20 | 3651:41 | 1333.0632 | 3989:29 | 18:49 | 97.6076 | 97.3863 | 1508.2236 | 170:45 | 97.4229 | 97.0843
23 | Mudhol | 194 | 194 | 381:30 | 2545:10 | 1620:53 | 2238:54 | 3859:47 | 1536.9736 | 4241:17 | 21:52 | 97.2367 | 96.9636 | 1643.0222 | 203:16 | 96.7531 | 96.529
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of December-2021 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of December-2021 |  |  |  | Reliability for cumulative period from Apr-21 to December-21
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 100:20 | 1856:20 | 1248:03 | 473:58 | 1722:01 | 23851:11 | 1822:21 | 39:37 | 94.9684 | 94.6752 | 1071.1465 | 558:52 | 92.1439 | 91.5324
2 | Dharwad Rural | 90 | 90 | 328:03 | 3669:16 | 1947:15 | 1530:20 | 3477:35 | 1775.9396 | 3805:38 | 42:17 | 94.8065 | 94.3166 | 1928.8257 | 514:21 | 92.8245 | 92.2068
3 | Gadag | 99 | 99 | 135:35 | 865:36 | 1314:42 | 1693:13 | 3007:55 | 1657.2715 | 3143:30 | 31:45 | 95.9163 | 95.7322 | 1693.3382 | 410:30 | 93.9127 | 93.7802
4 | Ron | 54 | 54 | 63:53 | 1548:59 | 561:00 | 339:48 | 900:48 | 14333:21 | 964:41 | 17:52 | 97.7579 | 97.5989 | 15882:20 | 294:07 | 95.9783 | 95.5437
5 | Haveri | 197 | 197 | 1371:14 | 12901:27 | 2959:23 | 5428:53 | 8388:16 | 5541.7736 | 9759:30 | 49:32 | 94.2769 | 93.3413 | 6079.334 | 740:38 | 89.7706 | 88.7783
6 | Ranebennur | 191 | 191 | 757:35 | 7128:44 | 3618:21 | 2792:49 | 6411:10 | 4548.259 | 7168:45 | 37:32 | 95.4884 | 94.9553 | 4845.2896 | 608:50 | 91.3408 | 90.7753
7 | Sirsi | 55 | 55 | 356:23 | 3986:52 | 736:04 | 1022:31 | 1758:35 | 1041.4 | 2114:58 | 38:27 | 95.7024 | 94.8315 | 1207.5194 | 526:55 | 93.1147 | 92.0164
8 | Dandeli | 22 | 22 | 228:26 | 1113:24 | 165:31 | 284:28 | 449:59 | 6833:06 | 678:25 | 30:50 | 97.2508 | 95.8552 | 7946:30 | 361:12 | 95.294 | 94.5272
9 | Karwar | 30 | 30 | 188:15 | 2901:55 | 320:24 | 234:51 | 555:15 | 10339:46 | 743:30 | 24:47 | 97.5123 | 96.6689 | 13241:41 | 441:23 | 94.7779 | 93.3123
10 | Honnavar | 40 | 40 | 364:08 | 3820:07 | 437:37 | 304:39 | 742:16 | 11596:21 | 1106:24 | 27:40 | 97.5058 | 96.2823 | 15416:28 | 385:25 | 95.6074 | 94.1604
11 | Belagavi | 142 | 142 | 844:41 | 5718:05 | 2470:10 | 1972:50 | 4443:00 | 2181.4681 | 5287:41 | 37:14 | 95.7945 | 94.995 | 2419.7215 | 408:58 | 94.4137 | 93.8035
12 | Bailhongal | 192 | 192 | 767:33 | 13140:50 | 2657:12 | 2362:21 | 5019:33 | 3020.8257 | 5787:06 | 30:08 | 96.4861 | 95.9488 | 3568.3604 | 446:03 | 94.2787 | 93.2417
13 | Ramdurg | 84 | 84 | 318:40 | 3450:10 | 1037:56 | 1072:26 | 2110:22 | 1429.1313 | 2429:02 | 28:55 | 96.6232 | 96.1133 | 1572.8882 | 449:24 | 93.8133 | 93.191
14 | Ghataprabha | 162 | 162 | 222:42 | 2654:07 | 907:52 | 736:07 | 1643:59 | 1299.1056 | 1866:41 | 11:31 | 98.636 | 98.4512 | 1409.6938 | 208:51 | 97.0839 | 96.8357
15 | Raibag | 174 | 174 | 442:52 | 4186:46 | 5391:27 | 967:51 | 6359:18 | 2597.9799 | 6802:10 | 39:06 | 95.0877 | 94.7456 | 2772.4285 | 382:24 | 94.5706 | 94.206
16 | Athani | 197 | 197 | 365:10 | 6118:05 | 2212:08 | 805:21 | 3017:29 | 1861.4569 | 3382:39 | 17:10 | 97.9412 | 97.6921 | 2116.3771 | 257:50 | 96.564 | 96.0934
17 | Chikkodi | 192 | 192 | 528:55 | 3826:48 | 1309:57 | 917:53 | 2227:50 | 1372.1986 | 2756:45 | 14:21 | 98.4404 | 98.0702 | 1531.6486 | 191:27 | 97.4011 | 97.0992
18 | Vijayapur | 173 | 173 | 161:09 | 3049:25 | 1295:36 | 2158:12 | 3453:48 | 2316.1576 | 3614:57 | 20:54 | 97.3166 | 97.1914 | 2443.2167 | 338:57 | 95.1316 | 94.8645
19 | Indi | 255 | 255 | 837:32 | 10010:01 | 2233:16 | 4523:36 | 6756:52 | 3884.0875 | 7594:24 | 29:47 | 96.4385 | 95.997 | 4301.1715 | 404:49 | 94.4612 | 93.8664
20 | B.Bagewadi | 142 | 142 | 175:07 | 4791:13 | 1337:17 | 1522:17 | 2859:34 | 1995.4437 | 3034:41 | 21:22 | 97.2933 | 97.1276 | 2195.0778 | 371:00 | 94.89 | 94.3788
21 | Bagalkot | 187 | 187 | 378:35 | 6608:11 | 2598:56 | 2399:00 | 4997:56 | 3280.1639 | 5376:31 | 28:45 | 96.4077 | 96.1356 | 3555.5049 | 456:19 | 93.6215 | 93.086
22 | Jamkhandi | 212 | 212 | 396:10 | 4600:01 | 1781:58 | 1050:56 | 2832:54 | 1451.1007 | 3229:04 | 15:14 | 98.2039 | 97.9528 | 1642.7681 | 185:58 | 97.511 | 97.1822
23 | Mudhol | 194 | 194 | 215:27 | 2760:37 | 1286:23 | 1283:52 | 2570:15 | 1644.0674 | 2785:42 | 14:22 | 98.2193 | 98.07 | 1759.0931 | 217:37 | 96.9183 | 96.7027
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of January-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of January-2022 |  |  |  | Reliability for cumulative period from Apr-21 to Jan-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 63:00 | 1919:20 | 664:18 | 363:15 | 1027:33 | 1036.6139 | 1090:33 | 23:42 | 96.9976 | 96.8135 | 1116.5861 | 582:34 | 91.8054 | 91.1732
2 | Dharwad Rural | 90 | 90 | 441:41 | 4110:57 | 1673:18 | 744:09 | 2417:27 | 1876.6667 | 2859:08 | 31:46 | 96.3897 | 95.7301 | 2047.9562 | 546:07 | 92.4175 | 91.7254
3 | Gadag | 101 | 101 | 18:10 | 883:46 | 1023:53 | 484:14 | 1508:07 | 1720.1097 | 1526:17 | 15:07 | 97.9525 | 97.9278 | 1756.9333 | 417:29 | 93.6819 | 93.5466
4 | Ron | 54 | 54 | 104:17 | 1653:16 | 512:57 | 196:44 | 709:41 | 15043:02 | 813:58 | 15:04 | 98.2336 | 97.974 | 16696:18 | 309:11 | 95.7792 | 95.3153
5 | Haveri | 197 | 197 | 1183:08 | 14084:35 | 2912:47 | 1978:00 | 4890:47 | 5745.5562 | 6073:55 | 30:50 | 96.6631 | 95.8559 | 6332.4139 | 771:28 | 89.3945 | 88.3112
6 | Ranebennur | 192 | 192 | 450:19 | 7579:03 | 3750:28 | 1902:39 | 5653:07 | 4783.8056 | 6103:26 | 31:47 | 96.0218 | 95.705 | 5099.5993 | 637:27 | 90.8923 | 90.2911
7 | Sirsi | 56 | 56 | 313:12 | 4300:04 | 516:13 | 848:28 | 1364:41 | 1098.2618 | 1677:53 | 29:58 | 96.665 | 95.8996 | 1277.4312 | 547:28 | 92.7388 | 91.5542
8 | Dandeli | 22 | 22 | 11:06 | 1124:30 | 161:48 | 184:43 | 346:31 | 7179:37 | 357:37 | 16:15 | 97.883 | 97.8151 | 8304:07 | 377:28 | 95.0554 | 94.2809
9 | Karwar | 29 | 29 | 89:55 | 2991:50 | 292:33 | 134:31 | 427:04 | 10766:50 | 516:59 | 17:50 | 98.0866 | 97.6838 | 13758:40 | 474:26 | 94.5622 | 93.0512
10 | Honnavar | 40 | 40 | 249:24 | 4069:31 | 372:45 | 242:47 | 615:32 | 12211:53 | 864:56 | 21:37 | 97.9317 | 97.0936 | 16281:24 | 407:02 | 95.3743 | 93.8328
11 | Belagavi | 149 | 149 | 612:43 | 6330:48 | 1938:35 | 1308:01 | 3246:36 | 2316.7431 | 3859:19 | 25:54 | 96.927 | 96.347 | 2580.5264 | 415:39 | 94.0672 | 93.3917
12 | Bailhongal | 192 | 192 | 1253:34 | 14394:24 | 2683:35 | 1267:18 | 3950:53 | 3185.4458 | 5204:27 | 27:06 | 97.2342 | 96.3567 | 3785.2125 | 473:09 | 93.967 | 92.831
13 | Ramdurg | 85 | 85 | 280:48 | 3730:58 | 1075:28 | 566:42 | 1642:10 | 1497.5549 | 1922:58 | 22:37 | 97.3724 | 96.9231 | 1653.0118 | 466:44 | 93.5171 | 92.8441
14 | Ghataprabha | 162 | 162 | 291:41 | 2945:48 | 961:52 | 583:52 | 1545:44 | 1363.5111 | 1837:25 | 11:21 | 98.7175 | 98.4755 | 1486.2528 | 220:11 | 96.9394 | 96.6639
15 | Raibag | 175 | 175 | 281:17 | 4468:03 | 5072:13 | 762:24 | 5834:37 | 2841.0889 | 6115:54 | 34:57 | 95.493 | 95.2757 | 3027.2576 | 415:10 | 94.0625 | 93.6734
16 | Athani | 197 | 197 | 221:18 | 6339:23 | 2255:34 | 534:08 | 2789:42 | 1977.6944 | 3011:00 | 15:17 | 98.0967 | 97.9457 | 2241.8354 | 273:07 | 96.3494 | 95.8619
17 | Chikkodi | 192 | 192 | 278:45 | 4105:33 | 1263:11 | 679:57 | 1943:08 | 1453.1625 | 2221:53 | 11:34 | 98.6397 | 98.4446 | 1624.2271 | 203:02 | 97.2478 | 96.9238
18 | Vijayapur | 174 | 174 | 393:19 | 3442:44 | 1360:53 | 875:43 | 2236:36 | 2409.3493 | 2629:55 | 15:07 | 98.2623 | 97.9567 | 2552.7965 | 352:07 | 94.9357 | 94.6342
19 | Indi | 255 | 255 | 1160:34 | 11170:35 | 2147:44 | 2849:23 | 4997:07 | 4092.3007 | 6157:41 | 24:09 | 97.3661 | 96.7543 | 4557.7417 | 428:58 | 94.1643 | 93.5005
20 | B.Bagewadi | 142 | 142 | 507:24 | 5298:37 | 1805:40 | 788:16 | 2593:56 | 2103.5243 | 3101:20 | 21:50 | 97.5447 | 97.0645 | 2324.3 | 392:50 | 94.6133 | 94.0479
21 | Bagalkot | 187 | 187 | 341:50 | 6950:01 | 2209:49 | 1395:08 | 3604:57 | 3430.3701 | 3946:47 | 21:06 | 97.4089 | 97.1632 | 3719.9542 | 477:26 | 93.3294 | 92.7663
22 | Jamkhandi | 212 | 212 | 307:20 | 4907:21 | 2131:03 | 521:38 | 2652:41 | 1561.6292 | 2960:01 | 13:58 | 98.3182 | 98.1233 | 1766.1021 | 199:56 | 97.3214 | 96.9707
23 | Mudhol | 194 | 194 | 311:50 | 3072:27 | 1288:58 | 759:50 | 2048:48 | 1729.434 | 2360:38 | 12:10 | 98.5805 | 98.3645 | 1857.4528 | 229:47 | 96.7583 | 96.5184
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of February-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of February-2022 |  |  |  | Reliability for cumulative period from Apr-21 to Feb-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 51:00 | 1970:20 | 494:17 | 280:32 | 774:49 | 1068.8979 | 825:49 | 17:57 | 97.4935 | 97.3285 | 1150.9951 | 600:31 | 93.0428 | 92.5085
2 | Dharwad Rural | 90 | 90 | 60:35 | 4171:32 | 2645:55 | 780:53 | 3426:48 | 2019.45 | 3487:23 | 38:45 | 94.334 | 94.2338 | 2193.2639 | 584:52 | 93.2819 | 92.7037
3 | Gadag | 101 | 101 | 15:05 | 898:51 | 808:50 | 381:18 | 1190:08 | 1769.6986 | 1205:13 | 11:56 | 98.2465 | 98.2243 | 1807.1507 | 429:25 | 94.754 | 94.6429
4 | Ron | 54 | 54 | 155:01 | 1808:17 | 388:57 | 509:46 | 898:43 | 15941:45 | 1053:44 | 19:31 | 97.5234 | 97.0962 | 17750:02 | 328:42 | 96.3171 | 95.8994
5 | Haveri | 199 | 199 | 758:03 | 14842:38 | 3491:45 | 1490:59 | 4982:44 | 5953.1701 | 5740:47 | 28:51 | 96.274 | 95.7071 | 6571.6132 | 792:33 | 91.0433 | 90.1128
6 | Ranebennur | 192 | 192 | 824:07 | 8403:10 | 3141:53 | 1610:01 | 4751:54 | 4981.8014 | 5576:01 | 29:03 | 96.317 | 95.6783 | 5331.9333 | 666:30 | 92.2315 | 91.6855
7 | Sirsi | 56 | 56 | 392:29 | 4692:33 | 755:03 | 796:36 | 1551:39 | 1162.9139 | 1944:08 | 34:43 | 95.8768 | 94.8338 | 1358.4368 | 582:11 | 93.7825 | 92.7372
8 | Dandeli | 22 | 22 | 41:11 | 1165:41 | 193:34 | 208:41 | 402:15 | 7581:52 | 443:26 | 20:09 | 97.2792 | 97.0006 | 8747:33 | 397:37 | 95.7007 | 95.0397
9 | Karwar | 29 | 29 | 120:42 | 3112:32 | 469:30 | 514:05 | 983:35 | 11750:25 | 1104:17 | 38:05 | 94.9529 | 94.3335 | 14862:57 | 512:31 | 94.9453 | 93.6063
10 | Honnavar | 40 | 40 | 291:33 | 4361:04 | 327:57 | 208:12 | 536:09 | 12748:02 | 827:42 | 20:42 | 98.0054 | 96.9208 | 17109:06 | 427:44 | 96.0242 | 94.6641
11 | Belagavi | 149 | 149 | 294:22 | 6625:10 | 1715:19 | 925:08 | 2640:27 | 2426.7618 | 2934:49 | 19:42 | 97.3629 | 97.0689 | 2702.8104 | 435:21 | 95.1237 | 94.569
12 | Bailhongal | 192 | 192 | 1146:51 | 15541:15 | 2434:34 | 1001:08 | 3435:42 | 3328.6 | 4582:33 | 23:52 | 97.3372 | 96.4483 | 3976.1521 | 497:01 | 94.8094 | 93.7997
13 | Ramdurg | 85 | 85 | 204:09 | 3935:07 | 1127:45 | 481:07 | 1608:52 | 1564.591 | 1813:01 | 21:20 | 97.1834 | 96.826 | 1728.5542 | 488:04 | 94.4889 | 93.9114
14 | Ghataprabha | 162 | 162 | 82:28 | 3028:16 | 922:22 | 487:59 | 1410:21 | 1422.2757 | 1492:49 | 9:13 | 98.7045 | 98.6287 | 1548.4535 | 229:24 | 97.3714 | 97.1382
15 | Raibag | 175 | 175 | 133:52 | 4601:55 | 3480:04 | 632:52 | 4112:56 | 3012.4611 | 4246:48 | 24:16 | 96.5026 | 96.3888 | 3204.2076 | 439:26 | 94.8461 | 94.518
16 | Athani | 200 | 200 | 280:55 | 6620:18 | 1982:45 | 429:21 | 2412:06 | 2078.1986 | 2693:01 | 13:28 | 98.2053 | 97.9963 | 2354.0444 | 282:29 | 96.8889 | 96.476
17 | Chikkodi | 192 | 192 | 280:55 | 4386:28 | 1052:49 | 676:59 | 1729:48 | 1525.2375 | 2010:43 | 10:28 | 98.6593 | 98.4416 | 1708.0069 | 213:30 | 97.6216 | 97.3366
18 | Vijayapur | 184 | 184 | 108:41 | 3551:25 | 1171:30 | 916:21 | 2087:51 | 2496.3431 | 2196:32 | 11:56 | 98.3115 | 98.2236 | 2644.3187 | 344:55 | 95.938 | 95.6972
19 | Indi | 256 | 256 | 725:02 | 11895:37 | 1906:37 | 3425:14 | 5331:51 | 4314.4611 | 6056:53 | 23:40 | 96.9007 | 96.4792 | 4810.1118 | 450:57 | 94.9541 | 94.3744
20 | B.Bagewadi | 142 | 142 | 150:55 | 5449:32 | 1396:23 | 419:12 | 1815:35 | 2179.1736 | 1966:30 | 13:51 | 98.0974 | 97.9392 | 2406.2375 | 406:41 | 95.4053 | 94.9265
21 | Bagalkot | 187 | 187 | 323:35 | 7273:36 | 1677:24 | 1090:48 | 2768:12 | 3545.7118 | 3091:47 | 16:32 | 97.7971 | 97.5396 | 3848.7785 | 493:58 | 94.323 | 93.8378
22 | Jamkhandi | 212 | 212 | 372:43 | 5280:04 | 1974:12 | 459:48 | 2434:00 | 1663.0458 | 2806:43 | 13:14 | 98.2915 | 98.0299 | 1883.0486 | 213:11 | 97.6513 | 97.3406
23 | Mudhol | 194 | 194 | 169:49 | 3242:16 | 1010:39 | 528:28 | 1539:07 | 1793.5639 | 1708:56 | 8:49 | 98.8194 | 98.6891 | 1928.6583 | 238:36 | 97.232 | 97.0235
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of March-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 21-22 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of March-2022 |  |  |  | Reliability for cumulative period from Apr-21 to Mar-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 21-22 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 233:00 | 2203:20 | 903:09 | 1120:24 | 2023:33 | 1153.2125 | 2256:33 | 49:03 | 94.0873 | 93.4065 | 1245.0181 | 649:34 | 93.1316 | 92.5848
2 | Dharwad Rural | 91 | 91 | 24:05 | 4195:37 | 2705:31 | 3757:10 | 6462:41 | 2288.7285 | 6486:46 | 71:17 | 90.4545 | 90.4189 | 2463.5458 | 649:44 | 93.1094 | 92.583
3 | Gadag | 101 | 101 | 125:15 | 1024:06 | 1547:37 | 800:32 | 2348:09 | 1867.5382 | 2473:24 | 24:29 | 96.8751 | 96.7085 | 1910.209 | 453:55 | 94.9341 | 94.8184
4 | Ron | 57 | 57 | 144:05 | 1952:22 | 605:40 | 628:19 | 1233:59 | 17175:44 | 1378:04 | 24:11 | 97.0902 | 96.7505 | 19128:06 | 335:35 | 96.5602 | 96.1692
5 | Haveri | 199 | 199 | 1887:40 | 16730:18 | 3330:46 | 4589:50 | 7920:36 | 6283.1951 | 9808:16 | 49:17 | 94.6503 | 93.3753 | 6980.291 | 841:51 | 91.3496 | 90.3899
6 | Ranebennur | 193 | 193 | 1097:15 | 9500:25 | 3733:52 | 2932:58 | 6666:50 | 5259.5861 | 7764:05 | 40:14 | 95.3571 | 94.593 | 5655.4368 | 703:16 | 92.5338 | 91.9718
7 | Sirsi | 59 | 59 | 368:20 | 5060:53 | 593:14 | 1246:42 | 1839:56 | 1239.5778 | 2208:16 | 37:26 | 95.8084 | 94.9693 | 1450.4479 | 590:01 | 94.2439 | 93.2647
8 | Dandeli | 22 | 22 | 81:51 | 1247:32 | 310:58 | 387:07 | 698:05 | 8279:57 | 779:56 | 35:27 | 95.7351 | 95.235 | 9527:29 | 433:04 | 95.7036 | 95.0563
9 | Karwar | 32 | 32 | 268:57 | 3381:29 | 248:56 | 214:25 | 463:21 | 12213:46 | 732:18 | 22:53 | 98.0538 | 96.9241 | 15595:15 | 487:21 | 95.6429 | 94.4366
10 | Honnavar | 40 | 40 | 353:50 | 4714:54 | 362:52 | 330:19 | 693:11 | 13441:13 | 1047:01 | 26:11 | 97.6708 | 96.4818 | 18156:07 | 453:54 | 96.164 | 94.8185
11 | Belagavi | 149 | 149 | 707:39 | 7332:49 | 2647:43 | 2118:51 | 4766:34 | 2625.3688 | 5474:13 | 36:44 | 95.7002 | 95.0619 | 2930.9028 | 472:06 | 95.1726 | 94.6108
12 | Bailhongal | 194 | 194 | 1652:19 | 17193:34 | 3725:08 | 2139:30 | 5864:38 | 3572.9597 | 7516:57 | 38:45 | 95.9368 | 94.792 | 4289.3583 | 530:39 | 94.9542 | 93.9424
13 | Ramdurg | 87 | 87 | 808:37 | 4743:44 | 1471:35 | 1631:17 | 3102:52 | 1693.8771 | 3911:29 | 44:58 | 95.2063 | 93.957 | 1891.5326 | 521:48 | 94.6658 | 94.0434
14 | Ghataprabha | 163 | 163 | 674:53 | 3703:09 | 1315:54 | 1017:27 | 2333:21 | 1519.4986 | 3008:14 | 18:27 | 98.0759 | 97.5194 | 1673.7965 | 246:27 | 97.446 | 97.1867
15 | Raibag | 175 | 175 | 553:55 | 5155:50 | 4510:12 | 908:17 | 5418:29 | 3238.2313 | 5972:24 | 34:08 | 95.8383 | 95.4129 | 3453.0576 | 473:34 | 94.9304 | 94.594
16 | Athani | 200 | 200 | 866:06 | 7486:24 | 2652:21 | 1074:50 | 3727:11 | 2233.4979 | 4593:17 | 22:58 | 97.4952 | 96.9131 | 2545.4313 | 305:27 | 96.9404 | 96.5131
17 | Chikkodi | 192 | 192 | 700:30 | 5086:58 | 1522:30 | 1564:14 | 3086:44 | 1653.8514 | 3787:14 | 19:44 | 97.8391 | 97.3488 | 1865.8083 | 233:14 | 97.6401 | 97.3376
18 | Vijayapur | 184 | 184 | 188:55 | 3740:20 | 1447:42 | 1475:26 | 2923:08 | 2618.1403 | 3112:03 | 16:55 | 97.8647 | 97.7267 | 2773.9875 | 361:49 | 96.1016 | 95.8696
19 | Indi | 265 | 265 | 386:11 | 12281:48 | 2632:46 | 1829:45 | 4462:31 | 4500.3993 | 4848:42 | 18:18 | 97.7366 | 97.5407 | 5012.141 | 453:56 | 95.3472 | 94.8182
20 | B.Bagewadi | 142 | 142 | 404:55 | 5854:27 | 1818:13 | 942:12 | 2760:25 | 2294.191 | 3165:20 | 22:17 | 97.3872 | 97.0039 | 2538.1264 | 428:59 | 95.5736 | 95.103
21 | Bagalkot | 187 | 187 | 1290:33 | 8564:09 | 2797:13 | 2280:17 | 5077:30 | 3757.2743 | 6368:03 | 34:03 | 96.3505 | 95.4229 | 4114.1139 | 528:01 | 94.4952 | 93.9724
22 | Jamkhandi | 213 | 213 | 380:29 | 5660:33 | 3020:04 | 846:57 | 3867:01 | 1824.1715 | 4247:30 | 19:56 | 97.5598 | 97.3197 | 2060.0278 | 232:07 | 97.6536 | 97.3503
23 | Mudhol | 194 | 194 | 523:35 | 3765:51 | 1435:22 | 959:58 | 2395:20 | 1893.3694 | 2918:55 | 15:03 | 98.3404 | 97.9777 | 2050.2799 | 253:39 | 97.3261 | 97.1045
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]