## DHQ
Annex-1 | [13 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of April-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Apr-22
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 38 | 38 | 34:38 | 34:38 | 542:46 | 410:41 | 953:27 | 953:27 | 988:05 | 26:00 | 96.5152 | 96.3886 | 988:05 | 26:00 | 96.5152 | 96.3886
2 | Gadag | 13 | 13 | 2:55 | 2:55 | 79:29 | 65:21 | 144:50 | 144:50 | 147:45 | 11:22 | 98.4526 | 98.4215 | 147:45 | 11:22 | 98.4526 | 98.4215
3 | Haveri | 8 | 8 | 0:00 | 0:00 | 34:33 | 38:42 | 73:15 | 73:15 | 73:15 | 9:09 | 98.7283 | 98.7283 | 73:15 | 9:09 | 98.7283 | 98.7283
4 | Karwar | 10 | 10 | 46:58 | 46:58 | 78:37 | 100:05 | 178:42 | 178:42 | 225:40 | 22:34 | 97.5181 | 96.8657 | 225:40 | 22:34 | 97.5181 | 96.8657
5 | Belagavi | 80 | 80 | 251:17 | 251:17 | 187:21 | 285:33 | 472:54 | 472:54 | 724:11 | 9:03 | 99.179 | 98.7427 | 724:11 | 9:03 | 99.179 | 98.7427
6 | Vijayapur | 39 | 39 | 142:23 | 142:23 | 254:15 | 444:22 | 698:37 | 698:37 | 841:00 | 21:34 | 97.512 | 97.005 | 841:00 | 21:34 | 97.512 | 97.005
7 | Bagalkot | 12 | 12 | 2:40 | 2:40 | 42:39 | 41:37 | 84:16 | 84:16 | 86:56 | 7:15 | 99.0247 | 98.9938 | 86:56 | 7:15 | 99.0247 | 98.9938
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of May-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2022 |  |  |  | Reliability for cumulative period from Apr-22 to May-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 40 | 40 | 58:33 | 93:11 | 621:15 | 332:28 | 953:43 | 1907:10 | 1012:16 | 25:18 | 96.7953 | 96.5986 | 2000:21 | 50:01 | 96.7432 | 96.5841
2 | Gadag | 13 | 13 | 17:15 | 20:10 | 68:12 | 69:04 | 137:16 | 282:06 | 154:31 | 11:53 | 98.5808 | 98.4024 | 302:16 | 23:15 | 98.5178 | 98.4118
3 | Haveri | 8 | 8 | 8:50 | 8:50 | 105:05 | 46:00 | 151:05 | 224:20 | 159:55 | 19:59 | 97.4616 | 97.3132 | 233:10 | 29:09 | 98.0846 | 98.0092
4 | Karwar | 10 | 10 | 7:52 | 54:50 | 81:58 | 92:36 | 174:34 | 353:16 | 182:26 | 18:15 | 97.6537 | 97.5479 | 408:06 | 40:49 | 97.587 | 97.2124
5 | Belagavi | 80 | 80 | 274:38 | 525:55 | 238:23 | 329:56 | 568:19 | 1041:13 | 842:57 | 10:32 | 99.0452 | 98.5838 | 1567:08 | 19:35 | 99.111 | 98.6619
6 | Vijayapur | 38 | 38 | 222:58 | 365:21 | 174:31 | 508:39 | 683:10 | 1381:47 | 906:08 | 23:51 | 97.5836 | 96.7949 | 1747:08 | 45:59 | 97.5162 | 96.8595
7 | Bagalkot | 12 | 12 | 51:16 | 53:56 | 72:11 | 118:13 | 190:24 | 274:40 | 241:40 | 20:08 | 97.8674 | 97.2932 | 328:36 | 27:23 | 98.4366 | 98.1296
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of June-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2022 |  |  |  | Reliability for cumulative period from Apr-22 to June-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 41 | 41 | 14:40 | 107:51 | 638:51 | 163:23 | 802:14 | 2709:24 | 816:54 | 19:55 | 97.2824 | 97.2327 | 2817:15 | 68:43 | 96.9742 | 96.8538
2 | Gadag | 13 | 13 | 10:00 | 30:10 | 106:34 | 38:46 | 145:20 | 427:26 | 155:20 | 11:57 | 98.4473 | 98.3405 | 457:36 | 35:12 | 98.4945 | 98.3883
3 | Haveri | 8 | 8 | 3:20 | 12:10 | 45:45 | 18:45 | 64:30 | 288:50 | 67:50 | 8:29 | 98.8802 | 98.8223 | 301:00 | 37:38 | 98.3469 | 98.2772
4 | Karwar | 10 | 10 | 8:50 | 63:40 | 82:07 | 118:58 | 201:05 | 554:21 | 209:55 | 21:00 | 97.2072 | 97.0845 | 618:01 | 61:48 | 97.4618 | 97.1703
5 | Belagavi | 80 | 80 | 229:55 | 755:50 | 221:06 | 182:56 | 404:02 | 1445:15 | 633:57 | 7:55 | 99.2986 | 98.8994 | 2201:05 | 27:31 | 99.1728 | 98.7402
6 | Vijayapur | 40 | 40 | 122:02 | 487:23 | 359:27 | 195:55 | 555:22 | 1937:09 | 677:24 | 16:56 | 98.0716 | 97.6479 | 2424:32 | 60:37 | 97.7826 | 97.2247
7 | Bagalkot | 12 | 12 | 96:00 | 149:56 | 79:24 | 85:31 | 164:55 | 439:35 | 260:55 | 21:45 | 98.0912 | 96.9801 | 589:31 | 49:08 | 98.3227 | 97.7506
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]

## URBAN
Annex-II | [13 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of April-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Apr-22
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 80 | 80 | 61:25 | 61:25 | 540:15 | 407:09 | 947:24 | 947:24 | 1008:49 | 12:37 | 98.3552 | 98.2486 | 1008:49 | 12:37 | 98.3552 | 98.2486
2 | Dharwad(R) | 14 | 14 | 1:40 | 1:40 | 151:26 | 242:33 | 393:59 | 393:59 | 395:39 | 28:16 | 96.0914 | 96.0749 | 395:39 | 28:16 | 96.0914 | 96.0749
3 | Kundagol | 1 | 1 | 37:05 | 37:05 | 6:30 | 5:05 | 11:35 | 11:35 | 48:40 | 48:40 | 98.3912 | 93.2407 | 48:40 | 48:40 | 98.3912 | 93.2407
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 8:23 | 22:13 | 30:36 | 30:36 | 30:36 | 30:36 | 95.75 | 95.75 | 30:36 | 30:36 | 95.75 | 95.75
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 12:37 | 43:23 | 56:00 | 56:00 | 56:00 | 56:00 | 92.2222 | 92.2222 | 56:00 | 56:00 | 92.2222 | 92.2222
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 17:50 | 44:20 | 62:10 | 62:10 | 62:10 | 31:05 | 95.6829 | 95.6829 | 62:10 | 31:05 | 95.6829 | 95.6829
7 | Alnavar | 2 | 2 | 0:00 | 0:00 | 14:45 | 9:15 | 24:00 | 24:00 | 24:00 | 12:00 | 98.3333 | 98.3333 | 24:00 | 12:00 | 98.3333 | 98.3333
8 | Naragund | 2 | 2 | 19:10 | 19:10 | 22:15 | 29:20 | 51:35 | 51:35 | 70:45 | 35:22 | 96.4178 | 95.0868 | 70:45 | 35:22 | 96.4178 | 95.0868
9 | Shirahatti | 1 | 1 | 0:00 | 0:00 | 6:15 | 16:40 | 22:55 | 22:55 | 22:55 | 22:55 | 96.8171 | 96.8171 | 22:55 | 22:55 | 96.8171 | 96.8171
10 | Laxmeshwar | 3 | 3 | 0:00 | 0:00 | 44:35 | 66:15 | 110:50 | 110:50 | 110:50 | 36:57 | 94.8688 | 94.8688 | 110:50 | 36:57 | 94.8688 | 94.8688
11 | Naregal | 1 | 1 | 1:10 | 1:10 | 4:55 | 6:35 | 11:30 | 11:30 | 12:40 | 12:40 | 98.4028 | 98.2407 | 12:40 | 12:40 | 98.4028 | 98.2407
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 27:30 | 22:40 | 50:10 | 50:10 | 50:10 | 25:05 | 96.5162 | 96.5162 | 50:10 | 25:05 | 96.5162 | 96.5162
13 | Ron | 3 | 3 | 0:00 | 0:00 | 54:40 | 44:42 | 99:22 | 99:22 | 99:22 | 33:07 | 95.3997 | 95.3997 | 99:22 | 33:07 | 95.3997 | 95.3997
14 | Mundaragi | 1 | 1 | 0:00 | 0:00 | 4:25 | 10:05 | 14:30 | 14:30 | 14:30 | 14:30 | 97.9861 | 97.9861 | 14:30 | 14:30 | 97.9861 | 97.9861
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 15:43 | 83:24 | 99:07 | 99:07 | 99:07 | 99:07 | 86.2338 | 86.2338 | 99:07 | 99:07 | 86.2338 | 86.2338
16 | Savanur | 2 | 2 | 0:00 | 0:00 | 22:15 | 8:00 | 30:15 | 30:15 | 30:15 | 15:08 | 97.8993 | 97.8993 | 30:15 | 15:08 | 97.8993 | 97.8993
17 | Shiggaon | 3 | 3 | 49:55 | 49:55 | 18:25 | 37:20 | 55:45 | 55:45 | 105:40 | 35:13 | 97.419 | 95.108 | 105:40 | 35:13 | 97.419 | 95.108
18 | Bankapur | 1 | 1 | 10:05 | 10:05 | 18:00 | 12:10 | 30:10 | 30:10 | 40:15 | 40:15 | 95.8102 | 94.4097 | 40:15 | 40:15 | 95.8102 | 94.4097
19 | Hangal | 2 | 2 | 2:26 | 2:26 | 4:30 | 19:00 | 23:30 | 23:30 | 25:56 | 12:58 | 98.3681 | 98.1991 | 25:56 | 12:58 | 98.3681 | 98.1991
20 | Ranebennur | 10 | 10 | 34:01 | 34:01 | 46:25 | 71:01 | 117:26 | 117:26 | 151:27 | 15:09 | 98.369 | 97.8965 | 151:27 | 15:09 | 98.369 | 97.8965
21 | Tuminakatti | 1 | 1 | 3:05 | 3:05 | 21:00 | 3:25 | 24:25 | 24:25 | 27:30 | 27:30 | 96.6088 | 96.1806 | 27:30 | 27:30 | 96.6088 | 96.1806
22 | Rattihalli | 1 | 1 | 6:25 | 6:25 | 4:25 | 12:55 | 17:20 | 17:20 | 23:45 | 23:45 | 97.5926 | 96.7014 | 23:45 | 23:45 | 97.5926 | 96.7014
23 | Hirekerur | 1 | 1 | 4:15 | 4:15 | 8:05 | 18:40 | 26:45 | 26:45 | 31:00 | 31:00 | 96.2847 | 95.6944 | 31:00 | 31:00 | 96.2847 | 95.6944
24 | Byadagi | 5 | 5 | 46:55 | 46:55 | 57:25 | 31:25 | 88:50 | 88:50 | 135:45 | 27:09 | 97.5324 | 96.2292 | 135:45 | 27:09 | 97.5324 | 96.2292
25 | Sirsi | 6 | 6 | 49:11 | 49:11 | 49:10 | 34:20 | 83:30 | 83:30 | 132:41 | 22:07 | 98.0671 | 96.9286 | 132:41 | 22:07 | 98.0671 | 96.9286
26 | Yellapur | 1 | 1 | 16:00 | 16:00 | 3:55 | 4:55 | 8:50 | 8:50 | 24:50 | 24:50 | 98.7731 | 96.5509 | 24:50 | 24:50 | 98.7731 | 96.5509
27 | Mundagod | 1 | 1 | 0:00 | 0:00 | 2:40 | 10:10 | 12:50 | 12:50 | 12:50 | 12:50 | 98.2176 | 98.2176 | 12:50 | 12:50 | 98.2176 | 98.2176
28 | Siddapur | 1 | 1 | 10:40 | 10:40 | 8:35 | 7:15 | 15:50 | 15:50 | 26:30 | 26:30 | 97.8009 | 96.3194 | 26:30 | 26:30 | 97.8009 | 96.3194
29 | Dandeli | 7 | 7 | 1:20 | 1:20 | 77:16 | 35:51 | 113:07 | 113:07 | 114:27 | 16:21 | 97.7556 | 97.7292 | 114:27 | 16:21 | 97.7556 | 97.7292
30 | Haliyal | 2 | 2 | 0:52 | 0:52 | 20:55 | 23:55 | 44:50 | 44:50 | 45:42 | 22:51 | 96.8866 | 96.8264 | 45:42 | 22:51 | 96.8866 | 96.8264
31 | Ankola | 3 | 3 | 26:42 | 26:42 | 11:28 | 24:45 | 36:13 | 36:13 | 62:55 | 20:58 | 98.3233 | 97.0872 | 62:55 | 20:58 | 98.3233 | 97.0872
32 | Kumta | 3 | 3 | 15:12 | 15:12 | 11:21 | 17:02 | 28:23 | 28:23 | 43:35 | 14:32 | 98.686 | 97.9823 | 43:35 | 14:32 | 98.686 | 97.9823
33 | Gokarna | 1 | 1 | 24:05 | 24:05 | 1:10 | 0:15 | 1:25 | 1:25 | 25:30 | 25:30 | 99.8032 | 96.4583 | 25:30 | 25:30 | 99.8032 | 96.4583
34 | Kasarkod | 1 | 1 | 11:21 | 11:21 | 2:35 | 4:55 | 7:30 | 7:30 | 18:51 | 18:51 | 98.9583 | 97.3819 | 18:51 | 18:51 | 98.9583 | 97.3819
35 | Honnavar | 3 | 3 | 16:06 | 16:06 | 20:00 | 16:36 | 36:36 | 36:36 | 52:42 | 17:34 | 98.3056 | 97.5602 | 52:42 | 17:34 | 98.3056 | 97.5602
36 | Murdeshwar | 4 | 4 | 24:32 | 24:32 | 28:04 | 13:59 | 42:03 | 42:03 | 66:35 | 16:39 | 98.5399 | 97.6881 | 66:35 | 16:39 | 98.5399 | 97.6881
37 | Bhatkal | 3 | 3 | 20:18 | 20:18 | 9:14 | 11:16 | 20:30 | 20:30 | 40:48 | 13:36 | 99.0509 | 98.1111 | 40:48 | 13:36 | 99.0509 | 98.1111
38 | Khanapur | 2 | 2 | 20:30 | 20:30 | 43:10 | 30:00 | 73:10 | 73:10 | 93:40 | 46:50 | 94.919 | 93.4954 | 93:40 | 46:50 | 94.919 | 93.4954
39 | Bailhongal | 3 | 3 | 0:00 | 0:00 | 103:10 | 43:15 | 146:25 | 146:25 | 146:25 | 48:48 | 93.2215 | 93.2215 | 146:25 | 48:48 | 93.2215 | 93.2215
40 | Kittur | 1 | 1 | 0:45 | 0:45 | 7:05 | 14:10 | 21:15 | 21:15 | 22:00 | 22:00 | 97.0486 | 96.9444 | 22:00 | 22:00 | 97.0486 | 96.9444
41 | M K Hubli | 1 | 1 | 0:25 | 0:25 | 18:25 | 10:50 | 29:15 | 29:15 | 29:40 | 29:40 | 95.9375 | 95.8796 | 29:40 | 29:40 | 95.9375 | 95.8796
42 | Soundatti | 3 | 3 | 11:50 | 11:50 | 40:05 | 23:03 | 63:08 | 63:08 | 74:58 | 24:59 | 97.0772 | 96.5293 | 74:58 | 24:59 | 97.0772 | 96.5293
43 | Munavalli | 1 | 1 | 10:10 | 10:10 | 28:50 | 4:25 | 33:15 | 33:15 | 43:25 | 43:25 | 95.3819 | 93.9699 | 43:25 | 43:25 | 95.3819 | 93.9699
44 | Yaragatti | 1 | 1 | 14:11 | 14:11 | 29:22 | 9:43 | 39:05 | 39:05 | 53:16 | 53:16 | 94.5718 | 92.6019 | 53:16 | 53:16 | 94.5718 | 92.6019
45 | Ramdurg | 2 | 2 | 11:46 | 11:46 | 38:25 | 18:07 | 56:32 | 56:32 | 68:18 | 34:09 | 96.0741 | 95.2569 | 68:18 | 34:09 | 96.0741 | 95.2569
46 | Gokak | 10 | 10 | 64:26 | 64:26 | 11:06 | 45:10 | 56:16 | 56:16 | 120:42 | 12:04 | 99.2185 | 98.3236 | 120:42 | 12:04 | 99.2185 | 98.3236
47 | Mudalagi | 2 | 2 | 0:15 | 0:15 | 23:05 | 31:35 | 54:40 | 54:40 | 54:55 | 27:27 | 96.2037 | 96.1863 | 54:55 | 27:27 | 96.2037 | 96.1863
48 | Konnur | 1 | 1 | 1:05 | 1:05 | 17:45 | 17:30 | 35:15 | 35:15 | 36:20 | 36:20 | 95.1042 | 94.9537 | 36:20 | 36:20 | 95.1042 | 94.9537
49 | Raibag | 1 | 1 | 0:00 | 0:00 | 31:35 | 20:00 | 51:35 | 51:35 | 51:35 | 51:35 | 92.8356 | 92.8356 | 51:35 | 51:35 | 92.8356 | 92.8356
50 | Kudachi | 1 | 1 | 0:40 | 0:40 | 48:00 | 20:05 | 68:05 | 68:05 | 68:45 | 68:45 | 90.544 | 90.4514 | 68:45 | 68:45 | 90.544 | 90.4514
51 | Athani | 7 | 7 | 51:12 | 51:12 | 80:28 | 176:33 | 257:01 | 257:01 | 308:13 | 44:02 | 94.9005 | 93.8846 | 308:13 | 44:02 | 94.9005 | 93.8846
52 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 8:50 | 35:15 | 44:05 | 44:05 | 44:05 | 22:02 | 96.9387 | 96.9387 | 44:05 | 22:02 | 96.9387 | 96.9387
53 | Nippani | 5 | 5 | 0:00 | 0:00 | 60:30 | 35:50 | 96:20 | 96:20 | 96:20 | 19:16 | 97.3241 | 97.3241 | 96:20 | 19:16 | 97.3241 | 97.3241
54 | Sadalaga | 1 | 1 | 1:25 | 1:25 | 15:40 | 11:10 | 26:50 | 26:50 | 28:15 | 28:15 | 96.2731 | 96.0764 | 28:15 | 28:15 | 96.2731 | 96.0764
55 | Muddebihal | 2 | 2 | 11:35 | 11:35 | 38:40 | 12:05 | 50:45 | 50:45 | 62:20 | 31:10 | 96.4757 | 95.6713 | 62:20 | 31:10 | 96.4757 | 95.6713
56 | Talikoti | 1 | 1 | 2:30 | 2:30 | 17:15 | 6:40 | 23:55 | 23:55 | 26:25 | 26:25 | 96.6782 | 96.331 | 26:25 | 26:25 | 96.6782 | 96.331
57 | B.Bagewadi | 1 | 1 | 6:52 | 6:52 | 12:41 | 9:40 | 22:21 | 22:21 | 29:13 | 29:13 | 96.8958 | 95.9421 | 29:13 | 29:13 | 96.8958 | 95.9421
58 | Indi | 3 | 3 | 6:58 | 6:58 | 25:07 | 6:24 | 31:31 | 31:31 | 38:29 | 12:50 | 98.5409 | 98.2184 | 38:29 | 12:50 | 98.5409 | 98.2184
59 | Sindagi | 2 | 2 | 16:50 | 16:50 | 22:40 | 11:55 | 34:35 | 34:35 | 51:25 | 25:42 | 97.5984 | 96.4294 | 51:25 | 25:42 | 97.5984 | 96.4294
60 | Guledgudda | 1 | 1 | 0:51 | 0:51 | 6:27 | 7:28 | 13:55 | 13:55 | 14:46 | 14:46 | 98.0671 | 97.9491 | 14:46 | 14:46 | 98.0671 | 97.9491
61 | Ilkal | 7 | 7 | 22:42 | 22:42 | 45:12 | 107:23 | 152:35 | 152:35 | 175:17 | 25:02 | 96.9726 | 96.5222 | 175:17 | 25:02 | 96.9726 | 96.5222
62 | Kerur | 1 | 1 | 2:45 | 2:45 | 24:27 | 15:20 | 39:47 | 39:47 | 42:32 | 42:32 | 94.4745 | 94.0926 | 42:32 | 42:32 | 94.4745 | 94.0926
63 | Hungund | 4 | 4 | 9:58 | 9:58 | 60:45 | 66:01 | 126:46 | 126:46 | 136:44 | 34:11 | 95.5984 | 95.2523 | 136:44 | 34:11 | 95.5984 | 95.2523
64 | Badami | 1 | 1 | 2:34 | 2:34 | 5:10 | 19:05 | 24:15 | 24:15 | 26:49 | 26:49 | 96.6319 | 96.2755 | 26:49 | 26:49 | 96.6319 | 96.2755
65 | Jamkhandi | 6 | 6 | 9:10 | 9:10 | 77:35 | 30:15 | 107:50 | 107:50 | 117:00 | 19:30 | 97.5039 | 97.2917 | 117:00 | 19:30 | 97.5039 | 97.2917
66 | Mahalingapur | 2 | 2 | 2:46 | 2:46 | 30:01 | 7:34 | 37:35 | 37:35 | 40:21 | 20:10 | 97.39 | 97.1979 | 40:21 | 20:10 | 97.39 | 97.1979
67 | Rannabelagali | 1 | 1 | 2:52 | 2:52 | 13:40 | 2:50 | 16:30 | 16:30 | 19:22 | 19:22 | 97.7083 | 97.3102 | 19:22 | 19:22 | 97.7083 | 97.3102
68 | Rabakavi | 2 | 2 | 6:05 | 6:05 | 24:40 | 12:25 | 37:05 | 37:05 | 43:10 | 21:35 | 97.4248 | 97.0023 | 43:10 | 21:35 | 97.4248 | 97.0023
69 | Banahatti | 2 | 2 | 4:10 | 4:10 | 25:10 | 4:50 | 30:00 | 30:00 | 34:10 | 17:05 | 97.9167 | 97.6273 | 34:10 | 17:05 | 97.9167 | 97.6273
70 | Terdal | 2 | 2 | 18:30 | 18:30 | 58:52 | 9:05 | 67:57 | 67:57 | 86:27 | 43:14 | 95.2812 | 93.9965 | 86:27 | 43:14 | 95.2812 | 93.9965
71 | Mudhol | 4 | 4 | 11:58 | 11:58 | 121:13 | 6:02 | 127:15 | 127:15 | 139:13 | 34:48 | 95.5816 | 95.1661 | 139:13 | 34:48 | 95.5816 | 95.1661
72 | Bilagi | 1 | 1 | 2:25 | 2:25 | 18:45 | 5:00 | 23:45 | 23:45 | 26:10 | 26:10 | 96.7014 | 96.3657 | 26:10 | 26:10 | 96.7014 | 96.3657
73 | Lokapur | 2 | 2 | 0:25 | 0:25 | 36:20 | 7:10 | 43:30 | 43:30 | 43:55 | 21:58 | 96.9792 | 96.9502 | 43:55 | 21:58 | 96.9792 | 96.9502
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of May-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2022 |  |  |  | Reliability for cumulative period from Apr-22 to May-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 80 | 80 | 32:59 | 94:24 | 377:16 | 458:56 | 836:12 | 1783:36 | 869:11 | 10:52 | 98.5951 | 98.5397 | 1878:00 | 23:29 | 98.4771 | 98.3965
2 | Dharwad(R) | 14 | 14 | 1:40 | 3:20 | 90:53 | 163:45 | 254:38 | 648:37 | 256:18 | 18:18 | 97.5554 | 97.5394 | 651:57 | 46:34 | 96.8354 | 96.8191
3 | Kundagol | 1 | 1 | 9:55 | 47:00 | 5:20 | 4:00 | 9:20 | 20:55 | 19:15 | 19:15 | 98.7455 | 97.4126 | 67:55 | 67:55 | 98.5713 | 95.3609
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 3:51 | 18:29 | 22:20 | 52:56 | 22:20 | 22:20 | 96.9982 | 96.9982 | 52:56 | 52:56 | 96.3843 | 96.3843
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 2:40 | 15:22 | 18:02 | 74:02 | 18:02 | 18:02 | 97.5762 | 97.5762 | 74:02 | 74:02 | 94.9431 | 94.9431
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 70:00 | 23:00 | 93:00 | 155:10 | 93:00 | 46:30 | 93.75 | 93.75 | 155:10 | 77:35 | 94.7006 | 94.7006
7 | Alnavar | 2 | 2 | 0:00 | 0:00 | 4:50 | 51:55 | 56:45 | 80:45 | 56:45 | 28:22 | 96.1862 | 96.1862 | 80:45 | 40:22 | 97.2421 | 97.2421
8 | Naragund | 2 | 2 | 17:20 | 36:30 | 34:35 | 15:30 | 50:05 | 101:40 | 67:25 | 33:43 | 96.6342 | 95.4693 | 138:10 | 69:05 | 96.5278 | 95.2812
9 | Shirahatti | 1 | 1 | 0:00 | 0:00 | 6:15 | 16:40 | 22:55 | 45:50 | 22:55 | 22:55 | 96.9198 | 96.9198 | 45:50 | 45:50 | 96.8693 | 96.8693
10 | Laxmeshwar | 3 | 3 | 0:00 | 0:00 | 53:42 | 38:37 | 92:19 | 203:09 | 92:19 | 30:46 | 95.8639 | 95.8639 | 203:09 | 67:43 | 95.3745 | 95.3745
11 | Naregal | 1 | 1 | 1:40 | 2:50 | 9:15 | 6:05 | 15:20 | 26:50 | 17:00 | 17:00 | 97.9391 | 97.7151 | 29:40 | 29:40 | 98.1671 | 97.9736
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 33:35 | 21:25 | 55:00 | 105:10 | 55:00 | 27:30 | 96.3038 | 96.3038 | 105:10 | 52:35 | 96.4082 | 96.4082
13 | Ron | 3 | 3 | 0:00 | 0:00 | 42:00 | 40:07 | 82:07 | 181:29 | 82:07 | 27:22 | 96.3209 | 96.3209 | 181:29 | 60:30 | 95.8679 | 95.8679
14 | Mundaragi | 1 | 1 | 0:00 | 0:00 | 19:45 | 40:15 | 60:00 | 74:30 | 60:00 | 60:00 | 91.9355 | 91.9355 | 74:30 | 74:30 | 94.9112 | 94.9112
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 22:06 | 67:59 | 90:05 | 189:12 | 90:05 | 90:05 | 87.892 | 87.892 | 189:12 | 189:12 | 87.0765 | 87.0765
16 | Savanur | 2 | 2 | 3:05 | 3:05 | 35:40 | 25:20 | 61:00 | 91:15 | 64:05 | 32:02 | 95.9005 | 95.6933 | 94:20 | 47:10 | 96.8835 | 96.7782
17 | Shiggaon | 3 | 3 | 27:35 | 77:30 | 31:05 | 81:20 | 112:25 | 168:10 | 140:00 | 46:40 | 94.9634 | 93.7276 | 245:40 | 81:53 | 96.1711 | 94.4065
18 | Bankapur | 1 | 1 | 18:55 | 29:00 | 23:45 | 42:10 | 65:55 | 96:05 | 84:50 | 84:50 | 91.1402 | 88.5977 | 125:05 | 125:05 | 93.4369 | 91.4561
19 | Hangal | 2 | 2 | 1:34 | 4:00 | 24:05 | 47:45 | 71:50 | 95:20 | 73:24 | 36:42 | 95.1725 | 95.0672 | 99:20 | 49:40 | 96.7441 | 96.6075
20 | Ranebennur | 10 | 10 | 4:32 | 38:33 | 89:26 | 143:25 | 232:51 | 350:17 | 237:23 | 23:44 | 96.8703 | 96.8094 | 388:50 | 38:53 | 97.6074 | 97.344
21 | Tuminakatti | 1 | 1 | 0:25 | 3:30 | 15:10 | 3:55 | 19:05 | 43:30 | 19:30 | 19:30 | 97.435 | 97.379 | 47:00 | 47:00 | 97.0287 | 96.7896
22 | Rattihalli | 1 | 1 | 0:45 | 7:10 | 28:15 | 8:40 | 36:55 | 54:15 | 37:40 | 37:40 | 95.0381 | 94.9373 | 61:25 | 61:25 | 96.2944 | 95.8049
23 | Hirekerur | 1 | 1 | 1:20 | 5:35 | 24:25 | 10:25 | 34:50 | 61:35 | 36:10 | 36:10 | 95.3181 | 95.1389 | 67:10 | 67:10 | 95.7935 | 95.4121
24 | Byadagi | 5 | 5 | 49:55 | 96:50 | 67:20 | 69:00 | 136:20 | 225:10 | 186:15 | 37:15 | 96.3351 | 94.9933 | 322:00 | 64:24 | 96.924 | 95.6011
25 | Sirsi | 6 | 6 | 10:18 | 59:29 | 21:15 | 25:58 | 47:13 | 130:43 | 57:31 | 9:35 | 98.9423 | 98.7115 | 190:12 | 31:42 | 98.5119 | 97.8347
26 | Yellapur | 1 | 1 | 3:25 | 19:25 | 5:25 | 3:40 | 9:05 | 17:55 | 12:30 | 12:30 | 98.7791 | 98.3199 | 37:20 | 37:20 | 98.7762 | 97.4499
27 | Mundagod | 1 | 1 | 0:00 | 0:00 | 7:10 | 9:35 | 16:45 | 29:35 | 16:45 | 16:45 | 97.7487 | 97.7487 | 29:35 | 29:35 | 97.9793 | 97.9793
28 | Siddapur | 1 | 1 | 10:40 | 21:20 | 8:35 | 7:15 | 15:50 | 31:40 | 26:30 | 26:30 | 97.8719 | 96.4382 | 53:00 | 53:00 | 97.837 | 96.3798
29 | Dandeli | 7 | 7 | 7:06 | 8:26 | 43:05 | 17:38 | 60:43 | 173:50 | 67:49 | 9:41 | 98.8342 | 98.6978 | 182:16 | 26:02 | 98.3037 | 98.2214
30 | Haliyal | 2 | 2 | 4:44 | 5:36 | 23:55 | 10:20 | 34:15 | 79:05 | 38:59 | 19:30 | 97.6983 | 97.3802 | 84:41 | 42:21 | 97.2991 | 97.1078
31 | Ankola | 3 | 3 | 32:48 | 59:30 | 13:13 | 0:37 | 13:50 | 50:03 | 46:38 | 15:33 | 99.3802 | 97.9107 | 109:33 | 36:31 | 98.8604 | 97.5057
32 | Kumta | 3 | 3 | 8:18 | 23:30 | 12:38 | 25:42 | 38:20 | 66:43 | 46:38 | 15:33 | 98.2826 | 97.9107 | 90:13 | 30:04 | 98.481 | 97.9459
33 | Gokarna | 1 | 1 | 9:42 | 33:47 | 6:35 | 2:25 | 9:00 | 10:25 | 18:42 | 18:42 | 98.7903 | 97.4866 | 44:12 | 44:12 | 99.2885 | 96.9809
34 | Kasarkod | 1 | 1 | 5:51 | 17:12 | 3:48 | 11:01 | 14:49 | 22:19 | 20:40 | 20:40 | 98.0085 | 97.2222 | 39:31 | 39:31 | 98.4756 | 97.3008
35 | Honnavar | 3 | 3 | 26:33 | 42:39 | 23:31 | 30:13 | 53:44 | 90:20 | 80:17 | 26:46 | 97.5926 | 96.4031 | 132:59 | 44:20 | 97.9432 | 96.9721
36 | Murdeshwar | 4 | 4 | 35:56 | 60:28 | 31:08 | 36:28 | 67:36 | 109:39 | 103:32 | 25:53 | 97.7285 | 96.5211 | 170:07 | 42:32 | 98.1276 | 97.095
37 | Bhatkal | 3 | 3 | 46:36 | 66:54 | 36:00 | 7:12 | 43:12 | 63:42 | 89:48 | 29:56 | 98.0645 | 95.9767 | 130:36 | 43:32 | 98.5496 | 97.0264
38 | Khanapur | 2 | 2 | 3:00 | 23:30 | 45:45 | 18:30 | 64:15 | 137:25 | 67:15 | 33:37 | 95.6821 | 95.4805 | 160:55 | 80:28 | 95.3068 | 94.5042
39 | Bailhongal | 3 | 3 | 0:00 | 0:00 | 58:20 | 25:20 | 83:40 | 230:05 | 83:40 | 27:53 | 96.2515 | 96.2515 | 230:05 | 76:42 | 94.7613 | 94.7613
40 | Kittur | 1 | 1 | 0:00 | 0:45 | 17:20 | 8:00 | 25:20 | 46:35 | 25:20 | 25:20 | 96.595 | 96.595 | 47:20 | 47:20 | 96.8181 | 96.7668
41 | M K Hubli | 1 | 1 | 0:20 | 0:45 | 12:45 | 5:55 | 18:40 | 47:55 | 19:00 | 19:00 | 97.491 | 97.4462 | 48:40 | 48:40 | 96.727 | 96.6758
42 | Soundatti | 3 | 3 | 3:42 | 15:32 | 33:16 | 10:53 | 44:09 | 107:17 | 47:51 | 15:57 | 98.022 | 97.8562 | 122:49 | 40:56 | 97.5573 | 97.2036
43 | Munavalli | 1 | 1 | 10:10 | 20:20 | 28:50 | 4:25 | 33:15 | 66:30 | 43:25 | 43:25 | 95.5309 | 94.1644 | 86:50 | 86:50 | 95.4577 | 94.0688
44 | Yaragatti | 1 | 1 | 1:58 | 16:09 | 44:47 | 11:14 | 56:01 | 95:06 | 57:59 | 57:59 | 92.4709 | 92.2065 | 111:15 | 111:15 | 93.5041 | 92.401
45 | Ramdurg | 2 | 2 | 0:00 | 11:46 | 31:03 | 16:50 | 47:53 | 104:25 | 47:53 | 23:56 | 96.782 | 96.782 | 116:11 | 58:05 | 96.4339 | 96.032
46 | Gokak | 10 | 10 | 75:42 | 140:08 | 37:44 | 22:08 | 59:52 | 116:08 | 135:34 | 13:33 | 99.1953 | 98.1779 | 256:16 | 25:38 | 99.2067 | 98.2495
47 | Mudalagi | 2 | 2 | 1:20 | 1:35 | 54:45 | 24:10 | 78:55 | 133:35 | 80:15 | 40:08 | 94.6965 | 94.6069 | 135:10 | 67:35 | 95.4377 | 95.3837
48 | Konnur | 1 | 1 | 0:25 | 1:30 | 19:30 | 6:05 | 25:35 | 60:50 | 26:00 | 26:00 | 96.5614 | 96.5054 | 62:20 | 62:20 | 95.8447 | 95.7423
49 | Raibag | 1 | 1 | 0:00 | 0:00 | 41:20 | 15:20 | 56:40 | 108:15 | 56:40 | 56:40 | 92.3835 | 92.3835 | 108:15 | 108:15 | 92.6059 | 92.6059
50 | Kudachi | 1 | 1 | 0:00 | 0:40 | 59:45 | 14:25 | 74:10 | 142:15 | 74:10 | 74:10 | 90.0314 | 90.0314 | 142:55 | 142:55 | 90.2835 | 90.2379
51 | Athani | 7 | 7 | 46:12 | 97:24 | 90:06 | 196:37 | 286:43 | 543:44 | 332:55 | 47:34 | 94.4947 | 93.6076 | 641:08 | 91:35 | 94.6942 | 93.7438
52 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 21:10 | 9:25 | 30:35 | 74:40 | 30:35 | 15:18 | 97.9447 | 97.9447 | 74:40 | 37:20 | 97.4499 | 97.4499
53 | Nippani | 5 | 5 | 0:00 | 0:00 | 158:55 | 47:22 | 206:17 | 302:37 | 206:17 | 41:15 | 94.4547 | 94.4547 | 302:37 | 60:31 | 95.8659 | 95.8659
54 | Sadalaga | 1 | 1 | 13:40 | 15:05 | 20:25 | 7:05 | 27:30 | 54:20 | 41:10 | 41:10 | 96.3038 | 94.4668 | 69:25 | 69:25 | 96.2887 | 95.2584
55 | Muddebihal | 2 | 2 | 3:40 | 15:15 | 70:00 | 50:40 | 120:40 | 171:25 | 124:20 | 62:10 | 91.8907 | 91.6443 | 186:40 | 93:20 | 94.1456 | 93.6248
56 | Talikoti | 1 | 1 | 9:45 | 12:15 | 26:45 | 12:55 | 39:40 | 63:35 | 49:25 | 49:25 | 94.6685 | 93.358 | 75:50 | 75:50 | 95.6569 | 94.8201
57 | B.Bagewadi | 1 | 1 | 2:30 | 9:22 | 14:22 | 2:33 | 16:55 | 39:16 | 19:25 | 19:25 | 97.7263 | 97.3902 | 48:38 | 48:38 | 97.3179 | 96.6781
58 | Indi | 3 | 3 | 38:24 | 45:22 | 33:30 | 12:01 | 45:31 | 77:02 | 83:55 | 27:58 | 97.9607 | 96.2403 | 122:24 | 40:48 | 98.2461 | 97.2131
59 | Sindagi | 2 | 2 | 7:10 | 24:00 | 39:45 | 24:55 | 64:40 | 99:15 | 71:50 | 35:55 | 95.6541 | 95.1725 | 123:15 | 61:38 | 96.6103 | 95.7906
60 | Guledgudda | 1 | 1 | 0:00 | 0:51 | 11:35 | 8:21 | 19:56 | 33:51 | 19:56 | 19:56 | 97.3208 | 97.3208 | 34:42 | 34:42 | 97.6878 | 97.6298
61 | Ilkal | 7 | 7 | 17:00 | 39:42 | 107:25 | 139:06 | 246:31 | 399:06 | 263:31 | 37:39 | 95.2666 | 94.9402 | 438:48 | 62:41 | 96.1056 | 95.7182
62 | Kerur | 1 | 1 | 0:00 | 2:45 | 26:51 | 33:14 | 60:05 | 99:52 | 60:05 | 60:05 | 91.9243 | 91.9243 | 102:37 | 102:37 | 93.1785 | 92.9907
63 | Hungund | 4 | 4 | 9:49 | 19:47 | 82:52 | 82:30 | 165:22 | 292:08 | 175:11 | 43:48 | 94.4433 | 94.1135 | 311:55 | 77:59 | 95.0114 | 94.6736
64 | Badami | 1 | 1 | 0:20 | 2:54 | 12:10 | 14:57 | 27:07 | 51:22 | 27:27 | 27:27 | 96.3553 | 96.3105 | 54:16 | 54:16 | 96.4913 | 96.2933
65 | Jamkhandi | 6 | 6 | 0:00 | 9:10 | 183:35 | 64:55 | 248:30 | 356:20 | 248:30 | 41:25 | 94.4332 | 94.4332 | 365:30 | 60:55 | 95.9434 | 95.839
66 | Mahalingapur | 2 | 2 | 0:30 | 3:16 | 54:01 | 4:40 | 58:41 | 96:16 | 59:11 | 29:36 | 96.0562 | 96.0226 | 99:32 | 49:46 | 96.7122 | 96.6006
67 | Rannabelagali | 1 | 1 | 3:22 | 6:14 | 15:48 | 11:20 | 27:08 | 43:38 | 30:30 | 30:30 | 96.353 | 95.9005 | 49:52 | 49:52 | 97.0196 | 96.5938
68 | Rabakavi | 2 | 2 | 0:40 | 6:45 | 21:00 | 9:30 | 30:30 | 67:35 | 31:10 | 15:35 | 97.9503 | 97.9055 | 74:20 | 37:10 | 97.6918 | 97.4613
69 | Banahatti | 2 | 2 | 0:00 | 4:10 | 28:10 | 8:35 | 36:45 | 66:45 | 36:45 | 18:22 | 97.5302 | 97.5302 | 70:55 | 35:28 | 97.7203 | 97.578
70 | Terdal | 2 | 2 | 0:00 | 18:30 | 28:10 | 19:35 | 47:45 | 115:42 | 47:45 | 23:52 | 96.791 | 96.791 | 134:12 | 67:06 | 96.0485 | 95.4167
71 | Mudhol | 4 | 4 | 32:22 | 44:20 | 43:49 | 24:36 | 68:25 | 195:40 | 100:47 | 25:12 | 97.7011 | 96.6135 | 240:00 | 60:00 | 96.6587 | 95.9016
72 | Bilagi | 1 | 1 | 0:50 | 3:15 | 22:50 | 7:20 | 30:10 | 53:55 | 31:00 | 31:00 | 95.9453 | 95.8333 | 57:10 | 57:10 | 96.3172 | 96.0952
73 | Lokapur | 2 | 2 | 0:00 | 0:25 | 80:05 | 29:50 | 109:55 | 153:25 | 109:55 | 54:57 | 92.6131 | 92.6131 | 153:50 | 76:55 | 94.7604 | 94.7461
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of June-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2022 |  |  |  | Reliability for cumulative period from Apr-22 to June-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 80 | 80 | 157:27 | 251:51 | 379:20 | 253:07 | 632:27 | 2416:03 | 789:54 | 9:52 | 98.902 | 98.6286 | 2667:54 | 33:21 | 98.6172 | 98.473
2 | Dharwad(R) | 14 | 14 | 11:40 | 15:00 | 127:46 | 50:07 | 177:53 | 826:30 | 189:33 | 13:32 | 98.2353 | 98.1195 | 841:30 | 60:06 | 97.2969 | 97.2478
3 | Kundagol | 1 | 1 | 27:10 | 74:10 | 4:55 | 9:05 | 14:00 | 34:55 | 41:10 | 41:10 | 98.0556 | 94.2824 | 109:05 | 109:05 | 98.4013 | 95.0053
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 10:13 | 11:10 | 21:23 | 74:19 | 21:23 | 21:23 | 97.0301 | 97.0301 | 74:19 | 74:19 | 96.5972 | 96.5972
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 8:00 | 6:55 | 14:55 | 88:57 | 14:55 | 14:55 | 97.9282 | 97.9282 | 88:57 | 88:57 | 95.9272 | 95.9272
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 7:50 | 8:10 | 16:00 | 171:10 | 16:00 | 8:00 | 98.8889 | 98.8889 | 171:10 | 85:35 | 96.0813 | 96.0813
7 | Alnavar | 2 | 2 | 0:00 | 0:00 | 4:30 | 28:20 | 32:50 | 113:35 | 32:50 | 16:25 | 97.7199 | 97.7199 | 113:35 | 56:47 | 97.3996 | 97.3996
8 | Naragund | 2 | 2 | 1:10 | 37:40 | 17:30 | 32:30 | 50:00 | 151:40 | 51:10 | 25:35 | 96.5278 | 96.4468 | 189:20 | 94:40 | 96.5278 | 95.6654
9 | Shirahatti | 1 | 1 | 0:00 | 0:00 | 5:50 | 11:50 | 17:40 | 63:30 | 17:40 | 17:40 | 97.5463 | 97.5463 | 63:30 | 63:30 | 97.0925 | 97.0925
10 | Laxmeshwar | 3 | 3 | 0:00 | 0:00 | 20:36 | 15:50 | 36:26 | 239:35 | 36:26 | 12:09 | 98.3133 | 98.3133 | 239:35 | 79:52 | 96.3434 | 96.3434
11 | Naregal | 1 | 1 | 0:00 | 2:50 | 6:35 | 12:00 | 18:35 | 45:25 | 18:35 | 18:35 | 97.419 | 97.419 | 48:15 | 48:15 | 97.9205 | 97.7908
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 9:10 | 9:50 | 19:00 | 124:10 | 19:00 | 9:30 | 98.6806 | 98.6806 | 124:10 | 62:05 | 97.1574 | 97.1574
13 | Ron | 3 | 3 | 0:00 | 0:00 | 19:05 | 10:40 | 29:45 | 211:14 | 29:45 | 9:55 | 98.6227 | 98.6227 | 211:14 | 70:25 | 96.776 | 96.776
14 | Mundaragi | 1 | 1 | 0:00 | 0:00 | 16:55 | 18:50 | 35:45 | 110:15 | 35:45 | 35:45 | 95.0347 | 95.0347 | 110:15 | 110:15 | 94.9519 | 94.9519
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 18:18 | 57:46 | 76:04 | 265:16 | 76:04 | 76:04 | 89.4352 | 89.4352 | 265:16 | 265:16 | 87.8541 | 87.8541
16 | Savanur | 2 | 2 | 1:10 | 4:15 | 14:10 | 5:00 | 19:10 | 110:25 | 20:20 | 10:10 | 98.669 | 98.588 | 114:40 | 57:20 | 97.4721 | 97.3748
17 | Shiggaon | 3 | 3 | 13:40 | 91:10 | 37:10 | 19:10 | 56:20 | 224:30 | 70:00 | 23:20 | 97.392 | 96.7593 | 315:40 | 105:13 | 96.5736 | 95.1821
18 | Bankapur | 1 | 1 | 18:25 | 47:25 | 21:15 | 13:40 | 34:55 | 131:00 | 53:20 | 53:20 | 95.1505 | 92.5926 | 178:25 | 178:25 | 94.0018 | 91.8307
19 | Hangal | 2 | 2 | 6:04 | 10:04 | 26:15 | 44:50 | 71:05 | 166:25 | 77:09 | 38:34 | 95.0637 | 94.6424 | 176:29 | 88:14 | 96.1901 | 95.9596
20 | Ranebennur | 10 | 10 | 4:00 | 42:33 | 120:34 | 46:59 | 167:33 | 517:50 | 171:33 | 17:09 | 97.6729 | 97.6174 | 560:23 | 56:02 | 97.629 | 97.4341
21 | Tuminakatti | 1 | 1 | 0:35 | 4:05 | 35:20 | 10:05 | 45:25 | 88:55 | 46:00 | 46:00 | 93.6921 | 93.6111 | 93:00 | 93:00 | 95.9287 | 95.7418
22 | Rattihalli | 1 | 1 | 0:35 | 7:45 | 21:35 | 7:20 | 28:55 | 83:10 | 29:30 | 29:30 | 95.9838 | 95.9028 | 90:55 | 90:55 | 96.192 | 95.8371
23 | Hirekerur | 1 | 1 | 1:00 | 6:35 | 17:00 | 14:30 | 31:30 | 93:05 | 32:30 | 32:30 | 95.625 | 95.4861 | 99:40 | 99:40 | 95.7379 | 95.4365
24 | Byadagi | 5 | 5 | 27:21 | 124:11 | 38:18 | 27:35 | 65:53 | 291:03 | 93:14 | 18:39 | 98.1699 | 97.4102 | 415:14 | 83:03 | 97.3347 | 96.1975
25 | Sirsi | 6 | 6 | 41:13 | 100:42 | 74:32 | 18:09 | 92:41 | 223:24 | 133:54 | 22:19 | 97.8546 | 96.9005 | 324:06 | 54:01 | 98.2952 | 97.5267
26 | Yellapur | 1 | 1 | 14:25 | 33:50 | 11:45 | 3:40 | 15:25 | 33:20 | 29:50 | 29:50 | 97.8588 | 95.8565 | 67:10 | 67:10 | 98.4737 | 96.9246
27 | Mundagod | 1 | 1 | 1:40 | 1:40 | 7:10 | 9:35 | 16:45 | 46:20 | 18:25 | 18:25 | 97.6736 | 97.4421 | 48:00 | 48:00 | 97.8785 | 97.8022
28 | Siddapur | 1 | 1 | 7:20 | 28:40 | 5:25 | 5:30 | 10:55 | 42:35 | 18:15 | 18:15 | 98.4838 | 97.4653 | 71:15 | 71:15 | 98.0502 | 96.7376
29 | Dandeli | 7 | 7 | 17:18 | 25:44 | 65:44 | 11:53 | 77:37 | 251:27 | 94:55 | 13:34 | 98.46 | 98.1167 | 277:11 | 39:36 | 98.3552 | 98.1869
30 | Haliyal | 2 | 2 | 0:00 | 5:36 | 4:10 | 5:40 | 9:50 | 88:55 | 9:50 | 4:55 | 99.3171 | 99.3171 | 94:31 | 47:16 | 97.9644 | 97.8362
31 | Ankola | 3 | 3 | 22:17 | 81:47 | 36:45 | 39:58 | 76:43 | 126:46 | 99:00 | 33:00 | 96.4483 | 95.4167 | 208:33 | 69:31 | 98.0652 | 96.817
32 | Kumta | 3 | 3 | 0:48 | 24:18 | 23:50 | 28:04 | 51:54 | 118:37 | 52:42 | 17:34 | 97.5972 | 97.5602 | 142:55 | 47:38 | 98.1896 | 97.8187
33 | Gokarna | 1 | 1 | 12:10 | 45:57 | 4:05 | 3:50 | 7:55 | 18:20 | 20:05 | 20:05 | 98.9005 | 97.2106 | 64:17 | 64:17 | 99.1606 | 97.0566
34 | Kasarkod | 1 | 1 | 36:17 | 53:29 | 10:51 | 8:35 | 19:26 | 41:45 | 55:43 | 55:43 | 97.3009 | 92.2616 | 95:14 | 95:14 | 98.0884 | 95.6395
35 | Honnavar | 3 | 3 | 4:21 | 47:00 | 30:38 | 32:09 | 62:47 | 153:07 | 67:08 | 22:23 | 97.0934 | 96.892 | 200:07 | 66:42 | 97.6631 | 96.9457
36 | Murdeshwar | 4 | 4 | 6:52 | 67:20 | 55:59 | 29:45 | 85:44 | 195:23 | 92:36 | 23:09 | 97.0231 | 96.7847 | 262:43 | 65:41 | 97.7635 | 96.9927
37 | Bhatkal | 3 | 3 | 17:15 | 84:09 | 23:20 | 10:48 | 34:08 | 97:50 | 51:23 | 17:08 | 98.4198 | 97.6211 | 181:59 | 60:40 | 98.5068 | 97.2225
38 | Khanapur | 2 | 2 | 12:55 | 36:25 | 21:40 | 13:30 | 35:10 | 172:35 | 48:05 | 24:02 | 97.5579 | 96.6609 | 209:00 | 104:30 | 96.0489 | 95.2152
39 | Bailhongal | 3 | 3 | 0:00 | 0:00 | 21:10 | 15:35 | 36:45 | 266:50 | 36:45 | 12:15 | 98.2986 | 98.2986 | 266:50 | 88:57 | 95.9275 | 95.9275
40 | Kittur | 1 | 1 | 0:00 | 0:45 | 17:20 | 8:00 | 25:20 | 71:55 | 25:20 | 25:20 | 96.4815 | 96.4815 | 72:40 | 72:40 | 96.7071 | 96.6728
41 | M K Hubli | 1 | 1 | 0:00 | 0:45 | 20:10 | 1:45 | 21:55 | 69:50 | 21:55 | 21:55 | 96.956 | 96.956 | 70:35 | 70:35 | 96.8025 | 96.7682
42 | Soundatti | 3 | 3 | 6:55 | 22:27 | 24:18 | 4:28 | 28:46 | 136:03 | 35:41 | 11:54 | 98.6682 | 98.348 | 158:30 | 52:50 | 97.9235 | 97.5809
43 | Munavalli | 1 | 1 | 14:05 | 34:25 | 35:20 | 3:50 | 39:10 | 105:40 | 53:15 | 53:15 | 94.5602 | 92.6042 | 140:05 | 140:05 | 95.1618 | 93.5859
44 | Yaragatti | 1 | 1 | 8:50 | 24:59 | 34:20 | 9:47 | 44:07 | 139:13 | 52:57 | 52:57 | 93.8727 | 92.6458 | 164:12 | 164:12 | 93.6256 | 92.4817
45 | Ramdurg | 2 | 2 | 2:00 | 13:46 | 34:45 | 11:05 | 45:50 | 150:15 | 47:50 | 23:55 | 96.8171 | 96.6782 | 164:01 | 82:00 | 96.5602 | 96.245
46 | Gokak | 10 | 10 | 30:04 | 170:12 | 13:47 | 14:39 | 28:26 | 144:34 | 58:30 | 5:51 | 99.6051 | 99.1875 | 314:46 | 31:29 | 99.3381 | 98.5588
47 | Mudalagi | 2 | 2 | 1:10 | 2:45 | 31:50 | 5:00 | 36:50 | 170:25 | 38:00 | 19:00 | 97.4421 | 97.3611 | 173:10 | 86:35 | 96.0985 | 96.0356
48 | Konnur | 1 | 1 | 0:40 | 2:10 | 19:15 | 1:50 | 21:05 | 81:55 | 21:45 | 21:45 | 97.0718 | 96.9792 | 84:05 | 84:05 | 96.2492 | 96.15
49 | Raibag | 1 | 1 | 0:00 | 0:00 | 15:05 | 13:00 | 28:05 | 136:20 | 28:05 | 28:05 | 96.0995 | 96.0995 | 136:20 | 136:20 | 93.7576 | 93.7576
50 | Kudachi | 1 | 1 | 0:00 | 0:40 | 43:55 | 1:25 | 45:20 | 187:35 | 45:20 | 45:20 | 93.7037 | 93.7037 | 188:15 | 188:15 | 91.411 | 91.3805
51 | Athani | 7 | 7 | 26:21 | 123:45 | 41:04 | 83:43 | 124:47 | 668:31 | 151:08 | 21:35 | 97.5241 | 97.0013 | 792:16 | 113:11 | 95.6272 | 94.8177
52 | Chikkodi | 4 | 4 | 0:00 | 0:00 | 19:17 | 9:38 | 28:55 | 103:35 | 28:55 | 7:14 | 98.9959 | 98.9959 | 103:35 | 25:54 | 98.8143 | 98.8143
53 | Nippani | 5 | 5 | 0:00 | 0:00 | 94:00 | 37:35 | 131:35 | 434:12 | 131:35 | 26:19 | 96.3449 | 96.3449 | 434:12 | 86:50 | 96.0238 | 96.0238
54 | Sadalaga | 1 | 1 | 1:50 | 16:55 | 22:25 | 3:30 | 25:55 | 80:15 | 27:45 | 27:45 | 96.4005 | 96.1458 | 97:10 | 97:10 | 96.3255 | 95.551
55 | Muddebihal | 2 | 2 | 0:55 | 16:10 | 52:55 | 21:50 | 74:45 | 246:10 | 75:40 | 37:50 | 94.809 | 94.7454 | 262:20 | 131:10 | 94.3643 | 93.9942
56 | Talikoti | 1 | 1 | 4:30 | 16:45 | 40:25 | 19:40 | 60:05 | 123:40 | 64:35 | 64:35 | 91.6551 | 91.0301 | 140:25 | 140:25 | 94.3376 | 93.5707
57 | B.Bagewadi | 1 | 1 | 0:31 | 9:53 | 12:54 | 4:38 | 17:32 | 56:48 | 18:03 | 18:03 | 97.5648 | 97.4931 | 66:41 | 66:41 | 97.3993 | 96.9467
58 | Indi | 3 | 3 | 0:13 | 45:35 | 33:28 | 8:07 | 41:35 | 118:37 | 41:48 | 13:56 | 98.0748 | 98.0648 | 164:12 | 54:44 | 98.1896 | 97.4939
59 | Sindagi | 2 | 2 | 33:00 | 57:00 | 23:10 | 12:10 | 35:20 | 134:35 | 68:20 | 34:10 | 97.5463 | 95.2546 | 191:35 | 95:48 | 96.9189 | 95.6139
60 | Guledgudda | 1 | 1 | 0:10 | 1:01 | 21:21 | 10:10 | 31:31 | 65:22 | 31:41 | 31:41 | 95.6227 | 95.5995 | 66:23 | 66:23 | 97.007 | 96.9605
61 | Ilkal | 7 | 7 | 5:20 | 45:02 | 62:20 | 177:23 | 239:43 | 638:49 | 245:03 | 35:00 | 95.2437 | 95.1379 | 683:51 | 97:42 | 95.8215 | 95.5269
62 | Kerur | 1 | 1 | 8:47 | 11:32 | 24:59 | 17:56 | 42:55 | 142:47 | 51:42 | 51:42 | 94.0394 | 92.8194 | 154:19 | 154:19 | 93.4623 | 92.9342
63 | Hungund | 4 | 4 | 8:00 | 27:47 | 56:17 | 51:08 | 107:25 | 399:33 | 115:25 | 28:51 | 96.2703 | 95.9925 | 427:20 | 106:50 | 95.4264 | 95.1084
64 | Badami | 1 | 1 | 8:08 | 11:02 | 11:42 | 17:15 | 28:57 | 80:19 | 37:05 | 37:05 | 95.9792 | 94.8495 | 91:21 | 91:21 | 96.3225 | 95.8173
65 | Jamkhandi | 6 | 6 | 12:35 | 21:45 | 70:20 | 20:45 | 91:05 | 447:25 | 103:40 | 17:17 | 97.8916 | 97.6003 | 469:10 | 78:12 | 96.5856 | 96.4197
66 | Mahalingapur | 2 | 2 | 3:25 | 6:41 | 24:43 | 5:31 | 30:14 | 126:30 | 33:39 | 16:50 | 97.9005 | 97.6632 | 133:11 | 66:36 | 97.1039 | 96.9509
67 | Rannabelagali | 1 | 1 | 1:05 | 7:19 | 19:25 | 8:45 | 28:10 | 71:48 | 29:15 | 29:15 | 96.088 | 95.9375 | 79:07 | 79:07 | 96.7125 | 96.3774
68 | Rabakavi | 2 | 2 | 19:00 | 25:45 | 12:30 | 7:05 | 19:35 | 87:10 | 38:35 | 19:18 | 98.64 | 97.3206 | 112:55 | 56:27 | 98.0044 | 97.4149
69 | Banahatti | 2 | 2 | 2:20 | 6:30 | 57:40 | 10:25 | 68:05 | 134:50 | 70:25 | 35:12 | 95.272 | 95.11 | 141:20 | 70:40 | 96.9132 | 96.7643
70 | Terdal | 2 | 2 | 0:00 | 18:30 | 23:40 | 4:00 | 27:40 | 143:22 | 27:40 | 13:50 | 98.0787 | 98.0787 | 161:52 | 80:56 | 96.7178 | 96.2943
71 | Mudhol | 4 | 4 | 13:25 | 57:45 | 49:27 | 32:42 | 82:09 | 277:49 | 95:34 | 23:54 | 97.1476 | 96.6817 | 335:34 | 83:54 | 96.8199 | 96.1588
72 | Bilagi | 1 | 1 | 1:17 | 4:32 | 22:30 | 3:45 | 26:15 | 80:10 | 27:32 | 27:32 | 96.3542 | 96.1759 | 84:42 | 84:42 | 96.3294 | 96.1218
73 | Lokapur | 2 | 2 | 2:50 | 3:15 | 66:10 | 51:30 | 117:40 | 271:05 | 120:30 | 60:15 | 91.8287 | 91.6319 | 274:20 | 137:10 | 93.7939 | 93.7195
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]

## RURAL (Incl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Apr-22
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 387:10 | 387:10 | 5505:33 | 2950:22 | 8455:55 | 8455:55 | 8843:05 | 192:14 | 74.4689 | 73.2999 | 8843:05 | 192:14 | 74.4689 | 73.2999
2 | Dharwad Rural | 91 | 91 | 60:35 | 60:35 | 16984:51 | 7363:00 | 1014.4938 | 1014.4938 | 1017.0181 | 268:13 | 62.8391 | 62.7466 | 1017.0181 | 268:13 | 62.8391 | 62.7466
3 | Gadag | 113 | 113 | 105:20 | 105:20 | 23309:01 | 3687:12 | 1124.8424 | 1124.8424 | 1129.2313 | 239:50 | 66.8188 | 66.6893 | 1129.2313 | 239:50 | 66.8188 | 66.6893
4 | Ron | 58 | 58 | 267:37 | 267:37 | 14520:42 | 1415:39 | 15936:21 | 15936:21 | 16203:58 | 279:23 | 61.8382 | 61.1974 | 16203:58 | 279:23 | 61.8382 | 61.1974
5 | Haveri | 204 | 204 | 2018:12 | 2018:12 | 2450.8479 | 10752:39 | 2898.875 | 2898.875 | 2982.9667 | 350:56 | 52.6328 | 51.2587 | 2982.9667 | 350:56 | 52.6328 | 51.2587
6 | Ranebennur | 201 | 201 | 1632:38 | 1632:38 | 2524.6611 | 10276:01 | 2952.8285 | 2952.8285 | 3020.8549 | 360:42 | 51.031 | 49.9029 | 3020.8549 | 360:42 | 51.031 | 49.9029
7 | Sirsi | 63 | 63 | 597:16 | 597:16 | 607:37 | 2438:26 | 3046:03 | 3046:03 | 3643:19 | 57:50 | 93.2847 | 91.968 | 3643:19 | 57:50 | 93.2847 | 91.968
8 | Dandeli | 25 | 25 | 4:58 | 4:58 | 372:16 | 634:46 | 1007:02 | 1007:02 | 1012:00 | 40:29 | 94.4054 | 94.3778 | 1012:00 | 40:29 | 94.4054 | 94.3778
9 | Karwar | 33 | 33 | 322:49 | 322:49 | 339:39 | 502:59 | 842:38 | 842:38 | 1165:27 | 35:19 | 96.4536 | 95.0949 | 1165:27 | 35:19 | 96.4536 | 95.0949
10 | Honnavar | 40 | 40 | 509:40 | 509:40 | 516:01 | 679:05 | 1195:06 | 1195:06 | 1704:46 | 42:37 | 95.8503 | 94.0807 | 1704:46 | 42:37 | 95.8503 | 94.0807
11 | Belagavi | 149 | 149 | 1452:49 | 1452:49 | 16899:11 | 6408:04 | 23307:15 | 23307:15 | 1031.6694 | 166:10 | 78.2744 | 76.9201 | 1031.6694 | 166:10 | 78.2744 | 76.9201
12 | Bailhongal | 193 | 193 | 2284:40 | 2284:40 | 1936.1694 | 6009:09 | 2186.5507 | 2186.5507 | 2281.7451 | 283:44 | 62.2357 | 60.5916 | 2281.7451 | 283:44 | 62.2357 | 60.5916
13 | Ramdurg | 88 | 88 | 548:55 | 548:55 | 1123.4403 | 2736:32 | 1237.4625 | 1237.4625 | 1260.334 | 343:44 | 53.1264 | 52.2601 | 1260.334 | 343:44 | 53.1264 | 52.2601
14 | Ghataprabha | 168 | 168 | 693:28 | 693:28 | 1536.884 | 5868:12 | 1781.3924 | 1781.3924 | 1810.2868 | 258:37 | 64.6549 | 64.0816 | 1810.2868 | 258:37 | 64.6549 | 64.0816
15 | Raibag | 175 | 175 | 850:55 | 850:55 | 1808.6736 | 4709:21 | 2004.8965 | 2004.8965 | 2040.3514 | 279:49 | 61.8115 | 61.1362 | 2040.3514 | 279:49 | 61.8115 | 61.1362
16 | Athani | 200 | 200 | 1579:00 | 1579:00 | 1697.191 | 4934:10 | 1902.7812 | 1902.7812 | 1968.5729 | 236:14 | 68.287 | 67.1905 | 1968.5729 | 236:14 | 68.287 | 67.1905
17 | Chikkodi | 192 | 192 | 911:22 | 911:22 | 1958.1729 | 4750:36 | 2156.1146 | 2156.1146 | 2194.0882 | 274:16 | 62.5675 | 61.9082 | 2194.0882 | 274:16 | 62.5675 | 61.9082
18 | Vijayapur | 183 | 183 | 985:20 | 985:20 | 1969.1 | 6169:46 | 2226.1736 | 2226.1736 | 2267.2292 | 297:20 | 59.4504 | 58.7026 | 2267.2292 | 297:20 | 59.4504 | 58.7026
19 | Indi | 259 | 259 | 1037:24 | 1037:24 | 2574.8458 | 5591:36 | 2807.8292 | 2807.8292 | 2851.0542 | 264:11 | 63.8632 | 63.3069 | 2851.0542 | 264:11 | 63.8632 | 63.3069
20 | B.Bagewadi | 149 | 149 | 1169:20 | 1169:20 | 1512.2146 | 4869:55 | 1715.1278 | 1715.1278 | 1763.85 | 284:07 | 61.6303 | 60.5403 | 1763.85 | 284:07 | 61.6303 | 60.5403
21 | Bagalkot | 198 | 198 | 895:07 | 895:07 | 2169.325 | 5235:53 | 2387.4868 | 2387.4868 | 2424.7833 | 293:55 | 59.8066 | 59.1787 | 2424.7833 | 293:55 | 59.8066 | 59.1787
22 | Jamkhandi | 213 | 213 | 1204:22 | 1204:22 | 2412.5549 | 2941:48 | 2535.1299 | 2535.1299 | 2585.3118 | 291:18 | 60.3266 | 59.5413 | 2585.3118 | 291:18 | 60.3266 | 59.5413
23 | Mudhol | 195 | 195 | 551:07 | 551:07 | 2698.7271 | 2773:52 | 2814.3049 | 2814.3049 | 2837.2681 | 349:12 | 51.8922 | 51.4997 | 2837.2681 | 349:12 | 51.8922 | 51.4997
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2022 |  |  |  | Reliability for cumulative period from Apr-22 to May-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 243:11 | 630:21 | 6102:22 | 2397:15 | 8499:37 | 16955:32 | 8742:48 | 190:04 | 75.1647 | 74.4542 | 17585:53 | 382:18 | 74.8225 | 73.8865
2 | Dharwad Rural | 92 | 92 | 355:55 | 416:30 | 16771:46 | 5105:25 | 21877:11 | 1926.0431 | 22233:06 | 241:40 | 68.0382 | 67.5183 | 1943.3972 | 506:58 | 65.6799 | 65.3707
3 | Gadag | 113 | 113 | 317:30 | 422:50 | 22306:43 | 5964:36 | 1177.9715 | 2302.8139 | 1191.2007 | 253:00 | 66.3725 | 65.9948 | 2320.4319 | 492:50 | 66.592 | 66.3364
4 | Ron | 59 | 59 | 320:20 | 587:57 | 15727:55 | 1400:47 | 17128:42 | 1377.7104 | 17449:02 | 295:45 | 60.9789 | 60.2491 | 1402.2083 | 570:23 | 61.7196 | 61.0389
5 | Haveri | 205 | 205 | 2696:43 | 4714:55 | 2222.7917 | 1045.9306 | 3268.7222 | 6167.5972 | 3381.0854 | 395:50 | 48.5646 | 46.7965 | 6364.0521 | 745:04 | 50.679 | 49.1079
6 | Ranebennur | 204 | 204 | 1723:37 | 3356:15 | 2460.7118 | 19182:42 | 3259.991 | 6212.8194 | 3331.8083 | 391:59 | 48.4505 | 47.3149 | 6352.6632 | 747:22 | 50.0738 | 48.95
7 | Sirsi | 63 | 63 | 396:53 | 994:09 | 798:36 | 3201:18 | 3999:54 | 7045:57 | 4396:47 | 69:47 | 91.4663 | 90.6196 | 8040:06 | 127:37 | 92.3606 | 91.2827
8 | Dandeli | 25 | 25 | 278:09 | 283:07 | 378:30 | 506:37 | 885:07 | 1892:09 | 1163:16 | 46:32 | 95.2413 | 93.7459 | 2175:16 | 87:01 | 94.8302 | 94.0566
9 | Karwar | 33 | 33 | 315:09 | 637:58 | 321:58 | 643:52 | 965:50 | 1808:28 | 1280:59 | 38:49 | 96.0662 | 94.7826 | 2446:26 | 74:08 | 96.2567 | 94.9362
10 | Honnavar | 40 | 40 | 747:15 | 1256:55 | 588:20 | 1202:16 | 1790:36 | 2985:42 | 2537:51 | 63:27 | 93.9832 | 91.4723 | 4242:37 | 106:04 | 94.9015 | 92.7551
11 | Belagavi | 149 | 149 | 730:59 | 2183:48 | 15216:33 | 4259:01 | 19475:34 | 1782.6174 | 20206:33 | 135:37 | 82.4317 | 81.7723 | 1873.609 | 301:47 | 80.3871 | 79.386
12 | Bailhongal | 193 | 193 | 1302:00 | 3586:40 | 1965.2722 | 6516:39 | 2236.7993 | 4423.35 | 2291.0493 | 284:54 | 62.6141 | 61.7073 | 4572.7944 | 568:38 | 62.428 | 61.1586
13 | Ramdurg | 88 | 88 | 429:49 | 978:44 | 1188.7319 | 3608:59 | 1339.1062 | 2576.5687 | 1357.0153 | 370:06 | 50.9125 | 50.256 | 2617.3493 | 713:49 | 52.0013 | 51.2416
14 | Ghataprabha | 168 | 168 | 328:42 | 1022:10 | 1596.35 | 4386:09 | 1779.1063 | 3560.4986 | 1792.8021 | 256:07 | 65.839 | 65.576 | 3603.0889 | 514:44 | 65.2566 | 64.8411
15 | Raibag | 177 | 177 | 311:39 | 1162:34 | 1810.4215 | 3902:28 | 1973.0243 | 3977.9208 | 1986.0097 | 269:17 | 64.0418 | 63.8052 | 4026.3611 | 545:57 | 63.1572 | 62.7085
16 | Athani | 201 | 201 | 990:57 | 2569:57 | 1525.0035 | 5352:55 | 1748.0417 | 3650.8229 | 1789.3312 | 213:39 | 71.946 | 71.2834 | 3757.9042 | 448:42 | 70.2241 | 69.3508
17 | Chikkodi | 192 | 192 | 627:15 | 1538:37 | 1980.9264 | 2125:13 | 2069.4771 | 4225.5917 | 2095.6125 | 261:57 | 65.2306 | 64.7915 | 4289.7007 | 536:13 | 63.9208 | 63.3735
18 | Vijayapur | 189 | 189 | 958:18 | 1943:38 | 2543.1111 | 5502:47 | 2772.3938 | 4998.5674 | 2812.3229 | 357:07 | 52.6815 | 52 | 5079.5521 | 645:01 | 56.6435 | 55.9411
19 | Indi | 259 | 259 | 1969:19 | 3006:43 | 2866.9146 | 7124:07 | 3163.7528 | 5971.5819 | 3245.8076 | 300:46 | 60.5959 | 59.5739 | 6096.8618 | 564:58 | 62.2028 | 61.4098
20 | B.Bagewadi | 151 | 151 | 904:54 | 2074:14 | 1633.2486 | 5807:05 | 1875.2104 | 3590.3382 | 1912.9146 | 304:02 | 59.94 | 59.1345 | 3676.7646 | 584:23 | 61.0212 | 60.0829
21 | Bagalkot | 198 | 198 | 1023:00 | 1918:07 | 2142.8167 | 9598:43 | 2542.7632 | 4930.25 | 2585.3882 | 313:23 | 58.5734 | 57.879 | 5010.1715 | 607:18 | 59.1799 | 58.5182
22 | Jamkhandi | 213 | 213 | 587:11 | 1791:33 | 2485.3806 | 3596:22 | 2635.2292 | 5170.359 | 2659.6951 | 299:41 | 60.0904 | 59.7199 | 5245.0069 | 590:59 | 60.2066 | 59.6321
23 | Mudhol | 196 | 196 | 450:04 | 1001:11 | 2770.875 | 4424:44 | 2955.2389 | 5769.5438 | 2973.9917 | 364:10 | 51.3621 | 51.0535 | 5811.2597 | 711:35 | 51.7435 | 51.3946
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2022 |  |  |  | Reliability for cumulative period from Apr-22 to June-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 215:40 | 846:01 | 6554:33 | 1964:24 | 8518:57 | 1061.4368 | 8734:37 | 189:53 | 74.2785 | 73.6274 | 1096.6875 | 572:11 | 74.6432 | 73.8011
2 | Dharwad Rural | 92 | 92 | 140:50 | 557:20 | 16778:31 | 3557:03 | 20335:34 | 2773.3583 | 20476:24 | 222:34 | 69.3002 | 69.0876 | 2796.5806 | 729:33 | 66.8734 | 66.596
3 | Gadag | 113 | 113 | 285:25 | 708:15 | 21799:50 | 3859:03 | 1069.1201 | 3371.934 | 1081.0125 | 229:36 | 68.4625 | 68.1117 | 3401.4444 | 722:26 | 67.2087 | 66.9217
4 | Ron | 59 | 59 | 204:30 | 792:27 | 15036:05 | 1155:21 | 16191:26 | 2052.3535 | 16395:56 | 277:54 | 61.8846 | 61.4032 | 2085.3722 | 848:17 | 61.774 | 61.159
5 | Haveri | 205 | 205 | 1588:16 | 6303:11 | 2378.7465 | 11715:43 | 2866.9014 | 9034.4986 | 2933.0792 | 343:23 | 53.3837 | 52.3077 | 9297.1312 | 1088:27 | 51.5706 | 50.1628
6 | Ranebennur | 205 | 205 | 1155:23 | 4511:38 | 2571.3514 | 8863:58 | 2940.6833 | 9153.5028 | 2988.8243 | 349:55 | 52.184 | 51.4012 | 9341.4875 | 1093:38 | 50.9327 | 49.925
7 | Sirsi | 62 | 62 | 585:04 | 1579:13 | 754:47 | 2147:46 | 2902:33 | 9948:30 | 3487:37 | 56:15 | 93.4979 | 92.1872 | 11527:43 | 185:56 | 92.6529 | 91.4867
8 | Dandeli | 25 | 25 | 82:04 | 365:11 | 280:46 | 371:50 | 652:36 | 2544:45 | 734:40 | 29:23 | 96.3744 | 95.9185 | 2909:56 | 116:24 | 95.3393 | 94.6705
9 | Karwar | 29 | 29 | 369:00 | 1006:58 | 419:31 | 761:41 | 1181:12 | 2989:40 | 1550:12 | 53:27 | 94.3429 | 92.5757 | 3996:38 | 137:49 | 95.2797 | 93.6898
10 | Honnavar | 40 | 40 | 632:18 | 1889:13 | 654:36 | 1334:40 | 1989:16 | 4974:58 | 2621:34 | 65:32 | 93.0928 | 90.8973 | 6864:11 | 171:36 | 94.3052 | 92.1426
11 | Belagavi | 149 | 149 | 461:47 | 2645:35 | 14992:54 | 3018:00 | 18010:54 | 2533.0715 | 18472:41 | 123:59 | 83.2113 | 82.7809 | 2643.3042 | 425:46 | 81.3182 | 80.5052
12 | Bailhongal | 193 | 193 | 1597:58 | 5184:38 | 1907.8556 | 5162:26 | 2122.9569 | 6546.3069 | 2189.5389 | 272:16 | 63.3341 | 62.1841 | 6762.3333 | 840:55 | 62.7267 | 61.4967
13 | Ramdurg | 88 | 88 | 544:17 | 1523:01 | 1220.2785 | 3116:36 | 1350.1368 | 3926.7056 | 1372.8153 | 374:24 | 48.8585 | 47.9994 | 3990.1646 | 1088:14 | 50.9652 | 50.1728
14 | Ghataprabha | 170 | 170 | 532:08 | 1554:18 | 1527.8313 | 2084:42 | 1614.6938 | 5175.1924 | 1636.866 | 231:05 | 68.3393 | 67.9046 | 5239.9549 | 739:46 | 66.5469 | 66.1283
15 | Raibag | 178 | 178 | 511:06 | 1673:40 | 1754.9181 | 1578:02 | 1820.6694 | 5798.5903 | 1841.9653 | 248:21 | 65.9051 | 65.5063 | 5868.3264 | 791:14 | 64.2018 | 63.7713
16 | Athani | 201 | 201 | 661:13 | 3231:10 | 1662.8292 | 2032:14 | 1747.5056 | 5398.3285 | 1775.0562 | 211:57 | 71.0198 | 70.5629 | 5532.9604 | 660:39 | 70.4864 | 69.7504
17 | Chikkodi | 191 | 191 | 443:39 | 1982:16 | 1912.2097 | 1929:33 | 1992.6076 | 6218.1993 | 2011.0931 | 252:42 | 65.225 | 64.9024 | 6300.7937 | 791:43 | 64.2242 | 63.749
18 | Vijayapur | 190 | 190 | 745:36 | 2689:14 | 2504.3833 | 4392:19 | 2687.3965 | 7685.9639 | 2718.4632 | 343:23 | 52.8527 | 52.3077 | 7798.0153 | 985:01 | 55.5468 | 54.8987
19 | Indi | 261 | 261 | 1756:20 | 4763:03 | 2735.9396 | 9661:58 | 3138.5215 | 9110.1035 | 3211.7021 | 295:20 | 59.9167 | 58.9821 | 9308.5639 | 855:58 | 61.6433 | 60.8077
20 | B.Bagewadi | 151 | 151 | 423:46 | 2498:00 | 1574.9521 | 4895:05 | 1778.9139 | 5369.2521 | 1796.5708 | 285:33 | 60.7304 | 60.3406 | 5473.3354 | 869:56 | 60.9253 | 60.1679
21 | Bagalkot | 198 | 198 | 1050:23 | 2968:30 | 2134.1361 | 6714:09 | 2413.8924 | 7344.1424 | 2457.6583 | 297:54 | 59.3621 | 58.6253 | 7467.8299 | 905:11 | 59.24 | 58.5535
22 | Jamkhandi | 213 | 213 | 969:31 | 2761:04 | 2328.3472 | 1822:39 | 2404.291 | 7574.65 | 2444.6875 | 275:27 | 62.3742 | 61.742 | 7689.6944 | 866:27 | 60.9212 | 60.3276
23 | Mudhol | 196 | 196 | 477:05 | 1478:16 | 2676.9236 | 3771:11 | 2834.0562 | 8603.6 | 2853.9347 | 349:28 | 51.8018 | 51.4637 | 8665.1944 | 1061:03 | 51.7627 | 51.4174
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]

## RURAL(Excl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of April-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Apr-22
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 387:10 | 387:10 | 960:29 | 2950:22 | 3910:51 | 3910:51 | 4298:01 | 93:26 | 88.1919 | 87.0229 | 4298:01 | 93:26 | 88.1919 | 87.0229
2 | Dharwad Rural | 91 | 91 | 60:35 | 60:35 | 2872:52 | 7363:00 | 10235:52 | 10235:52 | 10296:27 | 113:09 | 84.3775 | 84.285 | 10296:27 | 113:09 | 84.3775 | 84.285
3 | Gadag | 113 | 113 | 105:20 | 105:20 | 1699:33 | 3687:12 | 5386:45 | 5386:45 | 5492:05 | 48:36 | 93.3791 | 93.2497 | 5492:05 | 48:36 | 93.3791 | 93.2497
4 | Ron | 58 | 58 | 267:37 | 267:37 | 1001:07 | 1415:39 | 2416:46 | 2416:46 | 2684:23 | 46:17 | 94.2127 | 93.5719 | 2684:23 | 46:17 | 94.2127 | 93.5719
5 | Haveri | 204 | 204 | 2018:12 | 2018:12 | 3507:35 | 10752:39 | 14260:14 | 14260:14 | 16278:26 | 79:48 | 90.2912 | 88.9172 | 16278:26 | 79:48 | 90.2912 | 88.9172
6 | Ranebennur | 201 | 201 | 1632:38 | 1632:38 | 4527:49 | 10276:01 | 14803:50 | 14803:50 | 16436:28 | 81:46 | 89.7707 | 88.6426 | 16436:28 | 81:46 | 89.7707 | 88.6426
7 | Sirsi | 63 | 63 | 597:16 | 597:16 | 607:37 | 2438:26 | 3046:03 | 3046:03 | 3643:19 | 57:50 | 93.2847 | 91.968 | 3643:19 | 57:50 | 93.2847 | 91.968
8 | Dandeli | 25 | 25 | 4:58 | 4:58 | 372:16 | 634:46 | 1007:02 | 1007:02 | 1012:00 | 40:29 | 94.4054 | 94.3778 | 1012:00 | 40:29 | 94.4054 | 94.3778
9 | Karwar | 33 | 33 | 322:49 | 322:49 | 337:49 | 502:59 | 840:48 | 840:48 | 1163:37 | 35:16 | 96.4613 | 95.1026 | 1163:37 | 35:16 | 96.4613 | 95.1026
10 | Honnavar | 40 | 40 | 509:40 | 509:40 | 516:01 | 679:05 | 1195:06 | 1195:06 | 1704:46 | 42:37 | 95.8503 | 94.0807 | 1704:46 | 42:37 | 95.8503 | 94.0807
11 | Belagavi | 149 | 149 | 1452:49 | 1452:49 | 4010:57 | 6408:04 | 10419:01 | 10419:01 | 11871:50 | 79:41 | 90.288 | 88.9338 | 11871:50 | 79:41 | 90.288 | 88.9338
12 | Bailhongal | 193 | 193 | 2284:40 | 2284:40 | 3713:37 | 6009:09 | 9722:46 | 9722:46 | 12007:26 | 62:13 | 93.0032 | 91.3591 | 12007:26 | 62:13 | 93.0032 | 91.3591
13 | Ramdurg | 88 | 88 | 548:55 | 548:55 | 1615:46 | 2736:32 | 4352:18 | 4352:18 | 4901:13 | 55:42 | 93.1308 | 92.2645 | 4901:13 | 55:42 | 93.1308 | 92.2645
14 | Ghataprabha | 168 | 168 | 693:28 | 693:28 | 2117:17 | 5868:12 | 7985:29 | 7985:29 | 8678:57 | 51:40 | 93.3982 | 92.8249 | 8678:57 | 51:40 | 93.3982 | 92.8249
15 | Raibag | 175 | 175 | 850:55 | 850:55 | 6864:34 | 4709:21 | 11573:55 | 11573:55 | 12424:50 | 71:00 | 90.8144 | 90.139 | 12424:50 | 71:00 | 90.8144 | 90.139
16 | Athani | 200 | 200 | 1579:00 | 1579:00 | 4500:32 | 4934:10 | 9434:42 | 9434:42 | 11013:42 | 55:04 | 93.4481 | 92.3516 | 11013:42 | 55:04 | 93.4481 | 92.3516
17 | Chikkodi | 192 | 192 | 911:22 | 911:22 | 2351:18 | 4750:36 | 7101:54 | 7101:54 | 8013:16 | 41:44 | 94.8626 | 94.2034 | 8013:16 | 41:44 | 94.8626 | 94.2034
18 | Vijayapur | 183 | 183 | 985:20 | 985:20 | 2544:37 | 6169:46 | 8714:23 | 8714:23 | 9699:43 | 53:00 | 93.3862 | 92.6383 | 9699:43 | 53:00 | 93.3862 | 92.6383
19 | Indi | 259 | 259 | 1037:24 | 1037:24 | 3434:10 | 5591:36 | 9025:46 | 9025:46 | 10063:10 | 38:51 | 95.1599 | 94.6036 | 10063:10 | 38:51 | 95.1599 | 94.6036
20 | B.Bagewadi | 149 | 149 | 1169:20 | 1169:20 | 2784:18 | 4869:55 | 7654:13 | 7654:13 | 8823:33 | 59:13 | 92.8652 | 91.7752 | 8823:33 | 59:13 | 92.8652 | 91.7752
21 | Bagalkot | 198 | 198 | 895:07 | 895:07 | 2965:43 | 5235:53 | 8201:36 | 8201:36 | 9096:43 | 45:57 | 94.2469 | 93.619 | 9096:43 | 45:57 | 94.2469 | 93.619
22 | Jamkhandi | 213 | 213 | 1204:22 | 1204:22 | 4892:27 | 2941:48 | 7834:15 | 7834:15 | 9038:37 | 42:26 | 94.8916 | 94.1063 | 9038:37 | 42:26 | 94.8916 | 94.1063
23 | Mudhol | 195 | 195 | 551:07 | 551:07 | 2195:49 | 2773:52 | 4969:41 | 4969:41 | 5520:48 | 28:19 | 96.4421 | 96.0475 | 5520:48 | 28:19 | 96.4421 | 96.0475
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of May-2022 |  |  |  | Reliability for cumulative period from Apr-22 to May-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 243:11 | 630:21 | 1024:57 | 2397:15 | 3422:12 | 7333:03 | 3665:23 | 79:41 | 90.0006 | 89.29 | 7963:24 | 173:07 | 89.1111 | 88.175
2 | Dharwad Rural | 92 | 92 | 355:55 | 416:30 | 2402:39 | 5105:25 | 7508:04 | 17743:56 | 7863:59 | 85:29 | 89.031 | 88.511 | 18160:26 | 197:24 | 86.8259 | 86.5167
3 | Gadag | 113 | 113 | 317:30 | 422:50 | 3056:10 | 5964:36 | 9020:46 | 14407:31 | 9338:16 | 82:38 | 89.2702 | 88.8925 | 14830:21 | 131:15 | 91.291 | 91.0354
4 | Ron | 59 | 59 | 320:20 | 587:57 | 1366:23 | 1400:47 | 2767:10 | 5183:56 | 3087:30 | 52:20 | 93.6961 | 92.9663 | 5771:53 | 97:50 | 93.9984 | 93.3177
5 | Haveri | 205 | 205 | 2696:43 | 4714:55 | 5266:35 | 1045.9306 | 1265.3715 | 1859.5479 | 1377.7347 | 161:18 | 80.0886 | 78.3205 | 2056.0028 | 240:42 | 85.1296 | 83.5586
6 | Ranebennur | 204 | 204 | 1723:37 | 3356:15 | 6995:48 | 19182:42 | 1090.7708 | 1707.5972 | 1162.5882 | 136:47 | 82.7519 | 81.6163 | 1847.441 | 217:21 | 86.2777 | 85.154
7 | Sirsi | 63 | 63 | 396:53 | 994:09 | 798:36 | 3201:18 | 3999:54 | 7045:57 | 4396:47 | 69:47 | 91.4663 | 90.6196 | 8040:06 | 127:37 | 92.3606 | 91.2827
8 | Dandeli | 25 | 25 | 278:09 | 283:07 | 378:30 | 506:37 | 885:07 | 1892:09 | 1163:16 | 46:32 | 95.2413 | 93.7459 | 2175:16 | 87:01 | 94.8302 | 94.0566
9 | Karwar | 33 | 33 | 315:09 | 637:58 | 319:23 | 643:52 | 963:15 | 1804:03 | 1278:24 | 38:44 | 96.0767 | 94.7931 | 2442:01 | 74:00 | 96.2658 | 94.9453
10 | Honnavar | 40 | 40 | 747:15 | 1256:55 | 588:20 | 1202:16 | 1790:36 | 2985:42 | 2537:51 | 63:27 | 93.9832 | 91.4723 | 4242:37 | 106:04 | 94.9015 | 92.7551
11 | Belagavi | 149 | 149 | 730:59 | 2183:48 | 2930:46 | 4259:01 | 7189:47 | 17608:48 | 7920:46 | 53:10 | 93.5143 | 92.8549 | 19792:36 | 132:50 | 91.9276 | 90.9265
12 | Bailhongal | 193 | 193 | 1302:00 | 3586:40 | 3578:27 | 6516:39 | 10095:06 | 19817:52 | 11397:06 | 59:03 | 92.9696 | 92.0629 | 23404:32 | 121:16 | 92.9861 | 91.7167
13 | Ramdurg | 88 | 88 | 429:49 | 978:44 | 1949:13 | 3608:59 | 5558:12 | 9910:30 | 5988:01 | 68:03 | 91.5106 | 90.8541 | 10889:14 | 123:44 | 92.3074 | 91.5477
14 | Ghataprabha | 168 | 168 | 328:42 | 1022:10 | 1734:17 | 4386:09 | 6120:26 | 14105:55 | 6449:08 | 38:23 | 95.1033 | 94.8404 | 15128:05 | 90:03 | 94.2648 | 93.8492
15 | Raibag | 177 | 177 | 311:39 | 1162:34 | 7100:50 | 3902:28 | 11003:18 | 22577:13 | 11314:57 | 63:56 | 91.6444 | 91.4078 | 23739:47 | 134:07 | 91.2872 | 90.8386
16 | Athani | 201 | 201 | 990:57 | 2569:57 | 3646:11 | 5352:55 | 8999:06 | 18433:48 | 9990:03 | 49:42 | 93.9823 | 93.3197 | 21003:45 | 104:30 | 93.7356 | 92.8623
17 | Chikkodi | 192 | 192 | 627:15 | 1538:37 | 2053:57 | 2125:13 | 4179:10 | 11281:04 | 4806:25 | 25:02 | 97.0744 | 96.6353 | 12819:41 | 66:46 | 95.9866 | 95.4393
18 | Vijayapur | 189 | 189 | 958:18 | 1943:38 | 2392:04 | 5502:47 | 7894:51 | 16609:14 | 8853:09 | 46:51 | 94.3855 | 93.704 | 18552:52 | 98:10 | 93.9973 | 93.2949
19 | Indi | 259 | 259 | 1969:19 | 3006:43 | 4284:16 | 7124:07 | 11408:23 | 20434:09 | 13377:42 | 51:39 | 94.0796 | 93.0576 | 23440:52 | 90:30 | 94.6109 | 93.8179
20 | B.Bagewadi | 151 | 151 | 904:54 | 2074:14 | 2924:47 | 5807:05 | 8731:52 | 16386:05 | 9636:46 | 63:49 | 92.2276 | 91.4221 | 18460:19 | 122:15 | 92.5876 | 91.6493
21 | Bagalkot | 198 | 198 | 1023:00 | 1918:07 | 4031:57 | 9598:43 | 13630:40 | 21832:16 | 14653:40 | 74:01 | 90.7471 | 90.0526 | 23750:23 | 119:57 | 92.4683 | 91.8066
22 | Jamkhandi | 213 | 213 | 587:11 | 1791:33 | 4337:43 | 3596:22 | 7934:05 | 15768:20 | 8521:16 | 40:00 | 94.9934 | 94.6229 | 17559:53 | 82:26 | 94.9433 | 94.3688
23 | Mudhol | 196 | 196 | 450:04 | 1001:11 | 2452:47 | 4424:44 | 6877:31 | 11847:12 | 7327:35 | 37:23 | 95.2837 | 94.975 | 12848:23 | 65:33 | 95.8713 | 95.5223
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of June-2022 |  |  |  | Reliability for cumulative period from Apr-22 to June-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 215:40 | 846:01 | 1067:42 | 1964:24 | 3032:06 | 10365:09 | 3247:46 | 70:36 | 90.8451 | 90.1939 | 11211:10 | 243:43 | 89.6827 | 88.8406
2 | Dharwad Rural | 92 | 92 | 140:50 | 557:20 | 1893:46 | 3557:03 | 5450:49 | 23194:45 | 5591:39 | 60:47 | 91.7711 | 91.5585 | 23752:05 | 258:10 | 88.4562 | 88.1788
3 | Gadag | 113 | 113 | 285:25 | 708:15 | 2002:07 | 3859:03 | 5861:10 | 20268:41 | 6146:35 | 54:24 | 92.796 | 92.4452 | 20976:56 | 185:38 | 91.7871 | 91.5002
4 | Ron | 59 | 59 | 204:30 | 792:27 | 913:00 | 1155:21 | 2068:21 | 7252:17 | 2272:51 | 38:31 | 95.131 | 94.6496 | 8044:44 | 136:21 | 94.3718 | 93.7568
5 | Haveri | 205 | 205 | 1588:16 | 6303:11 | 3959:53 | 11715:43 | 15675:36 | 2512.6979 | 17263:52 | 84:13 | 89.3797 | 88.3036 | 2775.3306 | 324:55 | 86.5307 | 85.1229
6 | Ranebennur | 205 | 205 | 1155:23 | 4511:38 | 4829:42 | 8863:58 | 13693:40 | 2278.1667 | 14849:03 | 72:26 | 90.7224 | 89.9397 | 2466.1514 | 288:43 | 87.7879 | 86.7802
7 | Sirsi | 62 | 62 | 585:04 | 1579:13 | 754:47 | 2147:46 | 2902:33 | 9948:30 | 3487:37 | 56:15 | 93.4979 | 92.1872 | 11527:43 | 185:56 | 92.6529 | 91.4867
8 | Dandeli | 25 | 25 | 82:04 | 365:11 | 280:46 | 371:50 | 652:36 | 2544:45 | 734:40 | 29:23 | 96.3744 | 95.9185 | 2909:56 | 116:24 | 95.3393 | 94.6705
9 | Karwar | 29 | 29 | 369:00 | 1006:58 | 419:31 | 761:41 | 1181:12 | 2985:15 | 1550:12 | 53:27 | 94.3429 | 92.5757 | 3992:13 | 137:40 | 95.2866 | 93.6968
10 | Honnavar | 40 | 40 | 632:18 | 1889:13 | 654:36 | 1334:40 | 1989:16 | 4974:58 | 2621:34 | 65:32 | 93.0928 | 90.8973 | 6864:11 | 171:36 | 94.3052 | 92.1426
11 | Belagavi | 149 | 149 | 461:47 | 2645:35 | 2546:37 | 3018:00 | 5564:37 | 23173:25 | 6026:24 | 40:27 | 94.813 | 94.3826 | 1075.7917 | 173:17 | 92.8788 | 92.0658
12 | Bailhongal | 193 | 193 | 1597:58 | 5184:38 | 3270:41 | 5162:26 | 8433:07 | 1177.1243 | 10031:05 | 51:58 | 93.9313 | 92.7813 | 1393.1507 | 173:14 | 93.2977 | 92.0677
13 | Ramdurg | 88 | 88 | 544:17 | 1523:01 | 1680:45 | 3116:36 | 4797:21 | 14707:51 | 5341:38 | 60:42 | 92.4284 | 91.5694 | 16230:52 | 184:26 | 92.3473 | 91.5549
14 | Ghataprabha | 170 | 170 | 532:08 | 1554:18 | 1602:54 | 2084:42 | 3687:36 | 17793:31 | 4219:44 | 24:49 | 96.9873 | 96.5525 | 19347:49 | 113:49 | 95.2075 | 94.7889
15 | Raibag | 178 | 178 | 511:06 | 1673:40 | 5793:30 | 1578:02 | 7371:32 | 1247.8646 | 7882:38 | 44:17 | 94.2482 | 93.8494 | 1317.6007 | 177:39 | 92.2962 | 91.8657
16 | Athani | 201 | 201 | 661:13 | 3231:10 | 3803:32 | 2032:14 | 5835:46 | 1011.2319 | 6496:59 | 32:19 | 95.9675 | 95.5107 | 1145.8639 | 136:49 | 94.4714 | 93.7354
17 | Chikkodi | 191 | 191 | 443:39 | 1982:16 | 1675:17 | 1929:33 | 3604:50 | 14885:54 | 4048:29 | 21:12 | 97.3787 | 97.0561 | 16868:10 | 88:19 | 96.4315 | 95.9563
18 | Vijayapur | 190 | 190 | 745:36 | 2689:14 | 2232:24 | 4392:19 | 6624:43 | 23233:57 | 7370:19 | 38:47 | 95.1574 | 94.6123 | 1080.1326 | 136:26 | 94.4009 | 93.7528
19 | Indi | 261 | 261 | 1756:20 | 4763:03 | 4043:47 | 9661:58 | 13705:45 | 1422.4958 | 15462:05 | 59:15 | 92.7066 | 91.772 | 1620.9562 | 149:03 | 94.0108 | 93.1752
20 | B.Bagewadi | 151 | 151 | 423:46 | 2498:00 | 3160:56 | 4895:05 | 8056:01 | 1018.4208 | 8479:47 | 56:09 | 92.5901 | 92.2003 | 1122.5042 | 178:25 | 92.5885 | 91.831
21 | Bagalkot | 198 | 198 | 1050:23 | 2968:30 | 3761:31 | 6714:09 | 10475:40 | 1346.1639 | 11526:03 | 58:13 | 92.6517 | 91.9149 | 1469.8514 | 178:10 | 92.5288 | 91.8423
22 | Jamkhandi | 213 | 213 | 969:31 | 2761:04 | 3281:08 | 1822:39 | 5103:47 | 20872:07 | 6073:18 | 28:31 | 96.672 | 96.0398 | 23633:11 | 110:57 | 95.5132 | 94.9197
23 | Mudhol | 196 | 196 | 477:05 | 1478:16 | 2772:33 | 3771:11 | 6543:44 | 18390:56 | 7020:49 | 35:49 | 95.363 | 95.0249 | 19869:12 | 101:22 | 95.7037 | 95.3584
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]