## DHQ
Annex-1 | [13 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of April-2019
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Apr-19 |  |  |  | Reliability for cumulative period from Apr-19
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 10:15 | 10:15 | 480:03 | 217:29 | 697:32 | 697:32 | 707:47 | 22:50 | 96.8749 | 96.8289 | 707:47 | 22:50 | 96.8749 | 96.8289
2 | Gadag | 15 | 15 | 0:00 | 0:00 | 64:25 | 71:25 | 135:50 | 135:50 | 135:50 | 9:03 | 98.7423 | 98.7423 | 135:50 | 9:03 | 98.7423 | 98.7423
3 | Haveri | 5 | 5 | 0:00 | 0:00 | 13:35 | 13:25 | 27:00 | 27:00 | 27:00 | 5:24 | 99.25 | 99.25 | 27:00 | 5:24 | 99.25 | 99.25
4 | Karwar | 10 | 10 | 17:50 | 17:50 | 36:23 | 14:52 | 51:15 | 51:15 | 69:05 | 6:55 | 99.2882 | 99.0405 | 69:05 | 6:55 | 99.2882 | 99.0405
5 | Belagavi | 64 | 64 | 88:51 | 88:51 | 256:55 | 176:02 | 432:57 | 432:57 | 521:48 | 8:09 | 99.0604 | 98.8676 | 521:48 | 8:09 | 99.0604 | 98.8676
6 | Vijayapur | 30 | 30 | 19:53 | 19:53 | 129:32 | 157:55 | 287:27 | 287:27 | 307:20 | 10:15 | 98.6692 | 98.5772 | 307:20 | 10:15 | 98.6692 | 98.5772
7 | Bagalkot | 11 | 11 | 1:40 | 1:40 | 36:42 | 56:06 | 92:48 | 92:48 | 94:28 | 8:35 | 98.8283 | 98.8072 | 94:28 | 8:35 | 98.8283 | 98.8072
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of May-2019
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-19 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 8:59 | 19:14 | 631:07 | 131:04 | 762:11 | 1459:43 | 771:10 | 24:53 | 96.6954 | 96.6564 | 1478:57 | 47:42 | 96.7836 | 96.7413
2 | Gadag | 15 | 15 | 0:00 | 0:00 | 96:13 | 64:05 | 160:18 | 296:08 | 160:18 | 10:41 | 98.5636 | 98.5636 | 296:08 | 19:45 | 98.6515 | 98.6515
3 | Haveri | 5 | 5 | 2:43 | 2:43 | 23:56 | 10:30 | 34:26 | 61:26 | 37:09 | 7:26 | 99.0744 | 99.0013 | 64:09 | 12:50 | 99.1607 | 99.1236
4 | Karwar | 10 | 10 | 138:10 | 156:00 | 93:51 | 79:20 | 173:11 | 224:26 | 311:21 | 31:08 | 97.6723 | 95.8152 | 380:26 | 38:03 | 98.467 | 97.4014
5 | Belagavi | 64 | 64 | 237:02 | 325:53 | 347:34 | 94:51 | 442:25 | 875:22 | 679:27 | 10:37 | 99.0709 | 98.5731 | 1201:15 | 18:46 | 99.0657 | 98.7179
6 | Vijayapur | 30 | 30 | 53:20 | 73:13 | 186:25 | 270:14 | 456:39 | 744:06 | 509:59 | 17:00 | 97.9541 | 97.7151 | 817:19 | 27:15 | 98.3058 | 98.1391
7 | Bagalkot | 11 | 11 | 79:00 | 80:40 | 121:27 | 163:29 | 284:56 | 377:44 | 363:56 | 33:05 | 96.5184 | 95.5531 | 458:24 | 41:40 | 97.6544 | 97.1535
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of June-2019
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-19 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 31:07 | 50:21 | 712:42 | 247:59 | 960:41 | 2420:24 | 991:48 | 32:00 | 95.6959 | 95.5565 | 2470:45 | 79:42 | 96.425 | 96.3507
2 | Gadag | 15 | 15 | 17:10 | 17:10 | 101:15 | 67:12 | 168:27 | 464:35 | 185:37 | 12:22 | 98.4403 | 98.2813 | 481:45 | 32:07 | 98.5819 | 98.5295
3 | Haveri | 5 | 5 | 0:00 | 2:43 | 50:10 | 26:35 | 76:45 | 138:11 | 76:45 | 15:21 | 97.8681 | 97.8681 | 140:54 | 28:11 | 98.7346 | 98.7097
4 | Karwar | 10 | 10 | 225:30 | 381:30 | 186:05 | 234:00 | 420:05 | 644:31 | 645:35 | 64:34 | 94.1655 | 91.0336 | 1026:01 | 102:36 | 97.0489 | 95.3021
5 | Belagavi | 64 | 64 | 49:54 | 375:47 | 469:58 | 196:39 | 666:37 | 1541:59 | 716:31 | 11:12 | 98.5533 | 98.4451 | 1917:46 | 29:58 | 98.8968 | 98.628
6 | Vijayapur | 30 | 30 | 0:00 | 73:13 | 209:38 | 392:28 | 602:06 | 1346:12 | 602:06 | 20:04 | 97.2125 | 97.2125 | 1419:25 | 47:19 | 97.9454 | 97.8336
7 | Bagalkot | 11 | 11 | 1:20 | 82:00 | 125:21 | 136:57 | 262:18 | 640:02 | 263:38 | 23:58 | 96.6881 | 96.6713 | 722:02 | 65:38 | 97.3359 | 96.9945
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of July-2019
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-19 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 12:00 | 62:21 | 672:37 | 226:46 | 899:23 | 3319:47 | 911:23 | 29:24 | 96.1005 | 96.0485 | 3382:08 | 109:06 | 96.3426 | 96.2739
2 | Gadag | 15 | 15 | 73:02 | 90:12 | 132:22 | 38:20 | 170:42 | 635:17 | 243:44 | 16:15 | 98.4704 | 97.816 | 725:29 | 48:22 | 98.5535 | 98.3482
3 | Haveri | 5 | 5 | 0:00 | 2:43 | 75:30 | 16:05 | 91:35 | 229:46 | 91:35 | 18:19 | 97.5381 | 97.5381 | 232:29 | 46:30 | 98.4306 | 98.412
4 | Karwar | 10 | 10 | 86:30 | 468:00 | 145:35 | 132:50 | 278:25 | 922:56 | 364:55 | 36:30 | 96.2578 | 95.0952 | 1390:56 | 139:06 | 96.8479 | 95.2495
5 | Belagavi | 64 | 64 | 21:31 | 397:18 | 173:18 | 164:35 | 337:53 | 1879:52 | 359:24 | 5:37 | 99.2904 | 99.2452 | 2277:10 | 35:35 | 98.9968 | 98.7848
6 | Vijayapur | 34 | 34 | 183:59 | 257:12 | 351:24 | 284:17 | 635:41 | 1981:53 | 819:40 | 24:06 | 97.487 | 96.7597 | 2239:05 | 65:51 | 98.0092 | 97.7508
7 | Bagalkot | 11 | 11 | 0:00 | 82:00 | 94:24 | 59:57 | 154:21 | 794:23 | 154:21 | 14:02 | 98.114 | 98.114 | 876:23 | 79:40 | 97.5336 | 97.279
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of August-2019
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of August-19 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 20:52 | 83:13 | 870:14 | 409:13 | 1279:27 | 4599:14 | 1300:19 | 41:57 | 94.4526 | 94.3621 | 4682:27 | 151:03 | 95.9596 | 95.8865
2 | Gadag | 15 | 15 | 73:02 | 163:14 | 127:23 | 36:00 | 163:23 | 798:40 | 236:25 | 15:46 | 98.536 | 97.8816 | 961:54 | 64:08 | 98.55 | 98.2536
3 | Haveri | 5 | 5 | 6:40 | 9:23 | 38:30 | 20:55 | 59:25 | 289:11 | 66:05 | 13:13 | 98.4028 | 98.2236 | 298:34 | 59:43 | 98.4249 | 98.3738
4 | Karwar | 10 | 10 | 32:40 | 500:40 | 185:50 | 148:20 | 334:10 | 1257:06 | 366:50 | 36:41 | 95.5085 | 95.0694 | 1757:46 | 175:47 | 96.5765 | 95.2131
5 | Belagavi | 65 | 65 | 928:14 | 1325:32 | 2397:10 | 236:49 | 2633:59 | 4513:51 | 3562:13 | 54:48 | 94.5534 | 92.634 | 5839:23 | 89:50 | 98.1088 | 97.5535
6 | Vijayapur | 34 | 34 | 13:36 | 270:48 | 603:20 | 186:11 | 789:31 | 2771:24 | 803:07 | 23:37 | 96.8789 | 96.8251 | 3042:12 | 89:29 | 97.7802 | 97.5633
7 | Bagalkot | 11 | 11 | 0:00 | 82:00 | 34:20 | 99:51 | 134:11 | 928:34 | 134:11 | 12:12 | 98.3604 | 98.3604 | 1010:34 | 91:52 | 97.7011 | 97.4981
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of September-2019
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of September-19 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 10:35 | 93:48 | 608:55 | 282:29 | 891:24 | 5490:38 | 901:59 | 29:06 | 96.0063 | 95.9589 | 5584:26 | 180:09 | 95.9673 | 95.8984
2 | Gadag | 15 | 15 | 59:50 | 223:04 | 56:20 | 39:06 | 95:26 | 894:06 | 155:16 | 10:21 | 99.1164 | 98.5623 | 1117:10 | 74:29 | 98.6428 | 98.3042
3 | Haveri | 5 | 5 | 0:00 | 9:23 | 50:00 | 10:05 | 60:05 | 349:16 | 60:05 | 12:01 | 98.331 | 98.331 | 358:39 | 71:44 | 98.4095 | 98.3668
4 | Karwar | 10 | 10 | 7:00 | 507:40 | 58:10 | 98:00 | 156:10 | 1413:16 | 163:10 | 16:19 | 97.831 | 97.7338 | 1920:56 | 192:06 | 96.7822 | 95.6263
5 | Belagavi | 64 | 64 | 171:44 | 1497:16 | 823:46 | 159:58 | 983:44 | 5497:35 | 1155:28 | 18:03 | 97.8652 | 97.4925 | 6994:51 | 109:18 | 98.0442 | 97.5115
6 | Vijayapur | 34 | 34 | 9:52 | 280:40 | 648:05 | 202:51 | 850:56 | 3622:20 | 860:48 | 25:19 | 96.524 | 96.4837 | 3903:00 | 114:48 | 97.5742 | 97.3863
7 | Bagalkot | 11 | 11 | 4:38 | 86:38 | 59:24 | 87:31 | 146:55 | 1075:29 | 151:33 | 13:47 | 98.145 | 98.0865 | 1162:07 | 105:39 | 97.7739 | 97.5946
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of October-2019
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of October-19 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 16:31 | 110:19 | 558:17 | 272:30 | 830:47 | 6321:25 | 847:18 | 27:20 | 96.3979 | 96.3263 | 6431:44 | 207:29 | 96.0297 | 95.9604
2 | Gadag | 15 | 15 | 15:00 | 238:04 | 65:02 | 41:03 | 106:05 | 1000:11 | 121:05 | 8:04 | 99.0494 | 98.915 | 1238:15 | 82:33 | 98.7017 | 98.3927
3 | Haveri | 5 | 5 | 0:00 | 9:23 | 24:40 | 48:55 | 73:35 | 422:51 | 73:35 | 14:43 | 98.022 | 98.022 | 432:14 | 86:27 | 98.3534 | 98.3168
4 | Karwar | 10 | 10 | 23:40 | 531:20 | 232:36 | 246:05 | 478:41 | 1891:57 | 502:21 | 50:14 | 93.5661 | 93.248 | 2423:17 | 242:20 | 96.3163 | 95.2818
5 | Belagavi | 64 | 64 | 158:45 | 1656:01 | 387:19 | 181:39 | 568:58 | 6066:33 | 727:43 | 11:22 | 98.8051 | 98.4717 | 7722:34 | 120:40 | 98.1544 | 97.6506
6 | Vijayapur | 34 | 34 | 213:45 | 494:25 | 1210:36 | 429:57 | 1640:33 | 5262:53 | 1854:18 | 54:32 | 93.5146 | 92.6696 | 5757:18 | 169:20 | 96.9862 | 96.703
7 | Bagalkot | 11 | 11 | 0:00 | 86:38 | 73:07 | 53:38 | 126:45 | 1202:14 | 126:45 | 11:31 | 98.4512 | 98.4512 | 1288:52 | 117:10 | 97.872 | 97.7187
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of November-2019
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of November-19 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 4:50 | 115:09 | 460:46 | 102:31 | 563:17 | 6884:42 | 568:07 | 18:20 | 97.4763 | 97.4547 | 6999:51 | 225:48 | 96.2075 | 96.1441
2 | Gadag | 15 | 15 | 13:30 | 251:34 | 62:44 | 41:58 | 104:42 | 1104:53 | 118:12 | 7:53 | 99.0306 | 98.9056 | 1356:27 | 90:26 | 98.7422 | 98.4558
3 | Haveri | 6 | 6 | 0:00 | 9:23 | 38:27 | 7:12 | 45:39 | 468:30 | 45:39 | 7:37 | 98.9433 | 98.9433 | 477:53 | 79:39 | 98.6666 | 98.6399
4 | Karwar | 10 | 10 | 28:30 | 559:50 | 100:45 | 54:35 | 155:20 | 2047:17 | 183:50 | 18:23 | 97.8426 | 97.4468 | 2607:07 | 260:43 | 96.504 | 95.548
5 | Belagavi | 64 | 64 | 124:57 | 1780:58 | 291:06 | 70:37 | 361:43 | 6428:16 | 486:40 | 7:36 | 99.215 | 98.9439 | 8209:14 | 128:16 | 98.2848 | 97.8096
6 | Vijayapur | 35 | 35 | 164:39 | 659:04 | 482:13 | 184:04 | 666:17 | 5929:10 | 830:56 | 23:44 | 97.356 | 96.7026 | 6588:14 | 188:14 | 97.1072 | 96.7856
7 | Bagalkot | 11 | 11 | 0:40 | 87:18 | 49:04 | 19:40 | 68:44 | 1270:58 | 69:24 | 6:19 | 99.1322 | 99.1237 | 1358:16 | 123:29 | 98.0269 | 97.8914
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of December-2019
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of December-19 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 4:35 | 119:44 | 616:13 | 75:24 | 691:37 | 7576:19 | 696:12 | 22:27 | 97.0013 | 96.9814 | 7696:03 | 248:16 | 96.297 | 96.2385
2 | Gadag | 15 | 15 | 13:30 | 265:04 | 73:04 | 40:00 | 113:04 | 1217:57 | 126:34 | 8:26 | 98.9869 | 98.8659 | 1483:01 | 98:52 | 98.7697 | 98.502
3 | Haveri | 6 | 6 | 0:00 | 9:23 | 10:23 | 12:39 | 23:02 | 491:32 | 23:02 | 3:50 | 99.484 | 99.484 | 500:55 | 83:29 | 98.7588 | 98.7351
4 | Karwar | 10 | 10 | 21:30 | 581:20 | 89:40 | 52:45 | 142:25 | 2189:42 | 163:55 | 16:24 | 98.0858 | 97.7968 | 2771:02 | 277:06 | 96.6823 | 95.8015
5 | Belagavi | 64 | 64 | 466:08 | 2247:06 | 489:29 | 81:29 | 570:58 | 6999:14 | 1037:06 | 16:12 | 98.8009 | 97.822 | 9246:20 | 144:28 | 98.343 | 97.811
6 | Vijayapur | 35 | 35 | 351:28 | 1010:32 | 321:05 | 194:10 | 515:15 | 6444:25 | 866:43 | 24:46 | 98.0213 | 96.6716 | 7454:57 | 213:00 | 97.2102 | 96.7727
7 | Bagalkot | 11 | 11 | 0:00 | 87:18 | 73:24 | 14:15 | 87:39 | 1358:37 | 87:39 | 7:58 | 98.929 | 98.929 | 1445:55 | 131:27 | 98.1286 | 98.0084
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of January-2020
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of January-2020 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 5:40 | 125:24 | 504:58 | 96:23 | 601:21 | 8177:40 | 607:01 | 19:35 | 97.3927 | 97.3681 | 8303:04 | 267:50 | 96.408 | 96.3529
2 | Gadag | 16 | 16 | 0:00 | 265:04 | 82:11 | 40:08 | 122:19 | 1340:16 | 122:19 | 7:39 | 98.9725 | 98.9725 | 1605:20 | 100:20 | 98.8594 | 98.6338
3 | Haveri | 6 | 6 | 0:00 | 9:23 | 39:40 | 12:22 | 52:02 | 543:34 | 52:02 | 8:40 | 98.8344 | 98.8344 | 552:57 | 92:09 | 98.7664 | 98.7451
4 | Karwar | 10 | 10 | 40:10 | 621:30 | 50:15 | 39:25 | 89:40 | 2279:22 | 129:50 | 12:59 | 98.7948 | 98.2549 | 2900:52 | 290:05 | 96.8963 | 96.05
5 | Belagavi | 64 | 64 | 147:50 | 2394:56 | 682:54 | 74:55 | 757:49 | 7757:03 | 905:39 | 14:09 | 98.4085 | 98.098 | 10151:59 | 158:37 | 98.3496 | 97.8401
6 | Vijayapur | 35 | 35 | 324:43 | 1335:15 | 319:45 | 194:10 | 513:55 | 6958:20 | 838:38 | 23:58 | 98.0264 | 96.7794 | 8293:35 | 236:58 | 97.2929 | 96.7734
7 | Bagalkot | 11 | 11 | 0:00 | 87:18 | 30:32 | 27:31 | 58:03 | 1416:40 | 58:03 | 5:17 | 99.2907 | 99.2907 | 1503:58 | 136:43 | 98.2464 | 98.1383
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of February-2020
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of February-2020 |  |  |  | Reliability for cumulative period from Apr-19 to Feb-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 8:25 | 133:49 | 565:47 | 58:07 | 623:54 | 8801:34 | 632:19 | 20:24 | 97.1084 | 97.0694 | 8935:23 | 288:14 | 96.4686 | 96.4149
2 | Gadag | 16 | 16 | 0:00 | 265:04 | 86:47 | 116:14 | 203:01 | 1543:17 | 203:01 | 12:41 | 98.1769 | 98.1769 | 1808:21 | 113:01 | 98.8003 | 98.5943
3 | Haveri | 6 | 6 | 0:00 | 9:23 | 39:40 | 12:22 | 52:02 | 595:36 | 52:02 | 8:40 | 98.754 | 98.754 | 604:59 | 100:50 | 98.7653 | 98.7459
4 | Karwar | 10 | 10 | 48:40 | 670:10 | 79:00 | 27:35 | 106:35 | 2385:57 | 155:15 | 15:32 | 98.4686 | 97.7694 | 3056:07 | 305:37 | 97.0324 | 96.1989
5 | Belagavi | 66 | 66 | 124:18 | 2519:14 | 751:38 | 66:13 | 817:51 | 8574:54 | 942:09 | 14:16 | 98.2196 | 97.949 | 11094:08 | 168:06 | 98.384 | 97.9093
6 | Vijayapur | 35 | 35 | 22:25 | 1357:40 | 124:54 | 50:37 | 175:31 | 7133:51 | 197:56 | 5:39 | 99.2795 | 99.1875 | 8491:31 | 242:37 | 97.4649 | 96.9824
7 | Bagalkot | 11 | 11 | 0:00 | 87:18 | 30:32 | 27:31 | 58:03 | 1474:43 | 58:03 | 5:17 | 99.2418 | 99.2418 | 1562:01 | 142:00 | 98.3325 | 98.2338
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of March-2020
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of March-2020 |  |  |  | Reliability for cumulative period from Apr-19 to Mar-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 31 | 31 | 8:10 | 141:59 | 496:43 | 120:12 | 616:55 | 9418:29 | 625:05 | 20:10 | 97.3252 | 97.2898 | 9560:28 | 308:24 | 96.5412 | 96.489
2 | Gadag | 16 | 16 | 0:00 | 265:04 | 51:15 | 26:27 | 77:42 | 1620:59 | 77:42 | 4:51 | 99.3473 | 99.3473 | 1886:03 | 117:53 | 98.8466 | 98.658
3 | Haveri | 6 | 6 | 0:00 | 9:23 | 9:35 | 4:45 | 14:20 | 609:56 | 14:20 | 2:23 | 99.6789 | 99.6789 | 619:19 | 103:13 | 98.8427 | 98.8249
4 | Karwar | 10 | 10 | 8:12 | 678:22 | 98:22 | 41:30 | 139:52 | 2525:49 | 148:04 | 14:48 | 98.1201 | 98.0099 | 3204:11 | 320:25 | 97.1245 | 96.3523
5 | Belagavi | 66 | 66 | 14:05 | 2533:19 | 477:45 | 149:49 | 627:34 | 9202:28 | 641:39 | 9:43 | 98.722 | 98.6933 | 11735:47 | 177:49 | 98.4127 | 97.9757
6 | Vijayapur | 35 | 35 | 3:00 | 1360:40 | 123:02 | 111:12 | 234:14 | 7368:05 | 237:14 | 6:47 | 99.1005 | 99.089 | 8728:45 | 249:24 | 97.6034 | 97.1608
7 | Bagalkot | 11 | 11 | 17:17 | 104:35 | 106:38 | 30:13 | 136:51 | 1611:34 | 154:08 | 14:01 | 98.3278 | 98.1167 | 1716:09 | 156:01 | 98.3321 | 98.2239
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]

## URBAN
Annex-II | [13 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of April-2019
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2019 |  |  |  | Reliability for cumulative period from Apr-19
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 78 | 78 | 99:49 | 99:49 | 228:10 | 434:08 | 662:18 | 662:18 | 762:07 | 9:46 | 98.8207 | 98.643 | 762:07 | 9:46 | 98.8207 | 98.643
2 | Dharwad(R) | 18 | 18 | 19:50 | 19:50 | 201:23 | 292:33 | 493:56 | 493:56 | 513:46 | 28:33 | 96.1888 | 96.0358 | 513:46 | 28:33 | 96.1888 | 96.0358
3 | Kundagol | 1 | 1 | 38:25 | 38:25 | 21:20 | 3:30 | 24:50 | 24:50 | 63:15 | 63:15 | 96.5509 | 91.2153 | 63:15 | 63:15 | 96.5509 | 91.2153
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 7:03 | 15:32 | 22:35 | 22:35 | 22:35 | 22:35 | 96.8634 | 96.8634 | 22:35 | 22:35 | 96.8634 | 96.8634
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 20:32 | 10:48 | 31:20 | 31:20 | 31:20 | 31:20 | 95.6481 | 95.6481 | 31:20 | 31:20 | 95.6481 | 95.6481
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 14:55 | 82:45 | 97:40 | 97:40 | 97:40 | 48:50 | 93.2176 | 93.2176 | 97:40 | 48:50 | 93.2176 | 93.2176
7 | Alnavar | 1 | 1 | 19:50 | 19:50 | 7:10 | 2:05 | 9:15 | 9:15 | 29:05 | 29:05 | 98.7153 | 95.9606 | 29:05 | 29:05 | 98.7153 | 95.9606
8 | Naragund | 2 | 2 | 15:30 | 15:30 | 29:05 | 72:25 | 101:30 | 101:30 | 117:00 | 58:30 | 92.9514 | 91.875 | 117:00 | 58:30 | 92.9514 | 91.875
9 | Shirahatti | 1 | 1 | 0:00 | 0:00 | 8:15 | 2:30 | 10:45 | 10:45 | 10:45 | 10:45 | 98.5069 | 98.5069 | 10:45 | 10:45 | 98.5069 | 98.5069
10 | Laxmeshwar | 6 | 6 | 0:00 | 0:00 | 89:37 | 78:16 | 167:53 | 167:53 | 167:53 | 27:59 | 96.1138 | 96.1138 | 167:53 | 27:59 | 96.1138 | 96.1138
11 | Naregal | 1 | 1 | 0:00 | 0:00 | 6:00 | 6:40 | 12:40 | 12:40 | 12:40 | 12:40 | 98.2407 | 98.2407 | 12:40 | 12:40 | 98.2407 | 98.2407
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 28:40 | 9:50 | 38:30 | 38:30 | 38:30 | 19:15 | 97.3264 | 97.3264 | 38:30 | 19:15 | 97.3264 | 97.3264
13 | Ron | 2 | 2 | 0:00 | 0:00 | 15:05 | 10:46 | 25:51 | 25:51 | 25:51 | 12:56 | 98.2049 | 98.2049 | 25:51 | 12:56 | 98.2049 | 98.2049
14 | Mundaragi | 3 | 3 | 1:45 | 1:45 | 37:15 | 31:25 | 68:40 | 68:40 | 70:25 | 23:28 | 96.821 | 96.74 | 70:25 | 23:28 | 96.821 | 96.74
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 21:23 | 27:18 | 48:41 | 48:41 | 48:41 | 48:41 | 93.2384 | 93.2384 | 48:41 | 48:41 | 93.2384 | 93.2384
16 | G.C.T.M | 1 | 1 | 18:20 | 18:20 | 19:25 | 23:35 | 43:00 | 43:00 | 61:20 | 61:20 | 94.0278 | 91.4815 | 61:20 | 61:20 | 94.0278 | 91.4815
17 | F.C.S.M | 2 | 2 | 34:30 | 34:30 | 10:25 | 37:35 | 48:00 | 48:00 | 82:30 | 41:15 | 96.6667 | 94.2708 | 82:30 | 41:15 | 96.6667 | 94.2708
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 11:08 | 9:10 | 20:18 | 20:18 | 20:18 | 20:18 | 97.1806 | 97.1806 | 20:18 | 20:18 | 97.1806 | 97.1806
19 | Hole-Alur | 1 | 1 | 14:40 | 14:40 | 14:55 | 9:30 | 24:25 | 24:25 | 39:05 | 39:05 | 96.6088 | 94.5718 | 39:05 | 39:05 | 96.6088 | 94.5718
20 | Savanur | 2 | 2 | 1:10 | 1:10 | 26:20 | 11:35 | 37:55 | 37:55 | 39:05 | 19:32 | 97.3669 | 97.2859 | 39:05 | 19:32 | 97.3669 | 97.2859
21 | Shiggaon | 2 | 2 | 16:00 | 16:00 | 23:30 | 11:20 | 34:50 | 34:50 | 50:50 | 25:25 | 97.581 | 96.4699 | 50:50 | 25:25 | 97.581 | 96.4699
22 | Bankapur | 1 | 1 | 7:45 | 7:45 | 3:15 | 6:20 | 9:35 | 9:35 | 17:20 | 17:20 | 98.669 | 97.5926 | 17:20 | 17:20 | 98.669 | 97.5926
23 | Hangal | 2 | 2 | 1:10 | 1:10 | 50:05 | 39:10 | 89:15 | 89:15 | 90:25 | 45:12 | 93.8021 | 93.7211 | 90:25 | 45:12 | 93.8021 | 93.7211
24 | Ranebennur | 16 | 16 | 10:26 | 10:26 | 115:13 | 61:24 | 176:37 | 176:37 | 187:03 | 11:41 | 98.4669 | 98.3763 | 187:03 | 11:41 | 98.4669 | 98.3763
25 | Halageri | 2 | 2 | 38:40 | 38:40 | 17:05 | 1:15 | 18:20 | 18:20 | 57:00 | 28:30 | 98.7269 | 96.0417 | 57:00 | 28:30 | 98.7269 | 96.0417
26 | Tuminakatti | 3 | 3 | 3:00 | 3:00 | 55:20 | 0:15 | 55:35 | 55:35 | 58:35 | 19:32 | 97.4267 | 97.2878 | 58:35 | 19:32 | 97.4267 | 97.2878
27 | Kahanderayanahalli | 2 | 2 | 21:45 | 21:45 | 65:39 | 37:55 | 103:34 | 103:34 | 125:19 | 62:39 | 92.8079 | 91.2975 | 125:19 | 62:39 | 92.8079 | 91.2975
28 | Rattihalli | 1 | 1 | 1:00 | 1:00 | 15:25 | 3:50 | 19:15 | 19:15 | 20:15 | 20:15 | 97.3264 | 97.1875 | 20:15 | 20:15 | 97.3264 | 97.1875
29 | Hirekerur | 3 | 3 | 41:45 | 41:45 | 55:30 | 29:50 | 85:20 | 85:20 | 127:05 | 42:22 | 96.0494 | 94.1165 | 127:05 | 42:22 | 96.0494 | 94.1165
30 | Byadagi | 6 | 6 | 19:40 | 19:40 | 46:25 | 53:20 | 99:45 | 99:45 | 119:25 | 19:54 | 97.691 | 97.2357 | 119:25 | 19:54 | 97.691 | 97.2357
31 | Sirsi | 3 | 3 | 25:53 | 25:53 | 6:15 | 2:05 | 8:20 | 8:20 | 34:13 | 11:24 | 99.6142 | 98.4159 | 34:13 | 11:24 | 99.6142 | 98.4159
32 | Yellapur | 3 | 3 | 19:50 | 19:50 | 87:20 | 49:30 | 136:50 | 136:50 | 156:40 | 52:13 | 93.6651 | 92.7469 | 156:40 | 52:13 | 93.6651 | 92.7469
33 | Mundagod | 3 | 3 | 9:55 | 9:55 | 22:05 | 6:55 | 29:00 | 29:00 | 38:55 | 12:58 | 98.6574 | 98.1983 | 38:55 | 12:58 | 98.6574 | 98.1983
34 | Siddapur | 2 | 2 | 0:00 | 0:00 | 19:55 | 13:25 | 33:20 | 33:20 | 33:20 | 16:40 | 97.6852 | 97.6852 | 33:20 | 16:40 | 97.6852 | 97.6852
35 | Dandeli | 8 | 8 | 13:08 | 13:08 | 68:57 | 106:56 | 175:53 | 175:53 | 189:01 | 23:38 | 96.9465 | 96.7185 | 189:01 | 23:38 | 96.9465 | 96.7185
36 | Haliyal | 3 | 3 | 6:04 | 6:04 | 40:32 | 17:52 | 58:24 | 58:24 | 64:28 | 21:29 | 97.2963 | 97.0154 | 64:28 | 21:29 | 97.2963 | 97.0154
37 | Ankola | 3 | 3 | 31:12 | 31:12 | 0:38 | 0:18 | 0:56 | 0:56 | 32:08 | 10:43 | 99.9568 | 98.5123 | 32:08 | 10:43 | 99.9568 | 98.5123
38 | Kumta | 3 | 3 | 12:06 | 12:06 | 39:32 | 6:15 | 45:47 | 45:47 | 57:53 | 19:18 | 97.8804 | 97.3202 | 57:53 | 19:18 | 97.8804 | 97.3202
39 | Gokarna | 1 | 1 | 17:21 | 17:21 | 1:50 | 1:10 | 3:00 | 3:00 | 20:21 | 20:21 | 99.5833 | 97.1736 | 20:21 | 20:21 | 99.5833 | 97.1736
40 | Kasargod | 1 | 1 | 0:24 | 0:24 | 4:45 | 2:55 | 7:40 | 7:40 | 8:04 | 8:04 | 98.9352 | 98.8796 | 8:04 | 8:04 | 98.9352 | 98.8796
41 | Honnavar | 3 | 3 | 30:30 | 30:30 | 3:36 | 5:02 | 8:38 | 8:38 | 39:08 | 13:03 | 99.6003 | 98.1883 | 39:08 | 13:03 | 99.6003 | 98.1883
42 | Murdeshwar | 4 | 4 | 40:52 | 40:52 | 62:27 | 10:35 | 73:02 | 73:02 | 113:54 | 28:28 | 97.4641 | 96.0451 | 113:54 | 28:28 | 97.4641 | 96.0451
43 | Bhatkal | 2 | 2 | 24:54 | 24:54 | 21:38 | 14:26 | 36:04 | 36:04 | 60:58 | 30:29 | 97.4954 | 95.7662 | 60:58 | 30:29 | 97.4954 | 95.7662
44 | Khanapur | 2 | 2 | 15:52 | 15:52 | 26:40 | 21:35 | 48:15 | 48:15 | 64:07 | 32:03 | 96.6493 | 95.5475 | 64:07 | 32:03 | 96.6493 | 95.5475
45 | Bailhongal | 3 | 3 | 0:00 | 0:00 | 20:55 | 18:15 | 39:10 | 39:10 | 39:10 | 13:03 | 98.1867 | 98.1867 | 39:10 | 13:03 | 98.1867 | 98.1867
46 | Soundatti | 3 | 3 | 10:46 | 10:46 | 26:34 | 14:03 | 40:37 | 40:37 | 51:23 | 17:08 | 98.1196 | 97.6211 | 51:23 | 17:08 | 98.1196 | 97.6211
47 | Ramdurg | 2 | 2 | 5:30 | 5:30 | 23:15 | 9:35 | 32:50 | 32:50 | 38:20 | 19:10 | 97.7199 | 97.338 | 38:20 | 19:10 | 97.7199 | 97.338
48 | Gokak | 7 | 7 | 5:15 | 5:15 | 232:40 | 55:15 | 287:55 | 287:55 | 293:10 | 41:53 | 94.2874 | 94.1832 | 293:10 | 41:53 | 94.2874 | 94.1832
49 | Mudalagi | 2 | 2 | 7:20 | 7:20 | 30:40 | 2:30 | 33:10 | 33:10 | 40:30 | 20:15 | 97.6968 | 97.1875 | 40:30 | 20:15 | 97.6968 | 97.1875
50 | Konnur | 1 | 1 | 0:00 | 0:00 | 16:20 | 3:30 | 19:50 | 19:50 | 19:50 | 19:50 | 97.2454 | 97.2454 | 19:50 | 19:50 | 97.2454 | 97.2454
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 10:45 | 6:30 | 17:15 | 17:15 | 17:15 | 17:15 | 97.6042 | 97.6042 | 17:15 | 17:15 | 97.6042 | 97.6042
52 | Kudachi | 1 | 1 | 0:20 | 0:20 | 20:35 | 6:05 | 26:40 | 26:40 | 27:00 | 27:00 | 96.2963 | 96.25 | 27:00 | 27:00 | 96.2963 | 96.25
53 | Athani | 6 | 6 | 22:38 | 22:38 | 53:06 | 45:47 | 98:53 | 98:53 | 121:31 | 20:15 | 97.711 | 97.1871 | 121:31 | 20:15 | 97.711 | 97.1871
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 4:35 | 4:35 | 9:10 | 9:10 | 9:10 | 4:35 | 99.3634 | 99.3634 | 9:10 | 4:35 | 99.3634 | 99.3634
55 | Nippani | 5 | 5 | 2:30 | 2:30 | 30:50 | 16:00 | 46:50 | 46:50 | 49:20 | 9:52 | 98.6991 | 98.6296 | 49:20 | 9:52 | 98.6991 | 98.6296
56 | Sadalaga | 1 | 1 | 0:00 | 0:00 | 14:30 | 2:50 | 17:20 | 17:20 | 17:20 | 17:20 | 97.5926 | 97.5926 | 17:20 | 17:20 | 97.5926 | 97.5926
57 | Muddebihal | 2 | 2 | 6:10 | 6:10 | 62:40 | 12:20 | 75:00 | 75:00 | 81:10 | 40:35 | 94.7917 | 94.3634 | 81:10 | 40:35 | 94.7917 | 94.3634
58 | Talikot | 1 | 1 | 16:05 | 16:05 | 19:10 | 22:20 | 41:30 | 41:30 | 57:35 | 57:35 | 94.2361 | 92.0023 | 57:35 | 57:35 | 94.2361 | 92.0023
59 | B.Bagewadi | 1 | 1 | 1:30 | 1:30 | 5:42 | 5:20 | 11:02 | 11:02 | 12:32 | 12:32 | 98.4676 | 98.2593 | 12:32 | 12:32 | 98.4676 | 98.2593
60 | Indi | 1 | 1 | 2:27 | 2:27 | 10:37 | 0:46 | 11:23 | 11:23 | 13:50 | 13:50 | 98.419 | 98.0787 | 13:50 | 13:50 | 98.419 | 98.0787
61 | Sindagi | 2 | 2 | 21:30 | 21:30 | 13:25 | 10:10 | 23:35 | 23:35 | 45:05 | 22:32 | 98.3623 | 96.8692 | 45:05 | 22:32 | 98.3623 | 96.8692
62 | Guledgudda | 1 | 1 | 0:00 | 0:00 | 14:35 | 4:05 | 18:40 | 18:40 | 18:40 | 18:40 | 97.4074 | 97.4074 | 18:40 | 18:40 | 97.4074 | 97.4074
63 | Ilkal | 7 | 7 | 22:17 | 22:17 | 30:31 | 66:24 | 96:55 | 96:55 | 119:12 | 17:02 | 98.0771 | 97.6349 | 119:12 | 17:02 | 98.0771 | 97.6349
64 | Kerur | 1 | 1 | 0:18 | 0:18 | 11:10 | 2:05 | 13:15 | 13:15 | 13:33 | 13:33 | 98.1597 | 98.1181 | 13:33 | 13:33 | 98.1597 | 98.1181
65 | Hungund | 2 | 2 | 20:55 | 20:55 | 31:21 | 16:22 | 47:43 | 47:43 | 68:38 | 34:19 | 96.6863 | 95.2338 | 68:38 | 34:19 | 96.6863 | 95.2338
66 | Jamkhandi | 5 | 5 | 2:55 | 2:55 | 54:25 | 5:35 | 60:00 | 60:00 | 62:55 | 12:35 | 98.3333 | 98.2523 | 62:55 | 12:35 | 98.3333 | 98.2523
67 | Mahalingapur | 2 | 2 | 10:18 | 10:18 | 13:50 | 4:12 | 18:02 | 18:02 | 28:20 | 14:10 | 98.7477 | 98.0324 | 28:20 | 14:10 | 98.7477 | 98.0324
68 | Rabakavi | 2 | 2 | 4:40 | 4:40 | 15:35 | 2:10 | 17:45 | 17:45 | 22:25 | 11:12 | 98.7674 | 98.4433 | 22:25 | 11:12 | 98.7674 | 98.4433
69 | Banhatti | 2 | 2 | 8:35 | 8:35 | 20:00 | 0:25 | 20:25 | 20:25 | 29:00 | 14:30 | 98.5822 | 97.9861 | 29:00 | 14:30 | 98.5822 | 97.9861
70 | Terdal | 1 | 1 | 3:00 | 3:00 | 12:12 | 1:28 | 13:40 | 13:40 | 16:40 | 16:40 | 98.1019 | 97.6852 | 16:40 | 16:40 | 98.1019 | 97.6852
71 | Mudhol | 3 | 3 | 2:30 | 2:30 | 39:41 | 43:13 | 82:54 | 82:54 | 85:24 | 28:28 | 96.162 | 96.0463 | 85:24 | 28:28 | 96.162 | 96.0463
72 | Bilagi | 1 | 1 | 1:00 | 1:00 | 15:10 | 9:10 | 24:20 | 24:20 | 25:20 | 25:20 | 96.6204 | 96.4815 | 25:20 | 25:20 | 96.6204 | 96.4815
73 | Lokapur | 2 | 2 | 4:30 | 4:30 | 20:05 | 18:00 | 38:05 | 38:05 | 42:35 | 21:17 | 97.3553 | 97.0428 | 42:35 | 21:17 | 97.3553 | 97.0428
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of May-2019
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 78 | 78 | 35:25 | 135:14 | 520:18 | 310:26 | 830:44 | 1493:02 | 866:09 | 11:06 | 98.5685 | 98.5075 | 1628:16 | 20:53 | 98.6925 | 98.5741
2 | Dharwad(R) | 18 | 18 | 19:50 | 39:40 | 149:48 | 111:50 | 261:38 | 755:34 | 281:28 | 15:38 | 98.0463 | 97.8982 | 795:14 | 44:11 | 97.1328 | 96.9823
3 | Kundagol | 1 | 1 | 27:20 | 65:45 | 13:50 | 6:00 | 19:50 | 44:40 | 47:10 | 47:10 | 97.3342 | 93.6604 | 110:25 | 110:25 | 96.949 | 92.4579
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 8:46 | 10:43 | 19:29 | 42:04 | 19:29 | 19:29 | 97.3813 | 97.3813 | 42:04 | 42:04 | 97.1266 | 97.1266
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 35:20 | 7:45 | 43:05 | 74:25 | 43:05 | 43:05 | 94.2092 | 94.2092 | 74:25 | 74:25 | 94.9169 | 94.9169
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 41:50 | 31:50 | 73:40 | 171:20 | 73:40 | 36:50 | 95.0493 | 95.0493 | 171:20 | 85:40 | 94.1485 | 94.1485
7 | Alnavar | 1 | 1 | 19:50 | 39:40 | 15:50 | 7:00 | 22:50 | 32:05 | 42:40 | 42:40 | 96.931 | 94.2652 | 71:45 | 71:45 | 97.8085 | 95.099
8 | Naragund | 2 | 2 | 9:30 | 25:00 | 27:25 | 43:50 | 71:15 | 172:45 | 80:45 | 40:22 | 95.2117 | 94.5733 | 197:45 | 98:52 | 94.1001 | 93.2462
9 | Shirahatti | 2 | 2 | 0:00 | 0:00 | 15:10 | 15:00 | 30:10 | 40:55 | 30:10 | 15:05 | 97.9727 | 97.9727 | 40:55 | 20:28 | 98.6026 | 98.6026
10 | Laxmeshwar | 6 | 6 | 0:00 | 0:00 | 98:17 | 86:00 | 184:17 | 352:10 | 184:17 | 30:43 | 95.8718 | 95.8718 | 352:10 | 58:42 | 95.9908 | 95.9908
11 | Naregal | 1 | 1 | 0:00 | 0:00 | 6:00 | 6:40 | 12:40 | 25:20 | 12:40 | 12:40 | 98.2975 | 98.2975 | 25:20 | 25:20 | 98.2696 | 98.2696
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 24:20 | 16:25 | 40:45 | 79:15 | 40:45 | 20:22 | 97.2614 | 97.2614 | 79:15 | 39:38 | 97.2934 | 97.2934
13 | Ron | 2 | 2 | 10:50 | 10:50 | 23:10 | 22:10 | 45:20 | 71:11 | 56:10 | 28:05 | 96.9534 | 96.2254 | 82:01 | 41:00 | 97.5689 | 97.1989
14 | Mundaragi | 3 | 3 | 5:20 | 7:05 | 95:45 | 27:55 | 123:40 | 192:20 | 129:00 | 43:00 | 94.4594 | 94.2204 | 199:25 | 66:28 | 95.6208 | 95.4595
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 39:07 | 6:56 | 46:03 | 94:44 | 46:03 | 46:03 | 93.8105 | 93.8105 | 94:44 | 94:44 | 93.5291 | 93.5291
16 | G.C.T.M | 1 | 1 | 9:40 | 28:00 | 20:50 | 17:45 | 38:35 | 81:35 | 48:15 | 48:15 | 94.8141 | 93.5148 | 109:35 | 109:35 | 94.4274 | 92.5148
17 | F.C.S.M | 2 | 2 | 16:30 | 51:00 | 27:25 | 19:45 | 47:10 | 95:10 | 63:40 | 31:50 | 96.8302 | 95.7213 | 146:10 | 73:05 | 96.7498 | 95.008
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 8:36 | 15:05 | 23:41 | 43:59 | 23:41 | 23:41 | 96.8168 | 96.8168 | 43:59 | 43:59 | 96.9957 | 96.9957
19 | Hole-Alur | 1 | 1 | 14:25 | 29:05 | 14:55 | 16:05 | 31:00 | 55:25 | 45:25 | 45:25 | 95.8333 | 93.8956 | 84:30 | 84:30 | 96.2147 | 94.2281
20 | Savanur | 2 | 2 | 1:00 | 2:10 | 18:45 | 12:55 | 31:40 | 69:35 | 32:40 | 16:20 | 97.8719 | 97.8047 | 71:45 | 35:52 | 97.6235 | 97.5495
21 | Shiggaon | 2 | 2 | 19:15 | 35:15 | 14:40 | 8:40 | 23:20 | 58:10 | 42:35 | 21:18 | 98.4319 | 97.1382 | 93:25 | 46:42 | 98.0134 | 96.8095
22 | Bankapur | 1 | 1 | 7:15 | 15:00 | 5:25 | 3:00 | 8:25 | 18:00 | 15:40 | 15:40 | 98.8687 | 97.8943 | 33:00 | 33:00 | 98.7705 | 97.7459
23 | Hangal | 2 | 2 | 0:00 | 1:10 | 32:00 | 13:00 | 45:00 | 134:15 | 45:00 | 22:30 | 96.9758 | 96.9758 | 135:25 | 67:42 | 95.415 | 95.3751
24 | Ranebennur | 16 | 16 | 27:05 | 37:31 | 142:50 | 107:01 | 249:51 | 426:28 | 276:56 | 17:18 | 97.9011 | 97.6736 | 463:59 | 29:00 | 98.1794 | 98.0192
25 | Halageri | 2 | 2 | 20:00 | 58:40 | 6:05 | 1:30 | 7:35 | 25:55 | 27:35 | 13:48 | 99.4904 | 98.1463 | 84:35 | 42:18 | 99.1149 | 97.1112
26 | Tuminakatti | 3 | 3 | 2:30 | 5:30 | 54:10 | 0:00 | 54:10 | 109:45 | 56:40 | 18:53 | 97.5732 | 97.4612 | 115:15 | 38:25 | 97.5011 | 97.3759
27 | Kahanderayanahalli | 2 | 2 | 32:05 | 53:50 | 8:25 | 30:20 | 38:45 | 142:19 | 70:50 | 35:25 | 97.3958 | 95.2397 | 196:09 | 98:04 | 95.1395 | 93.3009
28 | Rattihalli | 1 | 1 | 2:15 | 3:15 | 13:30 | 3:55 | 17:25 | 36:40 | 19:40 | 19:40 | 97.6591 | 97.3566 | 39:55 | 39:55 | 97.4954 | 97.2735
29 | Hirekerur | 3 | 3 | 33:45 | 75:30 | 66:45 | 29:55 | 96:40 | 182:00 | 130:25 | 43:28 | 95.6691 | 94.157 | 257:30 | 85:50 | 95.8561 | 94.1371
30 | Byadagi | 6 | 6 | 41:45 | 61:25 | 51:20 | 44:45 | 96:05 | 195:50 | 137:50 | 22:58 | 97.8476 | 96.9123 | 257:15 | 42:53 | 97.7706 | 97.0714
31 | Sirsi | 3 | 3 | 25:35 | 51:28 | 3:35 | 11:24 | 14:59 | 23:19 | 40:34 | 13:31 | 99.3287 | 98.1825 | 74:47 | 24:56 | 99.4691 | 98.2973
32 | Yellapur | 3 | 3 | 4:39 | 24:29 | 73:10 | 21:55 | 95:05 | 231:55 | 99:44 | 33:15 | 95.74 | 95.5317 | 256:24 | 85:28 | 94.7196 | 94.1621
33 | Mundagod | 3 | 3 | 1:07 | 11:02 | 19:10 | 23:00 | 42:10 | 71:10 | 43:17 | 14:26 | 98.1108 | 98.0608 | 82:12 | 27:24 | 98.3796 | 98.1284
34 | Siddapur | 2 | 2 | 4:50 | 4:50 | 13:50 | 22:05 | 35:55 | 69:15 | 40:45 | 20:22 | 97.5862 | 97.2614 | 74:05 | 37:02 | 97.6349 | 97.4698
35 | Dandeli | 8 | 8 | 2:08 | 15:16 | 30:30 | 54:12 | 84:42 | 260:35 | 86:50 | 10:51 | 98.5769 | 98.5411 | 275:51 | 34:29 | 97.7751 | 97.6447
36 | Haliyal | 3 | 3 | 0:54 | 6:58 | 10:46 | 12:06 | 22:52 | 81:16 | 23:46 | 7:55 | 98.9755 | 98.9352 | 88:14 | 29:25 | 98.1497 | 97.991
37 | Ankola | 3 | 3 | 20:24 | 51:36 | 8:00 | 4:38 | 12:38 | 13:34 | 33:02 | 11:01 | 99.434 | 98.52 | 65:10 | 21:43 | 99.6911 | 98.5162
38 | Kumta | 3 | 3 | 0:00 | 12:06 | 17:08 | 4:33 | 21:41 | 67:28 | 21:41 | 7:14 | 99.0285 | 99.0285 | 79:34 | 26:31 | 98.4639 | 98.1884
39 | Gokarna | 1 | 1 | 24:12 | 41:33 | 5:05 | 1:25 | 6:30 | 9:30 | 30:42 | 30:42 | 99.1263 | 95.8737 | 51:03 | 51:03 | 99.3511 | 96.513
40 | Kasargod | 1 | 1 | 28:15 | 28:39 | 6:25 | 1:15 | 7:40 | 15:20 | 35:55 | 35:55 | 98.9695 | 95.1725 | 43:59 | 43:59 | 98.9526 | 96.9957
41 | Honnavar | 3 | 3 | 49:48 | 80:18 | 21:53 | 2:16 | 24:09 | 32:47 | 73:57 | 24:39 | 98.918 | 96.6868 | 113:05 | 37:42 | 99.2536 | 97.4252
42 | Murdeshwar | 4 | 4 | 0:44 | 41:36 | 38:48 | 5:53 | 44:41 | 117:43 | 45:25 | 11:21 | 98.4985 | 98.4739 | 159:19 | 39:50 | 97.9898 | 97.2794
43 | Bhatkal | 2 | 2 | 21:28 | 46:22 | 27:30 | 8:59 | 36:29 | 72:33 | 57:57 | 28:58 | 97.5482 | 96.1055 | 118:55 | 59:27 | 97.5222 | 95.9386
44 | Khanapur | 2 | 2 | 0:00 | 15:52 | 2:55 | 27:10 | 30:05 | 78:20 | 30:05 | 15:02 | 97.9783 | 97.9783 | 94:12 | 47:06 | 97.3247 | 96.7828
45 | Bailhongal | 3 | 3 | 2:15 | 2:15 | 16:15 | 10:40 | 26:55 | 66:05 | 29:10 | 9:43 | 98.7941 | 98.6932 | 68:20 | 22:47 | 98.4954 | 98.4441
46 | Soundatti | 3 | 3 | 0:00 | 10:46 | 71:08 | 19:46 | 90:54 | 131:31 | 90:54 | 30:18 | 95.9274 | 95.9274 | 142:17 | 47:26 | 97.0055 | 96.7604
47 | Ramdurg | 2 | 2 | 6:20 | 11:50 | 38:05 | 17:35 | 55:40 | 88:30 | 62:00 | 31:00 | 96.259 | 95.8333 | 100:20 | 50:10 | 96.9775 | 96.5733
48 | Gokak | 7 | 7 | 83:10 | 88:25 | 86:30 | 52:50 | 139:20 | 427:15 | 222:30 | 31:47 | 97.3246 | 95.7277 | 515:40 | 73:40 | 95.8309 | 94.9681
49 | Mudalagi | 2 | 2 | 9:30 | 16:50 | 12:30 | 8:10 | 20:40 | 53:50 | 30:10 | 15:05 | 98.6111 | 97.9727 | 70:40 | 35:20 | 98.1614 | 97.5865
50 | Konnur | 1 | 1 | 3:00 | 3:00 | 10:55 | 16:10 | 27:05 | 46:55 | 30:05 | 30:05 | 96.3598 | 95.9565 | 49:55 | 49:55 | 96.7953 | 96.5904
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 17:00 | 18:40 | 35:40 | 52:55 | 35:40 | 35:40 | 95.2061 | 95.2061 | 52:55 | 52:55 | 96.3855 | 96.3855
52 | Kudachi | 1 | 1 | 0:25 | 0:45 | 20:50 | 4:40 | 25:30 | 52:10 | 25:55 | 25:55 | 96.5726 | 96.5166 | 52:55 | 52:55 | 96.4367 | 96.3855
53 | Athani | 6 | 6 | 8:00 | 30:38 | 54:54 | 60:11 | 115:05 | 213:58 | 123:05 | 20:31 | 97.422 | 97.2428 | 244:36 | 40:46 | 97.5641 | 97.2154
54 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 7:25 | 4:45 | 12:10 | 21:20 | 12:10 | 6:05 | 99.1823 | 99.1823 | 21:20 | 10:40 | 99.2714 | 99.2714
55 | Nippani | 5 | 5 | 77:05 | 79:35 | 72:15 | 9:25 | 81:40 | 128:30 | 158:45 | 31:45 | 97.8047 | 95.7325 | 208:05 | 41:37 | 98.2445 | 97.1573
56 | Sadalaga | 1 | 1 | 2:30 | 2:30 | 5:50 | 2:30 | 8:20 | 25:40 | 10:50 | 10:50 | 98.8799 | 98.5439 | 28:10 | 28:10 | 98.2468 | 98.076
57 | Muddebihal | 2 | 2 | 8:10 | 14:20 | 45:00 | 10:35 | 55:35 | 130:35 | 63:45 | 31:52 | 96.2646 | 95.7157 | 144:55 | 72:28 | 95.5402 | 95.0507
58 | Talikot | 1 | 1 | 44:40 | 60:45 | 23:40 | 46:55 | 70:35 | 112:05 | 115:15 | 115:15 | 90.513 | 84.5094 | 172:50 | 172:50 | 92.344 | 88.1944
59 | B.Bagewadi | 1 | 1 | 2:30 | 4:00 | 3:05 | 3:30 | 6:35 | 17:37 | 9:05 | 9:05 | 99.1151 | 98.7791 | 21:37 | 21:37 | 98.7967 | 98.5235
60 | Indi | 1 | 1 | 3:38 | 6:05 | 11:59 | 2:28 | 14:27 | 25:50 | 18:05 | 18:05 | 98.0578 | 97.5694 | 31:55 | 31:55 | 98.2354 | 97.8199
61 | Sindagi | 2 | 2 | 10:10 | 31:40 | 8:35 | 5:05 | 13:40 | 37:15 | 23:50 | 11:55 | 99.0815 | 98.3983 | 68:55 | 34:28 | 98.7278 | 97.6463
62 | Guledgudda | 1 | 1 | 0:00 | 0:00 | 13:35 | 16:16 | 29:51 | 48:31 | 29:51 | 29:51 | 95.9879 | 95.9879 | 48:31 | 48:31 | 96.686 | 96.686
63 | Ilkal | 7 | 7 | 64:45 | 87:02 | 36:34 | 148:44 | 185:18 | 282:13 | 250:03 | 35:43 | 96.442 | 95.1987 | 369:15 | 52:45 | 97.2461 | 96.3969
64 | Kerur | 1 | 1 | 2:05 | 2:23 | 19:24 | 7:55 | 27:19 | 40:34 | 29:24 | 29:24 | 96.3284 | 96.0484 | 42:57 | 42:57 | 97.2291 | 97.0663
65 | Hungund | 2 | 2 | 16:50 | 37:45 | 59:27 | 34:03 | 93:30 | 141:13 | 110:20 | 55:10 | 93.7164 | 92.5851 | 178:58 | 89:29 | 95.177 | 93.8878
66 | Jamkhandi | 5 | 5 | 7:00 | 9:55 | 96:25 | 36:55 | 133:20 | 193:20 | 140:20 | 28:04 | 96.4158 | 96.2276 | 203:15 | 40:39 | 97.3588 | 97.2234
67 | Mahalingapur | 2 | 2 | 15:24 | 25:42 | 20:50 | 6:27 | 27:17 | 45:19 | 42:41 | 21:20 | 98.1664 | 97.1315 | 71:01 | 35:30 | 98.4523 | 97.5746
68 | Rabakavi | 2 | 2 | 15:40 | 20:20 | 22:01 | 12:25 | 34:26 | 52:11 | 50:06 | 25:03 | 97.6859 | 96.6331 | 72:31 | 36:16 | 98.2178 | 97.5233
69 | Banhatti | 2 | 2 | 9:00 | 17:35 | 26:30 | 3:55 | 30:25 | 50:50 | 39:25 | 19:42 | 97.9559 | 97.351 | 68:25 | 34:12 | 98.2639 | 97.6634
70 | Terdal | 1 | 1 | 7:06 | 10:06 | 16:05 | 5:55 | 22:00 | 35:40 | 29:06 | 29:06 | 97.043 | 96.0887 | 45:46 | 45:46 | 97.5638 | 96.8739
71 | Mudhol | 3 | 3 | 1:50 | 4:20 | 16:37 | 13:18 | 29:55 | 112:49 | 31:45 | 10:35 | 98.6596 | 98.5775 | 117:09 | 39:03 | 97.4313 | 97.3327
72 | Bilagi | 1 | 1 | 0:10 | 1:10 | 14:50 | 3:40 | 18:30 | 42:50 | 18:40 | 18:40 | 97.5134 | 97.491 | 44:00 | 44:00 | 97.0742 | 96.9945
73 | Lokapur | 2 | 2 | 0:00 | 4:30 | 34:05 | 67:50 | 101:55 | 140:00 | 101:55 | 50:58 | 93.1508 | 93.1508 | 144:30 | 72:15 | 95.2186 | 95.0649
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of June-2019
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 79:09 | 214:23 | 605:59 | 441:33 | 1047:32 | 2540:34 | 1126:41 | 14:16 | 98.1583 | 98.0192 | 2754:57 | 34:52 | 98.5275 | 98.4033
2 | Dharwad(R) | 18 | 18 | 32:41 | 72:21 | 216:49 | 254:57 | 471:46 | 1227:20 | 504:27 | 28:01 | 96.3598 | 96.1076 | 1299:41 | 72:12 | 96.878 | 96.6939
3 | Kundagol | 1 | 1 | 46:30 | 112:15 | 7:55 | 14:25 | 22:20 | 67:00 | 68:50 | 68:50 | 96.8981 | 90.4398 | 179:15 | 179:15 | 96.9322 | 91.7926
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 11:28 | 6:54 | 18:22 | 60:26 | 18:22 | 18:22 | 97.4491 | 97.4491 | 60:26 | 60:26 | 97.2329 | 97.2329
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 17:45 | 20:25 | 38:10 | 112:35 | 38:10 | 38:10 | 94.6991 | 94.6991 | 112:35 | 112:35 | 94.8451 | 94.8451
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 33:45 | 51:10 | 84:55 | 256:15 | 84:55 | 42:28 | 94.103 | 94.103 | 256:15 | 128:08 | 94.1335 | 94.1335
7 | Alnavar | 1 | 1 | 11:55 | 51:35 | 19:15 | 5:45 | 25:00 | 57:05 | 36:55 | 36:55 | 96.5278 | 94.8727 | 108:40 | 108:40 | 97.3863 | 95.0244
8 | Naragund | 2 | 2 | 1:50 | 26:50 | 27:35 | 52:25 | 80:00 | 252:45 | 81:50 | 40:55 | 94.4444 | 94.3171 | 279:35 | 139:48 | 94.2136 | 93.5993
9 | Shirahatti | 2 | 2 | 0:00 | 0:00 | 36:20 | 35:15 | 71:35 | 112:30 | 71:35 | 35:48 | 95.0289 | 95.0289 | 112:30 | 56:15 | 97.4245 | 97.4245
10 | Laxmeshwar | 6 | 6 | 0:00 | 0:00 | 105:25 | 156:30 | 261:55 | 614:05 | 261:55 | 43:39 | 93.9371 | 93.9371 | 614:05 | 102:21 | 95.3138 | 95.3138
11 | Naregal | 1 | 1 | 13:30 | 13:30 | 18:45 | 8:45 | 27:30 | 52:50 | 41:00 | 41:00 | 96.1806 | 94.3056 | 66:20 | 66:20 | 97.5809 | 96.9628
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 60:20 | 30:50 | 91:10 | 170:25 | 91:10 | 45:35 | 93.669 | 93.669 | 170:25 | 85:12 | 96.0985 | 96.0985
13 | Ron | 2 | 2 | 7:40 | 18:30 | 28:40 | 27:15 | 55:55 | 127:06 | 63:35 | 31:48 | 96.1169 | 95.5845 | 145:36 | 72:48 | 97.0902 | 96.6667
14 | Mundaragi | 3 | 3 | 17:05 | 24:10 | 90:00 | 52:50 | 142:50 | 335:10 | 159:55 | 53:18 | 93.3873 | 92.5965 | 359:20 | 119:47 | 94.8845 | 94.5157
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 29:26 | 31:05 | 60:31 | 155:15 | 60:31 | 60:31 | 91.5949 | 91.5949 | 155:15 | 155:15 | 92.8915 | 92.8915
16 | G.C.T.M | 1 | 1 | 13:50 | 41:50 | 34:25 | 9:50 | 44:15 | 125:50 | 58:05 | 58:05 | 93.8542 | 91.9329 | 167:40 | 167:40 | 94.2384 | 92.323
17 | F.C.S.M | 2 | 2 | 25:35 | 76:35 | 19:05 | 40:20 | 59:25 | 154:35 | 85:00 | 42:30 | 95.8738 | 94.0972 | 231:10 | 115:35 | 96.461 | 94.7077
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 7:33 | 5:17 | 12:50 | 56:49 | 12:50 | 12:50 | 98.2176 | 98.2176 | 56:49 | 56:49 | 97.3985 | 97.3985
19 | Hole-Alur | 1 | 1 | 7:20 | 36:25 | 20:45 | 18:20 | 39:05 | 94:30 | 46:25 | 46:25 | 94.5718 | 93.5532 | 130:55 | 130:55 | 95.6731 | 94.0056
20 | Savanur | 2 | 2 | 4:50 | 7:00 | 30:25 | 8:50 | 39:15 | 108:50 | 44:05 | 22:02 | 97.2743 | 96.9387 | 115:50 | 57:55 | 97.5084 | 97.3481
21 | Shiggaon | 2 | 2 | 10:45 | 46:00 | 9:50 | 31:00 | 40:50 | 99:00 | 51:35 | 25:48 | 97.1644 | 96.4178 | 145:00 | 72:30 | 97.7335 | 96.6804
22 | Bankapur | 1 | 1 | 16:15 | 31:15 | 7:20 | 8:05 | 15:25 | 33:25 | 31:40 | 31:40 | 97.8588 | 95.6019 | 64:40 | 64:40 | 98.4699 | 97.0391
23 | Hangal | 2 | 2 | 0:00 | 1:10 | 74:35 | 18:35 | 93:10 | 227:25 | 93:10 | 46:35 | 93.5301 | 93.5301 | 228:35 | 114:18 | 94.7936 | 94.7669
24 | Ranebennur | 16 | 16 | 3:50 | 41:21 | 230:57 | 161:58 | 392:55 | 819:23 | 396:45 | 24:48 | 96.5893 | 96.556 | 860:44 | 53:48 | 97.6552 | 97.5368
25 | Halageri | 2 | 2 | 56:50 | 115:30 | 6:45 | 1:40 | 8:25 | 34:20 | 65:15 | 32:38 | 99.4155 | 95.4688 | 149:50 | 74:55 | 99.214 | 96.5697
26 | Tuminakatti | 3 | 3 | 1:15 | 6:45 | 103:35 | 0:00 | 103:35 | 213:20 | 104:50 | 34:57 | 95.2045 | 95.1466 | 220:05 | 73:22 | 96.744 | 96.641
27 | Kahanderayanahalli | 2 | 2 | 20:35 | 74:25 | 90:40 | 19:30 | 110:10 | 252:29 | 130:45 | 65:23 | 92.3495 | 90.9201 | 326:54 | 163:27 | 94.2197 | 92.516
28 | Rattihalli | 1 | 1 | 0:30 | 3:45 | 24:10 | 6:10 | 30:20 | 67:00 | 30:50 | 30:50 | 95.787 | 95.7176 | 70:45 | 70:45 | 96.9322 | 96.7605
29 | Hirekerur | 3 | 3 | 39:05 | 114:35 | 69:10 | 60:10 | 129:20 | 311:20 | 168:25 | 56:08 | 94.0123 | 92.2029 | 425:55 | 141:58 | 95.2483 | 93.4994
30 | Byadagi | 6 | 6 | 37:35 | 99:00 | 77:35 | 158:00 | 235:35 | 431:25 | 273:10 | 45:32 | 94.5467 | 93.6767 | 530:25 | 88:24 | 96.7077 | 95.9523
31 | Sirsi | 5 | 5 | 39:10 | 90:38 | 66:05 | 44:25 | 110:30 | 133:49 | 149:40 | 29:56 | 96.9306 | 95.8426 | 224:27 | 44:53 | 98.7746 | 97.9446
32 | Yellapur | 3 | 3 | 69:55 | 94:24 | 44:05 | 17:49 | 61:54 | 293:49 | 131:49 | 43:56 | 97.1343 | 93.8974 | 388:13 | 129:24 | 95.5156 | 94.0748
33 | Mundagod | 3 | 3 | 5:45 | 16:47 | 70:45 | 47:50 | 118:35 | 189:45 | 124:20 | 41:27 | 94.51 | 94.2438 | 206:32 | 68:51 | 97.1039 | 96.8478
34 | Siddapur | 2 | 2 | 0:00 | 4:50 | 24:30 | 28:10 | 52:40 | 121:55 | 52:40 | 26:20 | 96.3426 | 96.3426 | 126:45 | 63:22 | 97.2089 | 97.0982
35 | Dandeli | 8 | 8 | 102:24 | 117:40 | 170:12 | 159:00 | 329:12 | 589:47 | 431:36 | 53:57 | 94.2847 | 92.5069 | 707:27 | 88:26 | 96.6244 | 95.951
36 | Haliyal | 3 | 3 | 5:17 | 12:15 | 24:31 | 18:15 | 42:46 | 124:02 | 48:03 | 16:01 | 98.0201 | 97.7755 | 136:17 | 45:26 | 98.1069 | 97.92
37 | Ankola | 3 | 3 | 105:24 | 157:00 | 1:34 | 27:12 | 28:46 | 42:20 | 134:10 | 44:43 | 98.6682 | 93.7886 | 199:20 | 66:27 | 99.3539 | 96.9577
38 | Kumta | 3 | 3 | 17:33 | 29:39 | 36:09 | 57:26 | 93:35 | 161:03 | 111:08 | 37:03 | 95.6674 | 94.8549 | 190:42 | 63:34 | 97.542 | 97.0894
39 | Gokarna | 1 | 1 | 15:46 | 57:19 | 1:10 | 8:38 | 9:48 | 19:18 | 25:34 | 25:34 | 98.6389 | 96.4491 | 76:37 | 76:37 | 99.1163 | 96.4919
40 | Kasargod | 1 | 1 | 19:50 | 48:29 | 11:25 | 18:40 | 30:05 | 45:25 | 49:55 | 49:55 | 95.8218 | 93.0671 | 93:54 | 93:54 | 97.9205 | 95.7005
41 | Honnavar | 3 | 3 | 41:48 | 122:06 | 60:37 | 35:26 | 96:03 | 128:50 | 137:51 | 45:57 | 95.5532 | 93.6181 | 250:56 | 83:39 | 98.0337 | 96.1701
42 | Murdeshwar | 4 | 4 | 107:40 | 149:16 | 75:20 | 58:33 | 133:53 | 251:36 | 241:33 | 60:23 | 95.3513 | 91.6128 | 400:52 | 100:13 | 97.12 | 95.4113
43 | Bhatkal | 2 | 2 | 7:56 | 54:18 | 53:12 | 23:31 | 76:43 | 149:16 | 84:39 | 42:20 | 94.6725 | 94.1215 | 203:34 | 101:47 | 96.5827 | 95.3396
44 | Khanapur | 2 | 2 | 2:00 | 17:52 | 18:20 | 9:45 | 28:05 | 106:25 | 30:05 | 15:02 | 98.0498 | 97.9109 | 124:17 | 62:08 | 97.5637 | 97.1547
45 | Bailhongal | 3 | 3 | 22:51 | 25:06 | 15:18 | 16:00 | 31:18 | 97:23 | 54:09 | 18:03 | 98.5509 | 97.4931 | 122:29 | 40:50 | 98.5137 | 98.1306
46 | Soundatti | 3 | 3 | 3:34 | 14:20 | 38:34 | 11:26 | 50:00 | 181:31 | 53:34 | 17:51 | 97.6852 | 97.5201 | 195:51 | 65:17 | 97.2296 | 97.0108
47 | Ramdurg | 2 | 2 | 6:20 | 18:10 | 39:55 | 24:00 | 63:55 | 152:25 | 70:15 | 35:08 | 95.5613 | 95.1215 | 170:35 | 85:18 | 96.5106 | 96.0947
48 | Gokak | 7 | 7 | 1:30 | 89:55 | 127:05 | 95:30 | 222:35 | 649:50 | 224:05 | 32:01 | 95.5837 | 95.5539 | 739:45 | 105:41 | 95.7494 | 95.1612
49 | Mudalagi | 2 | 2 | 10:30 | 27:20 | 25:15 | 24:00 | 49:15 | 103:05 | 59:45 | 29:52 | 96.5799 | 95.8507 | 130:25 | 65:12 | 97.64 | 97.0143
50 | Konnur | 1 | 1 | 0:00 | 3:00 | 14:25 | 13:45 | 28:10 | 75:05 | 28:10 | 28:10 | 96.088 | 96.088 | 78:05 | 78:05 | 96.5621 | 96.4248
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 26:10 | 0:24 | 26:34 | 79:29 | 26:34 | 26:34 | 96.3102 | 96.3102 | 79:29 | 79:29 | 96.3607 | 96.3607
52 | Kudachi | 1 | 1 | 0:50 | 1:35 | 42:35 | 5:50 | 48:25 | 100:35 | 49:15 | 49:15 | 93.2755 | 93.1597 | 102:10 | 102:10 | 95.3945 | 95.322
53 | Athani | 6 | 6 | 11:42 | 42:20 | 59:52 | 77:16 | 137:08 | 351:06 | 148:50 | 24:48 | 96.8256 | 96.5548 | 393:26 | 65:34 | 97.3207 | 96.9976
54 | Chikkodi | 2 | 2 | 1:40 | 1:40 | 18:25 | 9:35 | 28:00 | 49:20 | 29:40 | 14:50 | 98.0556 | 97.9398 | 51:00 | 25:30 | 98.8706 | 98.8324
55 | Nippani | 5 | 5 | 0:00 | 79:35 | 48:30 | 52:15 | 100:45 | 229:15 | 100:45 | 20:09 | 97.2014 | 97.2014 | 308:50 | 61:46 | 97.9006 | 97.1719
56 | Sadalaga | 1 | 1 | 0:00 | 2:30 | 23:53 | 9:13 | 33:06 | 58:46 | 33:06 | 33:06 | 95.4028 | 95.4028 | 61:16 | 61:16 | 97.3092 | 97.1947
57 | Muddebihal | 2 | 2 | 32:20 | 46:40 | 43:00 | 40:35 | 83:35 | 214:10 | 115:55 | 57:58 | 94.1956 | 91.9502 | 260:50 | 130:25 | 95.0969 | 94.0285
58 | Talikot | 1 | 1 | 37:40 | 98:25 | 13:55 | 67:40 | 81:35 | 193:40 | 119:15 | 119:15 | 88.669 | 83.4375 | 292:05 | 292:05 | 91.1325 | 86.6262
59 | B.Bagewadi | 1 | 1 | 16:25 | 20:25 | 6:05 | 9:59 | 16:04 | 33:41 | 32:29 | 32:29 | 97.7685 | 95.4884 | 54:06 | 54:06 | 98.4577 | 97.5229
60 | Indi | 1 | 1 | 0:00 | 6:05 | 12:36 | 13:51 | 26:27 | 52:17 | 26:27 | 26:27 | 96.3264 | 96.3264 | 58:22 | 58:22 | 97.6061 | 97.3275
61 | Sindagi | 2 | 2 | 87:30 | 119:10 | 14:55 | 17:50 | 32:45 | 70:00 | 120:15 | 60:08 | 97.7257 | 91.6493 | 189:10 | 94:35 | 98.3974 | 95.6693
62 | Guledgudda | 1 | 1 | 0:00 | 0:00 | 14:32 | 25:05 | 39:37 | 88:08 | 39:37 | 39:37 | 94.4977 | 94.4977 | 88:08 | 88:08 | 95.9646 | 95.9646
63 | Ilkal | 8 | 8 | 84:01 | 171:03 | 94:38 | 137:21 | 231:59 | 514:12 | 316:00 | 39:30 | 95.9725 | 94.5139 | 685:15 | 85:39 | 97.057 | 96.078
64 | Kerur | 2 | 2 | 3:10 | 5:33 | 25:48 | 8:03 | 33:51 | 74:25 | 37:01 | 18:30 | 97.6493 | 97.4294 | 79:58 | 39:59 | 98.2963 | 98.1693
65 | Hungund | 3 | 2 | 9:25 | 47:10 | 73:08 | 81:58 | 155:06 | 296:19 | 164:31 | 54:50 | 92.8194 | 92.3835 | 343:29 | 114:30 | 95.4775 | 94.7576
66 | GADDANKERI | 4 | 4 | 14:03 | 14:03 | 80:05 | 33:59 | 114:04 | 114:04 | 128:07 | 32:02 | 96.0394 | 95.5515 | 128:07 | 32:02 | 96.0394 | 95.5515
67 | RAMPUR | 1 | 1 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 100 | 100 | 0:00 | 0:00 | 100 | 100
68 | KALADAGI | 2 | 2 | 0:05 | 0:05 | 45:20 | 34:05 | 79:25 | 79:25 | 79:30 | 39:45 | 94.485 | 94.4792 | 79:30 | 39:45 | 94.485 | 94.4792
69 | ACHANUR | 1 | 1 | 0:00 | 0:00 | 52:00 | 109:00 | 161:00 | 161:00 | 161:00 | 161:00 | 77.6389 | 77.6389 | 161:00 | 161:00 | 77.6389 | 77.6389
70 | SHIRUR | 1 | 1 | 9:30 | 9:30 | 14:45 | 13:25 | 28:10 | 28:10 | 37:40 | 37:40 | 96.088 | 94.7685 | 37:40 | 37:40 | 96.088 | 94.7685
71 | BADAMI | 1 | 1 | 5:16 | 5:16 | 30:54 | 19:46 | 50:40 | 50:40 | 55:56 | 55:56 | 92.963 | 92.2315 | 55:56 | 55:56 | 92.963 | 92.2315
72 | KULAGERI | 1 | 1 | 1:45 | 1:45 | 5:35 | 0:55 | 6:30 | 6:30 | 8:15 | 8:15 | 99.0972 | 98.8542 | 8:15 | 8:15 | 99.0972 | 98.8542
73 | Jamkhandi | 5 | 5 | 19:50 | 29:45 | 81:06 | 58:11 | 139:17 | 332:37 | 159:07 | 31:49 | 96.131 | 95.5801 | 362:22 | 72:28 | 96.9541 | 96.6816
74 | Mahalingapur | 2 | 2 | 4:20 | 30:02 | 39:12 | 17:06 | 56:18 | 101:37 | 60:38 | 30:19 | 96.0903 | 95.7894 | 131:39 | 65:50 | 97.6736 | 96.986
75 | Rabakavi | 2 | 2 | 2:00 | 22:20 | 28:10 | 5:08 | 33:18 | 85:29 | 35:18 | 17:39 | 97.6875 | 97.5486 | 107:49 | 53:54 | 98.043 | 97.5317
76 | Banhatti | 2 | 2 | 8:40 | 26:15 | 26:09 | 2:59 | 29:08 | 79:58 | 37:48 | 18:54 | 97.9769 | 97.375 | 106:13 | 53:07 | 98.1693 | 97.5683
77 | Terdal | 1 | 1 | 1:45 | 11:51 | 21:02 | 8:55 | 29:57 | 65:37 | 31:42 | 31:42 | 95.8403 | 95.5972 | 77:28 | 77:28 | 96.9956 | 96.453
78 | Mudhol | 3 | 3 | 9:21 | 13:41 | 43:26 | 32:00 | 75:26 | 188:15 | 84:47 | 28:16 | 96.5077 | 96.0748 | 201:56 | 67:19 | 97.1268 | 96.918
79 | Bilagi | 1 | 1 | 6:30 | 7:40 | 33:50 | 17:50 | 51:40 | 94:30 | 58:10 | 58:10 | 92.8241 | 91.9213 | 102:10 | 102:10 | 95.6731 | 95.322
80 | Lokapur | 2 | 2 | 2:10 | 6:40 | 33:35 | 51:55 | 85:30 | 225:30 | 87:40 | 43:50 | 94.0625 | 93.912 | 232:10 | 116:05 | 94.8375 | 94.6848
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of July-2019
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 89:01 | 303:24 | 312:43 | 390:32 | 703:15 | 3243:49 | 792:16 | 10:02 | 98.8035 | 98.6521 | 3547:13 | 44:54 | 98.5976 | 98.4665
2 | Dharwad(R) | 18 | 18 | 4:55 | 77:16 | 251:13 | 197:28 | 448:41 | 1676:01 | 453:36 | 25:12 | 96.6496 | 96.6129 | 1753:17 | 97:24 | 96.8199 | 96.6733
3 | Kundagol | 1 | 1 | 31:25 | 143:40 | 5:55 | 2:15 | 8:10 | 75:10 | 39:35 | 39:35 | 98.9023 | 94.6797 | 218:50 | 218:50 | 97.4328 | 92.5262
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 5:27 | 5:19 | 10:46 | 71:12 | 10:46 | 10:46 | 98.5529 | 98.5529 | 71:12 | 71:12 | 97.5683 | 97.5683
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 20:46 | 16:47 | 37:33 | 150:08 | 37:33 | 37:33 | 94.953 | 94.953 | 150:08 | 150:08 | 94.8725 | 94.8725
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 31:10 | 15:30 | 46:40 | 302:55 | 46:40 | 23:20 | 96.8638 | 96.8638 | 302:55 | 151:28 | 94.8272 | 94.8272
7 | Alnavar | 1 | 1 | 2:25 | 54:00 | 18:00 | 2:00 | 20:00 | 77:05 | 22:25 | 22:25 | 97.3118 | 96.987 | 131:05 | 131:05 | 97.3674 | 95.5231
8 | Naragund | 2 | 2 | 1:20 | 28:10 | 34:00 | 45:25 | 79:25 | 332:10 | 80:45 | 40:22 | 94.6629 | 94.5733 | 360:20 | 180:10 | 94.3278 | 93.8468
9 | Shirahatti | 2 | 2 | 0:00 | 0:00 | 27:20 | 10:05 | 37:25 | 149:55 | 37:25 | 18:42 | 97.4854 | 97.4854 | 149:55 | 74:58 | 97.4399 | 97.4399
10 | Laxmeshwar | 6 | 6 | 0:00 | 0:00 | 125:35 | 54:45 | 180:20 | 794:25 | 180:20 | 30:03 | 95.9603 | 95.9603 | 794:25 | 132:24 | 95.478 | 95.478
11 | Naregal | 1 | 1 | 3:10 | 16:40 | 10:55 | 3:55 | 14:50 | 67:40 | 18:00 | 18:00 | 98.0063 | 97.5806 | 84:20 | 84:20 | 97.689 | 97.1198
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 35:50 | 14:15 | 50:05 | 220:30 | 50:05 | 25:02 | 96.6342 | 96.6342 | 220:30 | 110:15 | 96.2346 | 96.2346
13 | Ron | 3 | 3 | 13:10 | 31:40 | 30:10 | 23:50 | 54:00 | 181:06 | 67:10 | 22:23 | 97.5806 | 96.9907 | 212:46 | 70:55 | 97.9383 | 97.5778
14 | Mundaragi | 3 | 3 | 17:05 | 41:15 | 44:15 | 31:10 | 75:25 | 410:35 | 92:30 | 30:50 | 96.6211 | 95.8557 | 451:50 | 150:37 | 95.3258 | 94.8562
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 30:33 | 29:57 | 60:30 | 215:45 | 60:30 | 60:30 | 91.8683 | 91.8683 | 215:45 | 215:45 | 92.6315 | 92.6315
16 | G.C.T.M | 1 | 1 | 23:15 | 65:05 | 21:35 | 4:40 | 26:15 | 152:05 | 49:30 | 49:30 | 96.4718 | 93.3468 | 217:10 | 217:10 | 94.8059 | 92.5831
17 | F.C.S.M | 2 | 2 | 40:45 | 117:20 | 16:35 | 14:25 | 31:00 | 185:35 | 71:45 | 35:52 | 97.9167 | 95.1781 | 302:55 | 151:28 | 96.8309 | 94.8272
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 1:42 | 11:22 | 13:04 | 69:53 | 13:04 | 13:04 | 98.2437 | 98.2437 | 69:53 | 69:53 | 97.6133 | 97.6133
19 | Hole-Alur | 1 | 1 | 2:55 | 39:20 | 16:20 | 3:15 | 19:35 | 114:05 | 22:30 | 22:30 | 97.3678 | 96.9758 | 153:25 | 153:25 | 96.1037 | 94.7604
20 | Savanur | 2 | 2 | 1:30 | 8:30 | 55:45 | 9:35 | 65:20 | 174:10 | 66:50 | 33:25 | 95.6093 | 95.5085 | 182:40 | 91:20 | 97.0258 | 96.8807
21 | Shiggaon | 2 | 2 | 8:20 | 54:20 | 22:45 | 22:50 | 45:35 | 144:35 | 53:55 | 26:58 | 96.9366 | 96.3766 | 198:55 | 99:28 | 97.531 | 96.6032
22 | Bankapur | 1 | 1 | 11:45 | 43:00 | 12:50 | 3:10 | 16:00 | 49:25 | 27:45 | 27:45 | 97.8495 | 96.2702 | 92:25 | 92:25 | 98.3123 | 96.8437
23 | Hangal | 2 | 2 | 14:40 | 15:50 | 32:20 | 11:05 | 43:25 | 270:50 | 58:05 | 29:02 | 97.0822 | 96.0966 | 286:40 | 143:20 | 95.3751 | 95.1047
24 | Ranebennur | 16 | 16 | 1:30 | 42:51 | 322:53 | 92:23 | 415:16 | 1234:39 | 416:46 | 26:03 | 96.5115 | 96.4989 | 1277:30 | 79:51 | 97.3646 | 97.2731
25 | Halageri | 2 | 2 | 14:00 | 129:30 | 9:50 | 4:20 | 14:10 | 48:30 | 28:10 | 14:05 | 99.0479 | 98.1071 | 178:00 | 89:00 | 99.1718 | 96.9604
26 | Tuminakatti | 3 | 3 | 5:55 | 12:40 | 98:20 | 1:45 | 100:05 | 313:25 | 106:00 | 35:20 | 95.516 | 95.2509 | 326:05 | 108:42 | 96.432 | 96.2878
27 | Kahanderayanahalli | 2 | 2 | 8:05 | 82:30 | 41:25 | 26:30 | 67:55 | 320:24 | 76:00 | 38:00 | 95.4357 | 94.8925 | 402:54 | 201:27 | 94.5287 | 93.1199
28 | Rattihalli | 1 | 1 | 2:15 | 6:00 | 16:05 | 5:00 | 21:05 | 88:05 | 23:20 | 23:20 | 97.1662 | 96.8638 | 94:05 | 94:05 | 96.9917 | 96.7868
29 | Hirekerur | 3 | 3 | 13:35 | 128:10 | 59:05 | 43:55 | 103:00 | 414:20 | 116:35 | 38:52 | 95.3853 | 94.7767 | 542:30 | 180:50 | 95.2831 | 93.824
30 | Byadagi | 6 | 6 | 25:10 | 124:10 | 103:30 | 96:40 | 200:10 | 631:35 | 225:20 | 37:33 | 95.516 | 94.9522 | 755:45 | 125:57 | 96.4049 | 95.6981
31 | Sirsi | 5 | 5 | 39:10 | 129:48 | 28:35 | 43:55 | 72:30 | 206:19 | 111:40 | 22:20 | 98.0511 | 96.9982 | 336:07 | 67:13 | 98.5907 | 97.7041
32 | Yellapur | 3 | 3 | 11:05 | 105:29 | 26:55 | 22:24 | 49:19 | 343:08 | 60:24 | 20:08 | 97.7905 | 97.2939 | 448:37 | 149:32 | 96.0937 | 94.8928
33 | Mundagod | 3 | 3 | 15:30 | 32:17 | 59:35 | 19:10 | 78:45 | 268:30 | 94:15 | 31:25 | 96.4718 | 95.7773 | 300:47 | 100:16 | 96.9433 | 96.5758
34 | Siddapur | 2 | 2 | 0:00 | 4:50 | 13:55 | 30:35 | 44:30 | 166:25 | 44:30 | 22:15 | 97.0094 | 97.0094 | 171:15 | 85:38 | 97.1582 | 97.0756
35 | Dandeli | 8 | 8 | 18:12 | 135:52 | 43:01 | 54:39 | 97:40 | 687:27 | 115:52 | 14:29 | 98.3591 | 98.0533 | 823:19 | 102:55 | 97.0652 | 96.4852
36 | Haliyal | 3 | 3 | 1:00 | 13:15 | 36:55 | 13:13 | 50:08 | 174:10 | 51:08 | 17:03 | 97.7539 | 97.7091 | 187:25 | 62:28 | 98.0172 | 97.8664
37 | Ankola | 3 | 3 | 58:48 | 215:48 | 29:07 | 38:54 | 68:01 | 110:21 | 126:49 | 42:16 | 96.9527 | 94.3182 | 326:09 | 108:43 | 98.7437 | 96.287
38 | Kumta | 3 | 3 | 1:57 | 31:36 | 30:02 | 21:30 | 51:32 | 212:35 | 53:29 | 17:50 | 97.6912 | 97.6038 | 244:11 | 81:24 | 97.5799 | 97.2201
39 | Gokarna | 1 | 1 | 15:15 | 72:34 | 1:30 | 2:20 | 3:50 | 23:08 | 19:05 | 19:05 | 99.4848 | 97.435 | 95:42 | 95:42 | 99.2099 | 96.7316
40 | Kasargod | 1 | 1 | 22:17 | 70:46 | 10:20 | 5:25 | 15:45 | 61:10 | 38:02 | 38:02 | 97.8831 | 94.888 | 131:56 | 131:56 | 97.911 | 95.4941
41 | Honnavar | 3 | 3 | 16:54 | 139:00 | 51:53 | 30:59 | 82:52 | 211:42 | 99:46 | 33:15 | 96.2873 | 95.5302 | 350:42 | 116:54 | 97.5899 | 96.0075
42 | Murdeshwar | 4 | 4 | 26:12 | 175:28 | 72:41 | 49:04 | 121:45 | 373:21 | 147:57 | 36:59 | 95.9089 | 95.0286 | 548:49 | 137:12 | 96.8122 | 95.3141
43 | Bhatkal | 2 | 2 | 16:12 | 70:30 | 28:18 | 6:30 | 34:48 | 184:04 | 51:00 | 25:30 | 97.6613 | 96.5726 | 254:34 | 127:17 | 96.8568 | 95.6529
44 | Khanapur | 2 | 2 | 0:00 | 17:52 | 26:00 | 11:20 | 37:20 | 143:45 | 37:20 | 18:40 | 97.491 | 97.491 | 161:37 | 80:48 | 97.5453 | 97.2402
45 | Bailhongal | 3 | 3 | 0:00 | 25:06 | 33:55 | 20:10 | 54:05 | 151:28 | 54:05 | 18:02 | 97.5769 | 97.5769 | 176:34 | 58:51 | 98.2757 | 97.9899
46 | Soundatti | 3 | 3 | 0:00 | 14:20 | 25:13 | 8:13 | 33:26 | 214:57 | 33:26 | 11:09 | 98.5021 | 98.5021 | 229:17 | 76:26 | 97.5529 | 97.3898
47 | Ramdurg | 2 | 2 | 0:00 | 18:10 | 45:40 | 7:10 | 52:50 | 205:15 | 52:50 | 26:25 | 96.4494 | 96.4494 | 223:25 | 111:42 | 96.495 | 96.1848
48 | Gokak | 7 | 7 | 42:00 | 131:55 | 142:30 | 53:00 | 195:30 | 845:20 | 237:30 | 33:56 | 96.2462 | 95.4397 | 977:15 | 139:36 | 95.8756 | 95.232
49 | Mudalagi | 2 | 2 | 8:50 | 36:10 | 27:10 | 4:00 | 31:10 | 134:15 | 40:00 | 20:00 | 97.9055 | 97.3118 | 170:25 | 85:12 | 97.7075 | 97.0899
50 | Konnur | 1 | 1 | 0:00 | 3:00 | 15:00 | 3:40 | 18:40 | 93:45 | 18:40 | 18:40 | 97.491 | 97.491 | 96:45 | 96:45 | 96.7982 | 96.6957
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 18:55 | 3:45 | 22:40 | 102:09 | 22:40 | 22:40 | 96.9534 | 96.9534 | 102:09 | 102:09 | 96.5113 | 96.5113
52 | Kudachi | 1 | 1 | 6:30 | 8:05 | 43:20 | 6:50 | 50:10 | 150:45 | 56:40 | 56:40 | 93.2572 | 92.3835 | 158:50 | 158:50 | 94.8514 | 94.5754
53 | Athani | 6 | 6 | 11:02 | 53:22 | 66:33 | 57:05 | 123:38 | 474:44 | 134:40 | 22:27 | 97.2304 | 96.9833 | 528:06 | 88:01 | 97.2977 | 96.994
54 | Chikkodi | 2 | 2 | 0:00 | 1:40 | 25:30 | 6:20 | 31:50 | 81:10 | 31:50 | 15:55 | 97.8607 | 97.8607 | 82:50 | 41:25 | 98.614 | 98.5855
55 | Nippani | 5 | 5 | 0:00 | 79:35 | 41:25 | 19:20 | 60:45 | 290:00 | 60:45 | 12:09 | 98.3669 | 98.3669 | 369:35 | 73:55 | 98.0191 | 97.4755
56 | Sadalaga | 1 | 1 | 0:00 | 2:30 | 20:40 | 0:35 | 21:15 | 80:01 | 21:15 | 21:15 | 97.1438 | 97.1438 | 82:31 | 82:31 | 97.2672 | 97.1818
57 | Muddebihal | 2 | 2 | 2:10 | 48:50 | 52:25 | 20:20 | 72:45 | 286:55 | 74:55 | 37:28 | 95.1109 | 94.9653 | 335:45 | 167:53 | 95.1005 | 94.2666
58 | Talikot | 1 | 1 | 2:35 | 101:00 | 33:35 | 53:00 | 86:35 | 280:15 | 89:10 | 89:10 | 88.3625 | 88.0152 | 381:15 | 381:15 | 90.4286 | 86.9792
59 | B.Bagewadi | 1 | 1 | 3:52 | 24:17 | 6:10 | 9:59 | 16:09 | 49:50 | 20:01 | 20:01 | 97.8293 | 97.3096 | 74:07 | 74:07 | 98.298 | 97.4687
60 | Indi | 1 | 1 | 1:01 | 7:06 | 23:06 | 1:48 | 24:54 | 77:11 | 25:55 | 25:55 | 96.6532 | 96.5166 | 84:17 | 84:17 | 97.364 | 97.1215
61 | Sindagi | 2 | 2 | 4:40 | 123:50 | 16:20 | 18:30 | 34:50 | 104:50 | 39:30 | 19:45 | 97.6591 | 97.3454 | 228:40 | 114:20 | 98.2098 | 96.0952
62 | Guledgudda | 1 | 1 | 0:00 | 0:00 | 15:07 | 25:05 | 40:12 | 128:20 | 40:12 | 40:12 | 94.5968 | 94.5968 | 128:20 | 128:20 | 95.617 | 95.617
63 | Ilkal | 8 | 8 | 47:47 | 218:50 | 127:36 | 111:38 | 239:14 | 753:26 | 287:01 | 35:53 | 95.9806 | 95.1778 | 972:16 | 121:32 | 96.7835 | 95.8493
64 | Kerur | 2 | 2 | 0:45 | 6:18 | 32:29 | 8:03 | 40:32 | 114:57 | 41:17 | 20:38 | 97.276 | 97.2256 | 121:15 | 60:38 | 98.0371 | 97.9295
65 | Hungund | 3 | 3 | 7:30 | 54:40 | 67:07 | 24:29 | 91:36 | 387:55 | 99:06 | 33:02 | 95.8961 | 95.56 | 442:35 | 147:32 | 95.5838 | 94.9615
66 | GADDANKERI | 4 | 4 | 2:39 | 16:42 | 10:50 | 2:55 | 13:45 | 127:49 | 16:24 | 4:06 | 99.538 | 99.4489 | 144:31 | 36:08 | 98.9087 | 98.7661
67 | RAMPUR | 1 | 1 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 100 | 100 | 0:00 | 0:00 | 100 | 100
68 | KALADAGI | 2 | 2 | 0:00 | 0:05 | 29:54 | 18:48 | 48:42 | 128:07 | 48:42 | 24:21 | 96.7272 | 96.7272 | 128:12 | 64:06 | 97.8122 | 97.8108
69 | ACHANUR | 1 | 1 | 0:33 | 0:33 | 29:15 | 66:24 | 95:39 | 256:39 | 96:12 | 96:12 | 87.1438 | 87.0699 | 257:12 | 257:12 | 91.2346 | 91.2158
70 | SHIRUR | 1 | 1 | 12:30 | 22:00 | 0:00 | 0:00 | 0:00 | 28:10 | 12:30 | 12:30 | 100 | 98.3199 | 50:10 | 50:10 | 99.038 | 98.2867
71 | BADAMI | 1 | 1 | 1:03 | 6:19 | 26:45 | 19:46 | 46:31 | 97:11 | 47:34 | 47:34 | 93.7478 | 93.6066 | 103:30 | 103:30 | 96.6809 | 96.4652
72 | KULAGERI | 1 | 1 | 0:13 | 1:58 | 13:35 | 0:55 | 14:30 | 21:00 | 14:43 | 14:43 | 98.0511 | 98.022 | 22:58 | 22:58 | 99.2828 | 99.2156
73 | Jamkhandi | 5 | 5 | 4:59 | 34:44 | 92:30 | 11:11 | 103:41 | 436:18 | 108:40 | 21:44 | 97.2128 | 97.0789 | 471:02 | 94:12 | 97.0198 | 96.7826
74 | Mahalingapur | 2 | 2 | 1:28 | 31:30 | 35:26 | 6:37 | 42:03 | 143:40 | 43:31 | 21:46 | 97.1741 | 97.0755 | 175:10 | 87:35 | 97.5467 | 97.0088
75 | Rabakavi | 2 | 2 | 1:30 | 23:50 | 22:05 | 6:45 | 28:50 | 114:19 | 30:20 | 15:10 | 98.0623 | 97.9615 | 138:09 | 69:04 | 98.0479 | 97.6409
76 | Banhatti | 2 | 2 | 4:20 | 30:35 | 20:30 | 3:20 | 23:50 | 103:48 | 28:10 | 14:05 | 98.3983 | 98.1071 | 134:23 | 67:12 | 98.2275 | 97.7052
77 | Terdal | 1 | 1 | 3:55 | 15:46 | 24:03 | 4:15 | 28:18 | 93:55 | 32:13 | 32:13 | 96.1962 | 95.6698 | 109:41 | 109:41 | 96.7925 | 96.254
78 | Mudhol | 3 | 3 | 0:00 | 13:41 | 35:24 | 4:28 | 39:52 | 228:07 | 39:52 | 13:17 | 98.2139 | 98.2139 | 241:48 | 80:36 | 97.403 | 97.2473
79 | Bilagi | 1 | 1 | 0:45 | 8:25 | 17:03 | 3:04 | 20:07 | 114:37 | 20:52 | 20:52 | 97.2961 | 97.1953 | 123:02 | 123:02 | 96.0855 | 95.798
80 | Lokapur | 2 | 2 | 0:00 | 6:40 | 17:00 | 15:00 | 32:00 | 257:30 | 32:00 | 16:00 | 97.8495 | 97.8495 | 264:10 | 132:05 | 95.6028 | 95.489
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of August-2019
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Aug-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 44:55 | 348:19 | 903:48 | 681:42 | 1585:30 | 4829:19 | 1630:25 | 20:38 | 97.3025 | 97.2261 | 5177:38 | 65:32 | 98.3352 | 98.2152
2 | Dharwad(R) | 18 | 18 | 50:00 | 127:16 | 317:45 | 398:26 | 716:11 | 2392:12 | 766:11 | 42:34 | 94.6522 | 94.2788 | 2519:28 | 139:58 | 96.3807 | 96.1882
3 | Kundagol | 1 | 1 | 13:15 | 156:55 | 3:25 | 1:00 | 4:25 | 79:35 | 17:40 | 17:40 | 99.4064 | 97.6254 | 236:30 | 236:30 | 97.8327 | 93.5594
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 8:24 | 27:00 | 35:24 | 106:36 | 35:24 | 35:24 | 95.2419 | 95.2419 | 106:36 | 106:36 | 97.0969 | 97.0969
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 15:35 | 25:00 | 40:35 | 190:43 | 40:35 | 40:35 | 94.5453 | 94.5453 | 190:43 | 190:43 | 94.8062 | 94.8062
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 117:45 | 68:00 | 185:45 | 488:40 | 185:45 | 92:52 | 87.5168 | 87.5168 | 488:40 | 244:20 | 93.346 | 93.346
7 | Alnavar | 1 | 1 | 2:40 | 56:40 | 27:50 | 23:15 | 51:05 | 128:10 | 53:45 | 53:45 | 93.134 | 92.7755 | 184:50 | 184:50 | 96.5096 | 94.9664
8 | Naragund | 2 | 2 | 9:50 | 38:00 | 36:25 | 56:30 | 92:55 | 425:05 | 102:45 | 51:22 | 93.7556 | 93.0948 | 463:05 | 231:32 | 94.2118 | 93.6944
9 | Shirahatti | 2 | 2 | 0:00 | 0:00 | 39:05 | 63:00 | 102:05 | 252:00 | 102:05 | 51:02 | 93.1396 | 93.1396 | 252:00 | 126:00 | 96.5686 | 96.5686
10 | Laxmeshwar | 6 | 6 | 0:00 | 0:00 | 154:26 | 78:23 | 232:49 | 1027:14 | 232:49 | 38:48 | 94.7846 | 94.7846 | 1027:14 | 171:12 | 95.3375 | 95.3375
11 | Naregal | 1 | 1 | 1:15 | 17:55 | 10:10 | 3:30 | 13:40 | 81:20 | 14:55 | 14:55 | 98.1631 | 97.9951 | 99:15 | 99:15 | 97.785 | 97.2971
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 30:15 | 22:40 | 52:55 | 273:25 | 52:55 | 26:28 | 96.4438 | 96.4438 | 273:25 | 136:42 | 96.277 | 96.277
13 | Ron | 3 | 3 | 8:40 | 40:20 | 22:45 | 15:00 | 37:45 | 218:51 | 46:25 | 15:28 | 98.3087 | 97.9204 | 259:11 | 86:24 | 98.0133 | 97.6472
14 | Mundaragi | 3 | 3 | 0:00 | 41:15 | 38:30 | 68:50 | 107:20 | 517:55 | 107:20 | 35:47 | 95.1912 | 95.1912 | 559:10 | 186:23 | 95.2985 | 94.924
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 35:06 | 16:49 | 51:55 | 267:40 | 51:55 | 51:55 | 93.022 | 93.022 | 267:40 | 267:40 | 92.7106 | 92.7106
16 | G.C.T.M | 1 | 1 | 17:45 | 82:50 | 24:15 | 20:25 | 44:40 | 196:45 | 62:25 | 62:25 | 93.9964 | 91.6107 | 279:35 | 279:35 | 94.6419 | 92.3861
17 | F.C.S.M | 2 | 2 | 30:55 | 148:15 | 43:20 | 5:00 | 48:20 | 233:55 | 79:15 | 39:38 | 96.7518 | 94.6741 | 382:10 | 191:05 | 96.8149 | 94.7962
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 17:51 | 6:14 | 24:05 | 93:58 | 24:05 | 24:05 | 96.763 | 96.763 | 93:58 | 93:58 | 97.441 | 97.441
19 | Hole-Alur | 1 | 1 | 7:50 | 47:10 | 42:00 | 7:55 | 49:55 | 164:00 | 57:45 | 57:45 | 93.2908 | 92.2379 | 211:10 | 211:10 | 95.5338 | 94.2493
20 | Savanur | 2 | 2 | 2:50 | 11:20 | 20:15 | 15:30 | 35:45 | 209:55 | 38:35 | 19:18 | 97.5974 | 97.407 | 221:15 | 110:38 | 97.1417 | 96.9873
21 | Shiggaon | 2 | 2 | 29:00 | 83:20 | 42:55 | 34:25 | 77:20 | 221:55 | 106:20 | 53:10 | 94.8029 | 92.8539 | 305:15 | 152:38 | 96.9783 | 95.8435
22 | Bankapur | 1 | 1 | 11:10 | 54:10 | 13:40 | 8:30 | 22:10 | 71:35 | 33:20 | 33:20 | 97.0206 | 95.5197 | 125:45 | 125:45 | 98.0506 | 96.5754
23 | Hangal | 2 | 2 | 2:50 | 18:40 | 63:15 | 25:40 | 88:55 | 359:45 | 91:45 | 45:52 | 94.0244 | 93.834 | 378:25 | 189:12 | 95.1014 | 94.8473
24 | Ranebennur | 16 | 16 | 4:40 | 47:31 | 263:21 | 144:49 | 408:10 | 1642:49 | 412:50 | 25:48 | 96.5712 | 96.532 | 1690:20 | 105:39 | 97.2038 | 97.1229
25 | Halageri | 2 | 2 | 12:20 | 141:50 | 13:40 | 2:10 | 15:50 | 64:20 | 28:10 | 14:05 | 98.9359 | 98.1071 | 206:10 | 103:05 | 99.124 | 97.1927
26 | Tuminakatti | 3 | 3 | 1:30 | 14:10 | 90:00 | 2:10 | 92:10 | 405:35 | 93:40 | 31:13 | 95.8707 | 95.8035 | 419:45 | 139:55 | 96.3182 | 96.1896
27 | Kahanderayanahalli | 2 | 2 | 15:00 | 97:30 | 40:10 | 51:45 | 91:55 | 412:19 | 106:55 | 53:27 | 93.8228 | 92.8147 | 509:49 | 254:54 | 94.3857 | 93.0581
28 | Rattihalli | 1 | 1 | 0:45 | 6:45 | 15:20 | 6:10 | 21:30 | 109:35 | 22:15 | 22:15 | 97.1102 | 97.0094 | 116:20 | 116:20 | 97.0157 | 96.8319
29 | Hirekerur | 3 | 3 | 30:40 | 158:50 | 92:30 | 63:10 | 155:40 | 570:00 | 186:20 | 62:07 | 93.0257 | 91.6517 | 728:50 | 242:57 | 94.8257 | 93.3839
30 | Byadagi | 6 | 6 | 22:05 | 146:15 | 131:40 | 576:10 | 707:50 | 1339:25 | 729:55 | 121:39 | 84.1435 | 83.6488 | 1485:40 | 247:37 | 93.9206 | 93.2568
31 | Sirsi | 5 | 5 | 40:50 | 170:38 | 54:05 | 29:40 | 83:45 | 290:04 | 124:35 | 24:55 | 97.7487 | 96.651 | 460:42 | 92:08 | 98.4201 | 97.4907
32 | Yellapur | 3 | 3 | 52:15 | 157:44 | 61:15 | 32:45 | 94:00 | 437:08 | 146:15 | 48:45 | 95.7885 | 93.4476 | 594:52 | 198:17 | 96.0318 | 94.6
33 | Mundagod | 3 | 3 | 9:30 | 41:47 | 56:20 | 113:50 | 170:10 | 438:40 | 179:40 | 59:53 | 92.376 | 91.9504 | 480:27 | 160:09 | 96.0179 | 95.6386
34 | Siddapur | 2 | 2 | 0:00 | 4:50 | 20:55 | 38:10 | 59:05 | 225:30 | 59:05 | 29:32 | 96.0293 | 96.0293 | 230:20 | 115:10 | 96.9295 | 96.8637
35 | Dandeli | 8 | 8 | 86:24 | 222:16 | 53:01 | 54:39 | 107:40 | 795:07 | 194:04 | 24:15 | 98.1911 | 96.7395 | 1017:23 | 127:10 | 97.2933 | 96.5367
36 | Haliyal | 3 | 3 | 2:52 | 16:07 | 34:45 | 12:44 | 47:29 | 221:39 | 50:21 | 16:47 | 97.8726 | 97.7442 | 237:46 | 79:15 | 97.9879 | 97.8416
37 | Ankola | 3 | 3 | 40:18 | 256:06 | 24:59 | 73:49 | 98:48 | 209:09 | 139:06 | 46:22 | 95.5735 | 93.7679 | 465:15 | 155:05 | 98.1014 | 95.7766
38 | Kumta | 3 | 3 | 14:00 | 45:36 | 39:09 | 33:07 | 72:16 | 284:51 | 86:16 | 28:45 | 96.7622 | 96.135 | 330:27 | 110:09 | 97.4142 | 97.0003
39 | Gokarna | 1 | 1 | 60:21 | 132:55 | 10:30 | 0:30 | 11:00 | 34:08 | 71:21 | 71:21 | 98.5215 | 90.4099 | 167:03 | 167:03 | 99.0704 | 95.4507
40 | Kasargod | 1 | 1 | 20:08 | 90:54 | 27:20 | 13:50 | 41:10 | 102:20 | 61:18 | 61:18 | 94.4668 | 91.7608 | 193:14 | 193:14 | 97.2131 | 94.7377
41 | Honnavar | 3 | 3 | 14:27 | 153:27 | 55:05 | 33:46 | 88:51 | 300:33 | 103:18 | 34:26 | 96.0193 | 95.3719 | 454:00 | 151:20 | 97.2717 | 95.8787
42 | Murdeshwar | 4 | 4 | 19:24 | 194:52 | 92:44 | 61:55 | 154:39 | 528:00 | 174:03 | 43:31 | 94.8034 | 94.1515 | 722:52 | 180:43 | 96.4052 | 95.0785
43 | Bhatkal | 2 | 2 | 33:40 | 104:10 | 35:15 | 48:03 | 83:18 | 267:22 | 116:58 | 58:29 | 94.4019 | 92.1393 | 371:32 | 185:46 | 96.3594 | 94.941
44 | Khanapur | 2 | 2 | 3:10 | 21:02 | 27:55 | 21:38 | 49:33 | 193:18 | 52:43 | 26:22 | 96.67 | 96.4572 | 214:20 | 107:10 | 97.3679 | 97.0815
45 | Bailhongal | 3 | 3 | 6:45 | 31:51 | 25:45 | 14:00 | 39:45 | 191:13 | 46:30 | 15:30 | 98.2191 | 97.9167 | 223:04 | 74:21 | 98.2642 | 97.9751
46 | Soundatti | 3 | 3 | 5:57 | 20:17 | 62:29 | 552:19 | 614:48 | 829:45 | 620:45 | 206:55 | 72.4552 | 72.1886 | 850:02 | 283:21 | 92.4678 | 92.2836
47 | Ramdurg | 2 | 2 | 3:10 | 21:20 | 51:20 | 12:20 | 63:40 | 268:55 | 66:50 | 33:25 | 95.7213 | 95.5085 | 290:15 | 145:08 | 96.3383 | 96.0478
48 | Gokak | 7 | 7 | 5:05 | 137:00 | 387:25 | 107:55 | 495:20 | 1340:40 | 500:25 | 71:29 | 90.489 | 90.3914 | 1477:40 | 211:06 | 94.7842 | 94.2512
49 | Mudalagi | 2 | 2 | 4:20 | 40:30 | 49:20 | 4:00 | 53:20 | 187:35 | 57:40 | 28:50 | 96.4158 | 96.1246 | 228:05 | 114:02 | 97.4458 | 96.8943
50 | Konnur | 1 | 1 | 0:00 | 3:00 | 54:40 | 12:15 | 66:55 | 160:40 | 66:55 | 66:55 | 91.0058 | 91.0058 | 163:40 | 163:40 | 95.6245 | 95.5428
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 29:55 | 3:35 | 33:30 | 135:39 | 33:30 | 33:30 | 95.4973 | 95.4973 | 135:39 | 135:39 | 96.3058 | 96.3058
52 | Kudachi | 1 | 1 | 0:40 | 8:45 | 87:20 | 8:15 | 95:35 | 246:20 | 96:15 | 96:15 | 87.1528 | 87.0632 | 255:05 | 255:05 | 93.2916 | 93.0533
53 | Athani | 6 | 6 | 34:18 | 87:40 | 92:51 | 41:10 | 134:01 | 608:45 | 168:19 | 28:03 | 96.9978 | 96.2295 | 696:25 | 116:04 | 97.237 | 96.8391
54 | Chikkodi | 2 | 2 | 0:00 | 1:40 | 9:45 | 20:10 | 29:55 | 111:05 | 29:55 | 14:57 | 97.9895 | 97.9895 | 112:45 | 56:22 | 98.4874 | 98.4647
55 | Nippani | 5 | 5 | 0:00 | 79:35 | 56:20 | 13:45 | 70:05 | 360:05 | 70:05 | 14:01 | 98.116 | 98.116 | 439:40 | 87:56 | 98.0388 | 97.6053
56 | Sadalaga | 1 | 1 | 0:00 | 2:30 | 56:45 | 13:20 | 70:05 | 150:06 | 70:05 | 70:05 | 90.5802 | 90.5802 | 152:36 | 152:36 | 95.9123 | 95.8442
57 | Muddebihal | 2 | 2 | 11:40 | 60:30 | 59:40 | 3:55 | 63:35 | 350:30 | 75:15 | 37:38 | 95.7269 | 94.9429 | 411:00 | 205:30 | 95.2274 | 94.4036
58 | Talikot | 1 | 1 | 13:15 | 114:15 | 30:55 | 12:20 | 43:15 | 323:30 | 56:30 | 56:30 | 94.1868 | 92.4059 | 437:45 | 437:45 | 91.1901 | 88.0787
59 | B.Bagewadi | 1 | 1 | 3:04 | 27:21 | 24:45 | 0:00 | 24:45 | 74:35 | 27:49 | 27:49 | 96.6734 | 96.2612 | 101:56 | 101:56 | 97.9689 | 97.224
60 | Indi | 1 | 1 | 0:20 | 7:26 | 12:33 | 1:46 | 14:19 | 91:30 | 14:39 | 14:39 | 98.0757 | 98.0309 | 98:56 | 98:56 | 97.5082 | 97.3057
61 | Sindagi | 2 | 2 | 5:20 | 129:10 | 23:20 | 10:25 | 33:45 | 138:35 | 39:05 | 19:32 | 97.7319 | 97.3734 | 267:45 | 133:52 | 98.113 | 96.3542
62 | Guledgudda | 1 | 1 | 0:00 | 0:00 | 27:55 | 9:41 | 37:36 | 165:56 | 37:36 | 37:36 | 94.9462 | 94.9462 | 165:56 | 165:56 | 95.4811 | 95.4811
63 | Ilkal | 8 | 8 | 74:44 | 293:34 | 70:57 | 164:09 | 235:06 | 988:32 | 309:50 | 38:44 | 96.0501 | 94.7945 | 1282:06 | 160:16 | 96.6349 | 95.6356
64 | Kerur | 2 | 2 | 2:38 | 8:56 | 13:20 | 2:15 | 15:35 | 130:32 | 18:13 | 9:06 | 98.9527 | 98.7758 | 139:28 | 69:44 | 98.2226 | 98.1009
65 | Hungund | 3 | 3 | 16:52 | 71:32 | 84:57 | 21:14 | 106:11 | 494:06 | 123:03 | 41:01 | 95.2427 | 94.487 | 565:38 | 188:33 | 95.5147 | 94.8653
66 | GADDANKERI | 4 | 4 | 13:26 | 30:08 | 13:00 | 23:50 | 36:50 | 164:39 | 50:16 | 12:34 | 98.7623 | 98.3109 | 194:47 | 48:42 | 98.879 | 98.6739
67 | RAMPUR | 1 | 1 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 100 | 100 | 0:00 | 0:00 | 100 | 100
68 | KALADAGI | 2 | 2 | 0:00 | 0:05 | 83:12 | 4:27 | 87:39 | 215:46 | 87:39 | 43:50 | 94.1095 | 94.1095 | 215:51 | 107:56 | 97.062 | 97.0609
69 | ACHANUR | 1 | 1 | 0:03 | 0:36 | 22:24 | 5:09 | 27:33 | 284:12 | 27:36 | 27:36 | 96.297 | 96.2903 | 284:48 | 284:48 | 92.2603 | 92.244
70 | SHIRUR | 1 | 1 | 8:06 | 30:06 | 10:39 | 0:15 | 10:54 | 39:04 | 19:00 | 19:00 | 98.5349 | 97.4462 | 69:10 | 69:10 | 98.9361 | 98.1164
71 | BADAMI | 1 | 1 | 0:00 | 6:19 | 19:51 | 8:18 | 28:09 | 125:20 | 28:09 | 28:09 | 96.2164 | 96.2164 | 131:39 | 131:39 | 96.5868 | 96.4148
72 | KULAGERI | 1 | 1 | 0:33 | 2:31 | 3:15 | 0:00 | 3:15 | 24:15 | 3:48 | 3:48 | 99.5632 | 99.4892 | 26:46 | 26:46 | 99.3396 | 99.2711
73 | Jamkhandi | 5 | 5 | 0:00 | 34:44 | 62:10 | 21:11 | 83:21 | 519:39 | 83:21 | 16:40 | 97.7594 | 97.7594 | 554:23 | 110:53 | 97.1697 | 96.9805
74 | Mahalingapur | 2 | 2 | 1:40 | 33:10 | 37:10 | 3:17 | 40:27 | 184:07 | 42:07 | 21:04 | 97.2816 | 97.1696 | 217:17 | 108:38 | 97.493 | 97.0413
75 | Rabakavi | 2 | 2 | 4:00 | 27:50 | 20:33 | 4:04 | 24:37 | 138:56 | 28:37 | 14:19 | 98.3457 | 98.0768 | 166:46 | 83:23 | 98.1082 | 97.7292
76 | Banhatti | 2 | 2 | 0:00 | 30:35 | 34:42 | 1:09 | 35:51 | 139:39 | 35:51 | 17:56 | 97.5907 | 97.5907 | 170:14 | 85:07 | 98.0984 | 97.682
77 | Terdal | 1 | 1 | 2:03 | 17:49 | 27:05 | 1:55 | 29:00 | 122:55 | 31:03 | 31:03 | 96.1022 | 95.8266 | 140:44 | 140:44 | 96.6526 | 96.1674
78 | Mudhol | 3 | 3 | 7:55 | 21:36 | 88:57 | 14:00 | 102:57 | 331:04 | 110:52 | 36:57 | 95.3875 | 95.0329 | 352:40 | 117:33 | 96.9947 | 96.7986
79 | Bilagi | 1 | 1 | 0:35 | 9:00 | 13:50 | 1:20 | 15:10 | 129:47 | 15:45 | 15:45 | 97.9615 | 97.8831 | 138:47 | 138:47 | 96.4656 | 96.2205
80 | Lokapur | 2 | 2 | 0:00 | 6:40 | 39:20 | 13:30 | 52:50 | 310:20 | 52:50 | 26:25 | 96.4494 | 96.4494 | 317:00 | 158:30 | 95.7743 | 95.6836
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of September-2019
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of September-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 116:30 | 464:49 | 549:26 | 416:18 | 965:44 | 5795:03 | 1082:14 | 13:42 | 98.3022 | 98.0973 | 6259:52 | 79:14 | 98.3298 | 98.1958
2 | Dharwad(R) | 18 | 18 | 28:12 | 155:28 | 324:51 | 183:46 | 508:37 | 2900:49 | 536:49 | 29:49 | 96.0755 | 95.8579 | 3056:17 | 169:48 | 96.3307 | 96.134
3 | Kundagol | 1 | 1 | 3:00 | 159:55 | 7:10 | 4:15 | 11:25 | 91:00 | 14:25 | 14:25 | 98.4144 | 97.9977 | 250:55 | 250:55 | 97.9281 | 94.287
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 20:37 | 9:26 | 30:03 | 136:39 | 30:03 | 30:03 | 95.8264 | 95.8264 | 136:39 | 136:39 | 96.8887 | 96.8887
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 24:20 | 4:55 | 29:15 | 219:58 | 29:15 | 29:15 | 95.9375 | 95.9375 | 219:58 | 219:58 | 94.9917 | 94.9917
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 35:20 | 25:10 | 60:30 | 549:10 | 60:30 | 30:15 | 95.7986 | 95.7986 | 549:10 | 274:35 | 93.7481 | 93.7481
7 | Alnavar | 1 | 1 | 3:50 | 60:30 | 14:35 | 8:40 | 23:15 | 151:25 | 27:05 | 27:05 | 96.7708 | 96.2384 | 211:55 | 211:55 | 96.5524 | 95.1749
8 | Naragund | 2 | 2 | 3:20 | 41:20 | 30:05 | 34:45 | 64:50 | 489:55 | 68:10 | 34:05 | 95.4977 | 95.2662 | 531:15 | 265:38 | 94.4226 | 93.9521
9 | Shirahatti | 2 | 2 | 0:00 | 0:00 | 23:05 | 3:25 | 26:30 | 278:30 | 26:30 | 13:15 | 98.1597 | 98.1597 | 278:30 | 139:15 | 96.8295 | 96.8295
10 | Laxmeshwar | 6 | 6 | 0:00 | 0:00 | 57:51 | 24:04 | 81:55 | 1109:09 | 81:55 | 13:39 | 98.1038 | 98.1038 | 1109:09 | 184:52 | 95.791 | 95.791
11 | Naregal | 1 | 1 | 9:20 | 27:15 | 17:45 | 5:40 | 23:25 | 104:45 | 32:45 | 32:45 | 96.7477 | 95.4514 | 132:00 | 132:00 | 97.615 | 96.9945
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 24:55 | 10:40 | 35:35 | 309:00 | 35:35 | 17:48 | 97.5289 | 97.5289 | 309:00 | 154:30 | 96.4822 | 96.4822
13 | Ron | 3 | 3 | 13:20 | 53:40 | 28:55 | 7:40 | 36:35 | 255:26 | 49:55 | 16:38 | 98.3063 | 97.689 | 309:06 | 103:02 | 98.0614 | 97.6541
14 | Mundaragi | 3 | 3 | 9:30 | 50:45 | 42:05 | 35:50 | 77:55 | 595:50 | 87:25 | 29:08 | 96.3927 | 95.9529 | 646:35 | 215:32 | 95.4779 | 95.0927
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 21:45 | 4:40 | 26:25 | 294:05 | 26:25 | 26:25 | 96.331 | 96.331 | 294:05 | 294:05 | 93.3041 | 93.3041
16 | G.C.T.M | 1 | 1 | 11:45 | 94:35 | 20:40 | 4:10 | 24:50 | 221:35 | 36:35 | 36:35 | 96.5509 | 94.919 | 316:10 | 316:10 | 94.9548 | 92.8013
17 | F.C.S.M | 2 | 2 | 19:30 | 167:45 | 7:25 | 0:50 | 8:15 | 242:10 | 27:45 | 13:52 | 99.4271 | 98.0729 | 409:55 | 204:58 | 97.2431 | 95.3334
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 12:20 | 14:00 | 26:20 | 120:18 | 26:20 | 26:20 | 96.3426 | 96.3426 | 120:18 | 120:18 | 97.2609 | 97.2609
19 | Hole-Alur | 1 | 1 | 2:15 | 49:25 | 24:25 | 4:05 | 28:30 | 192:30 | 30:45 | 30:45 | 96.0417 | 95.7292 | 241:55 | 241:55 | 95.617 | 94.4919
20 | Savanur | 2 | 2 | 0:20 | 11:40 | 34:05 | 4:25 | 38:30 | 248:25 | 38:50 | 19:25 | 97.3264 | 97.3032 | 260:05 | 130:02 | 97.1719 | 97.0391
21 | Shiggaon | 2 | 2 | 3:20 | 86:40 | 13:10 | 16:05 | 29:15 | 251:10 | 32:35 | 16:18 | 97.9688 | 97.7373 | 337:50 | 168:55 | 97.1406 | 96.154
22 | Bankapur | 1 | 1 | 12:15 | 66:25 | 8:00 | 2:45 | 10:45 | 82:20 | 23:00 | 23:00 | 98.5069 | 96.8056 | 148:45 | 148:45 | 98.1254 | 96.6132
23 | Hangal | 2 | 2 | 2:50 | 21:30 | 33:15 | 4:40 | 37:55 | 397:40 | 40:45 | 20:22 | 97.3669 | 97.1701 | 419:10 | 209:35 | 95.4728 | 95.2281
24 | Ranebennur | 16 | 16 | 8:40 | 56:11 | 180:58 | 116:50 | 297:48 | 1940:37 | 306:28 | 19:09 | 97.4149 | 97.3397 | 1996:48 | 124:48 | 97.2384 | 97.1585
25 | Halageri | 2 | 2 | 0:20 | 142:10 | 5:40 | 0:25 | 6:05 | 70:25 | 6:25 | 3:12 | 99.5775 | 99.5544 | 212:35 | 106:17 | 99.1984 | 97.5799
26 | Tuminakatti | 3 | 3 | 1:15 | 15:25 | 38:20 | 0:10 | 38:30 | 444:05 | 39:45 | 13:15 | 98.2176 | 98.1597 | 459:30 | 153:10 | 96.6296 | 96.5126
27 | Kahanderayanahalli | 2 | 2 | 4:40 | 102:10 | 59:45 | 2:40 | 62:25 | 474:44 | 67:05 | 33:32 | 95.6655 | 95.3414 | 576:54 | 288:27 | 94.5955 | 93.4324
28 | Rattihalli | 1 | 1 | 0:30 | 7:15 | 9:35 | 5:30 | 15:05 | 124:40 | 15:35 | 15:35 | 97.9051 | 97.8356 | 131:55 | 131:55 | 97.1615 | 96.9964
29 | Hirekerur | 3 | 3 | 16:55 | 175:45 | 40:15 | 27:20 | 67:35 | 637:35 | 84:30 | 28:10 | 96.8711 | 96.088 | 813:20 | 271:07 | 95.161 | 93.8272
30 | Byadagi | 6 | 6 | 7:50 | 154:05 | 44:35 | 40:40 | 85:15 | 1424:40 | 93:05 | 15:31 | 98.0266 | 97.8452 | 1578:45 | 263:08 | 94.5937 | 94.009
31 | Sirsi | 5 | 5 | 29:35 | 200:13 | 45:30 | 8:35 | 54:05 | 344:09 | 83:40 | 16:44 | 98.4977 | 97.6759 | 544:22 | 108:52 | 98.4328 | 97.5211
32 | Yellapur | 3 | 3 | 10:50 | 168:34 | 53:40 | 30:15 | 83:55 | 521:03 | 94:45 | 31:35 | 96.115 | 95.6134 | 689:37 | 229:52 | 96.0455 | 94.7661
33 | Mundagod | 3 | 3 | 3:30 | 45:17 | 42:35 | 20:10 | 62:45 | 501:25 | 66:15 | 22:05 | 97.0949 | 96.9329 | 546:42 | 182:14 | 96.1945 | 95.8508
34 | Siddapur | 2 | 2 | 0:00 | 4:50 | 20:55 | 11:55 | 32:50 | 258:20 | 32:50 | 16:25 | 97.7199 | 97.7199 | 263:10 | 131:35 | 97.059 | 97.004
35 | Dandeli | 8 | 8 | 22:48 | 245:04 | 128:10 | 37:54 | 166:04 | 961:11 | 188:52 | 23:36 | 97.1169 | 96.7211 | 1206:15 | 150:47 | 97.2644 | 96.5669
36 | Haliyal | 3 | 3 | 0:15 | 16:22 | 20:14 | 13:19 | 33:33 | 255:12 | 33:48 | 11:16 | 98.4468 | 98.4352 | 271:34 | 90:31 | 98.0631 | 97.9389
37 | Ankola | 3 | 3 | 33:51 | 289:57 | 29:05 | 12:34 | 41:39 | 250:48 | 75:30 | 25:10 | 98.0718 | 96.5046 | 540:45 | 180:15 | 98.0965 | 95.8959
38 | Kumta | 3 | 3 | 1:18 | 46:54 | 33:32 | 10:14 | 43:46 | 328:37 | 45:04 | 15:01 | 97.9738 | 97.9136 | 375:31 | 125:10 | 97.5059 | 97.15
39 | Gokarna | 1 | 1 | 10:34 | 143:29 | 2:25 | 1:25 | 3:50 | 37:58 | 14:24 | 14:24 | 99.4676 | 98 | 181:27 | 181:27 | 99.1355 | 95.8686
40 | Kasargod | 1 | 1 | 5:49 | 96:43 | 15:25 | 3:15 | 18:40 | 121:00 | 24:29 | 24:29 | 97.4074 | 96.5995 | 217:43 | 217:43 | 97.245 | 95.0429
41 | Honnavar | 3 | 3 | 1:30 | 154:57 | 22:06 | 7:27 | 29:33 | 330:06 | 31:03 | 10:21 | 98.6319 | 98.5625 | 485:03 | 161:41 | 97.4947 | 96.3187
42 | Murdeshwar | 4 | 4 | 20:16 | 215:08 | 44:07 | 22:49 | 66:56 | 594:56 | 87:12 | 21:48 | 97.6759 | 96.9722 | 810:04 | 202:31 | 96.6135 | 95.389
43 | Bhatkal | 2 | 2 | 17:08 | 121:18 | 15:43 | 6:28 | 22:11 | 289:33 | 39:19 | 19:40 | 98.4595 | 97.2697 | 410:51 | 205:25 | 96.7037 | 95.3227
44 | Khanapur | 2 | 2 | 3:05 | 24:07 | 6:37 | 8:20 | 14:57 | 208:15 | 18:02 | 9:01 | 98.9618 | 98.7477 | 232:22 | 116:11 | 97.6292 | 97.3547
45 | Bailhongal | 3 | 3 | 0:00 | 31:51 | 161:00 | 12:10 | 173:10 | 364:23 | 173:10 | 57:43 | 91.983 | 91.983 | 396:14 | 132:05 | 97.2345 | 96.9928
46 | Soundatti | 3 | 3 | 0:00 | 20:17 | 18:40 | 9:02 | 27:42 | 857:27 | 27:42 | 9:14 | 98.7176 | 98.7176 | 877:44 | 292:35 | 93.4923 | 93.3384
47 | Ramdurg | 2 | 2 | 1:00 | 22:20 | 29:15 | 10:50 | 40:05 | 309:00 | 41:05 | 20:32 | 97.2164 | 97.147 | 331:20 | 165:40 | 96.4822 | 96.228
48 | Gokak | 7 | 7 | 13:20 | 150:20 | 109:05 | 77:15 | 186:20 | 1527:00 | 199:40 | 28:31 | 96.3029 | 96.0384 | 1677:20 | 239:37 | 95.0332 | 94.5442
49 | Mudalagi | 2 | 2 | 15:20 | 55:50 | 18:45 | 4:40 | 23:25 | 211:00 | 38:45 | 19:22 | 98.3738 | 97.309 | 266:50 | 133:25 | 97.5979 | 96.9623
50 | Konnur | 1 | 1 | 0:00 | 3:00 | 16:20 | 7:30 | 23:50 | 184:30 | 23:50 | 23:50 | 96.6898 | 96.6898 | 187:30 | 187:30 | 95.7992 | 95.7309
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 16:05 | 4:40 | 20:45 | 156:24 | 20:45 | 20:45 | 97.1181 | 97.1181 | 156:24 | 156:24 | 96.439 | 96.439
52 | Kudachi | 1 | 1 | 2:00 | 10:45 | 50:50 | 23:30 | 74:20 | 320:40 | 76:20 | 76:20 | 89.6759 | 89.3981 | 331:25 | 331:25 | 92.6988 | 92.4541
53 | Athani | 6 | 6 | 8:26 | 96:06 | 84:51 | 45:26 | 130:17 | 739:02 | 138:43 | 23:07 | 96.9842 | 96.789 | 835:08 | 139:11 | 97.1955 | 96.8309
54 | Chikkodi | 2 | 2 | 0:00 | 1:40 | 4:25 | 6:55 | 11:20 | 122:25 | 11:20 | 5:40 | 99.213 | 99.213 | 124:05 | 62:02 | 98.6064 | 98.5874
55 | Nippani | 5 | 5 | 0:00 | 79:35 | 44:35 | 107:45 | 152:20 | 512:25 | 152:20 | 30:28 | 95.7685 | 95.7685 | 592:00 | 118:24 | 97.6666 | 97.3042
56 | Sadalaga | 1 | 1 | 10:05 | 12:35 | 16:30 | 3:25 | 19:55 | 170:01 | 30:00 | 30:00 | 97.2338 | 95.8333 | 182:36 | 182:36 | 96.1289 | 95.8424
57 | Muddebihal | 2 | 2 | 2:25 | 62:55 | 53:20 | 29:20 | 82:40 | 433:10 | 85:05 | 42:33 | 94.2593 | 94.0914 | 496:05 | 248:03 | 95.0687 | 94.3524
58 | Talikot | 1 | 1 | 7:45 | 122:00 | 26:25 | 15:15 | 41:40 | 365:10 | 49:25 | 49:25 | 94.213 | 93.1366 | 487:10 | 487:10 | 91.6856 | 88.9079
59 | B.Bagewadi | 1 | 1 | 5:35 | 32:56 | 9:10 | 2:25 | 11:35 | 86:10 | 17:10 | 17:10 | 98.3912 | 97.6157 | 119:06 | 119:06 | 98.0381 | 97.2883
60 | Indi | 1 | 1 | 0:09 | 7:35 | 11:47 | 1:51 | 13:38 | 105:08 | 13:47 | 13:47 | 98.1065 | 98.0856 | 112:43 | 112:43 | 97.6063 | 97.4336
61 | Sindagi | 2 | 2 | 7:10 | 136:20 | 17:30 | 9:50 | 27:20 | 165:55 | 34:30 | 17:15 | 98.1019 | 97.6042 | 302:15 | 151:08 | 98.1111 | 96.5591
62 | Guledgudda | 1 | 1 | 2:53 | 2:53 | 11:45 | 21:08 | 32:53 | 198:49 | 35:46 | 35:46 | 95.4329 | 95.0324 | 201:42 | 201:42 | 95.4732 | 95.4076
63 | Ilkal | 8 | 8 | 87:40 | 381:14 | 91:30 | 231:16 | 322:46 | 1311:18 | 410:26 | 51:18 | 94.3964 | 92.8744 | 1692:32 | 211:34 | 96.2679 | 95.1829
64 | Kerur | 2 | 2 | 7:44 | 16:40 | 26:40 | 15:23 | 42:03 | 172:35 | 49:47 | 24:54 | 97.0799 | 96.5428 | 189:15 | 94:38 | 98.0353 | 97.8455
65 | Hungund | 3 | 3 | 24:23 | 95:55 | 60:16 | 19:05 | 79:21 | 573:27 | 103:44 | 34:35 | 96.3264 | 95.1975 | 669:22 | 223:07 | 95.6478 | 94.9198
66 | GADDANKERI | 4 | 4 | 4:48 | 34:56 | 12:43 | 28:47 | 41:30 | 206:09 | 46:18 | 11:34 | 98.559 | 98.3924 | 241:05 | 60:16 | 98.8266 | 98.6277
67 | RAMPUR | 1 | 1 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 100 | 100 | 0:00 | 0:00 | 100 | 100
68 | KALADAGI | 2 | 2 | 0:00 | 0:05 | 16:48 | 9:36 | 26:24 | 242:10 | 26:24 | 13:12 | 98.1667 | 98.1667 | 242:15 | 121:08 | 97.2431 | 97.2421
69 | ACHANUR | 1 | 1 | 8:24 | 9:00 | 1:12 | 2:24 | 3:36 | 287:48 | 12:00 | 12:00 | 99.5 | 98.3333 | 296:48 | 296:48 | 93.4472 | 93.2423
70 | SHIRUR | 1 | 1 | 9:36 | 39:42 | 15:36 | 4:48 | 20:24 | 59:28 | 30:00 | 30:00 | 97.1667 | 95.8333 | 99:10 | 99:10 | 98.646 | 97.7421
71 | BADAMI | 1 | 1 | 1:20 | 7:39 | 18:48 | 9:10 | 27:58 | 153:18 | 29:18 | 29:18 | 96.1157 | 95.9306 | 160:57 | 160:57 | 96.5096 | 96.3354
72 | KULAGERI | 1 | 1 | 1:21 | 3:52 | 0:20 | 0:45 | 1:05 | 25:20 | 2:26 | 2:26 | 99.8495 | 99.662 | 29:12 | 29:12 | 99.4232 | 99.3352
73 | Jamkhandi | 5 | 5 | 2:05 | 36:49 | 44:14 | 14:50 | 59:04 | 578:43 | 61:09 | 12:14 | 98.3593 | 98.3014 | 615:32 | 123:06 | 97.3647 | 97.197
74 | Mahalingapur | 2 | 2 | 0:30 | 33:40 | 19:34 | 9:01 | 28:35 | 212:42 | 29:05 | 14:32 | 98.015 | 97.9803 | 246:22 | 123:11 | 97.5786 | 97.1953
75 | Rabakavi | 2 | 2 | 0:10 | 28:00 | 25:53 | 5:00 | 30:53 | 169:49 | 31:03 | 15:32 | 97.8553 | 97.8438 | 197:49 | 98:54 | 98.0668 | 97.748
76 | Banhatti | 2 | 2 | 0:02 | 30:37 | 27:10 | 0:59 | 28:09 | 167:48 | 28:11 | 14:06 | 98.0451 | 98.0428 | 198:25 | 99:13 | 98.0897 | 97.7412
77 | Terdal | 1 | 1 | 0:03 | 17:52 | 18:15 | 4:15 | 22:30 | 145:25 | 22:33 | 22:33 | 96.875 | 96.8681 | 163:17 | 163:17 | 96.6891 | 96.2823
78 | Mudhol | 3 | 3 | 0:00 | 21:36 | 39:46 | 12:29 | 52:15 | 383:19 | 52:15 | 17:25 | 97.581 | 97.581 | 404:55 | 134:58 | 97.0908 | 96.9269
79 | Bilagi | 1 | 1 | 0:40 | 9:40 | 8:00 | 7:10 | 15:10 | 144:57 | 15:50 | 15:50 | 97.8935 | 97.8009 | 154:37 | 154:37 | 96.6997 | 96.4796
80 | Lokapur | 2 | 2 | 0:50 | 7:30 | 40:55 | 37:45 | 78:40 | 389:00 | 79:30 | 39:45 | 94.537 | 94.4792 | 396:30 | 198:15 | 95.5715 | 95.4861
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of October-2019
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of October-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 0:00 | 464:49 | 329:02 | 329:19 | 658:21 | 6453:24 | 658:21 | 8:20 | 98.8799 | 98.8799 | 6918:13 | 87:34 | 98.4095 | 98.2949
2 | Dharwad(R) | 18 | 18 | 5:45 | 161:13 | 170:38 | 260:16 | 430:54 | 3331:43 | 436:39 | 24:16 | 96.7824 | 96.7395 | 3492:56 | 194:03 | 96.3961 | 96.2217
3 | Kundagol | 1 | 1 | 12:05 | 172:00 | 11:00 | 6:05 | 17:05 | 108:05 | 29:10 | 29:10 | 97.7039 | 96.0797 | 280:05 | 280:05 | 97.8956 | 94.5467
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 24:25 | 7:24 | 31:49 | 168:28 | 31:49 | 31:49 | 95.7236 | 95.7236 | 168:28 | 168:28 | 96.7199 | 96.7199
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 14:35 | 13:35 | 28:10 | 248:08 | 28:10 | 28:10 | 96.2142 | 96.2142 | 248:08 | 248:08 | 95.1687 | 95.1687
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 16:00 | 18:55 | 34:55 | 584:05 | 34:55 | 17:28 | 97.6534 | 97.6534 | 584:05 | 292:02 | 94.3138 | 94.3138
7 | Alnavar | 1 | 1 | 4:30 | 65:00 | 16:20 | 21:45 | 38:05 | 189:30 | 42:35 | 42:35 | 94.8813 | 94.2764 | 254:30 | 254:30 | 96.3104 | 95.0448
8 | Naragund | 2 | 2 | 1:00 | 42:20 | 14:55 | 22:10 | 37:05 | 527:00 | 38:05 | 19:02 | 97.5078 | 97.4406 | 569:20 | 284:40 | 94.8695 | 94.4574
9 | Shirahatti | 2 | 2 | 0:00 | 0:00 | 31:35 | 32:05 | 63:40 | 342:10 | 63:40 | 31:50 | 95.7213 | 95.7213 | 342:10 | 171:05 | 96.6689 | 96.6689
10 | Laxmeshwar | 6 | 6 | 0:00 | 0:00 | 103:27 | 128:46 | 232:13 | 1341:22 | 232:13 | 38:42 | 94.798 | 94.798 | 1341:22 | 223:34 | 95.6472 | 95.6472
11 | Naregal | 1 | 1 | 0:15 | 27:30 | 6:20 | 3:40 | 10:00 | 114:45 | 10:15 | 10:15 | 98.6559 | 98.6223 | 142:15 | 142:15 | 97.7658 | 97.2303
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 46:30 | 21:35 | 68:05 | 377:05 | 68:05 | 34:02 | 95.4245 | 95.4245 | 377:05 | 188:32 | 96.329 | 96.329
13 | Ron | 3 | 3 | 6:10 | 59:50 | 36:05 | 49:55 | 86:00 | 341:26 | 92:10 | 30:43 | 96.147 | 95.8707 | 401:16 | 133:45 | 97.7841 | 97.3957
14 | Mundaragi | 3 | 3 | 8:05 | 58:50 | 25:30 | 55:30 | 81:00 | 676:50 | 89:05 | 29:42 | 96.371 | 96.0088 | 735:40 | 245:13 | 95.6073 | 95.2254
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 22:11 | 40:06 | 62:17 | 356:22 | 62:17 | 62:17 | 91.6286 | 91.6286 | 356:22 | 356:22 | 93.0614 | 93.0614
16 | G.C.T.M | 1 | 1 | 7:20 | 101:55 | 13:40 | 2:20 | 16:00 | 237:35 | 23:20 | 23:20 | 97.8495 | 96.8638 | 339:30 | 339:30 | 95.3742 | 93.3898
17 | F.C.S.M | 2 | 2 | 10:00 | 177:45 | 5:25 | 2:30 | 7:55 | 250:05 | 17:55 | 8:58 | 99.468 | 98.7959 | 427:50 | 213:55 | 97.5654 | 95.835
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 12:35 | 9:11 | 21:46 | 142:04 | 21:46 | 21:46 | 97.0744 | 97.0744 | 142:04 | 142:04 | 97.2339 | 97.2339
19 | Hole-Alur | 1 | 1 | 3:25 | 52:50 | 12:30 | 9:50 | 22:20 | 214:50 | 25:45 | 25:45 | 96.9982 | 96.539 | 267:40 | 267:40 | 95.8171 | 94.7884
20 | Savanur | 2 | 2 | 2:05 | 13:45 | 30:30 | 20:50 | 51:20 | 299:45 | 53:25 | 26:42 | 96.5502 | 96.4102 | 313:30 | 156:45 | 97.0819 | 96.948
21 | Shiggaon | 2 | 2 | 13:10 | 99:50 | 18:55 | 29:50 | 48:45 | 299:55 | 61:55 | 30:58 | 96.7238 | 95.8389 | 399:45 | 199:52 | 97.0803 | 96.1084
22 | Bankapur | 1 | 1 | 30:35 | 97:00 | 13:05 | 12:50 | 25:55 | 108:15 | 56:30 | 56:30 | 96.5166 | 92.4059 | 205:15 | 205:15 | 97.8923 | 96.0037
23 | Hangal | 2 | 2 | 7:40 | 29:10 | 29:15 | 47:45 | 77:00 | 474:40 | 84:40 | 42:20 | 94.8253 | 94.31 | 503:50 | 251:55 | 95.379 | 95.0951
24 | Ranebennur | 16 | 16 | 45:35 | 101:46 | 174:49 | 218:28 | 393:17 | 2333:54 | 438:52 | 27:26 | 96.6962 | 96.3133 | 2435:40 | 152:14 | 97.1599 | 97.036
25 | Halageri | 2 | 2 | 23:10 | 165:20 | 6:25 | 1:40 | 8:05 | 78:30 | 31:15 | 15:38 | 99.4568 | 97.8999 | 243:50 | 121:55 | 99.2358 | 97.6262
26 | Tuminakatti | 3 | 3 | 1:30 | 16:55 | 69:00 | 39:00 | 108:00 | 552:05 | 109:30 | 36:30 | 95.1613 | 95.0941 | 569:00 | 189:40 | 96.4169 | 96.3071
27 | Kahanderayanahalli | 2 | 2 | 10:50 | 113:00 | 88:50 | 79:35 | 168:25 | 643:09 | 179:15 | 89:38 | 88.6817 | 87.9536 | 756:09 | 378:04 | 93.7388 | 92.6387
28 | Rattihalli | 1 | 1 | 0:30 | 7:45 | 9:35 | 5:30 | 15:05 | 139:45 | 15:35 | 15:35 | 97.9727 | 97.9055 | 147:30 | 147:30 | 97.279 | 97.1281
29 | Hirekerur | 3 | 3 | 14:00 | 189:45 | 83:15 | 60:40 | 143:55 | 781:30 | 157:55 | 52:38 | 93.5521 | 92.9249 | 971:15 | 323:45 | 94.928 | 93.6965
30 | Byadagi | 6 | 6 | 49:05 | 203:10 | 68:05 | 159:00 | 227:05 | 1651:45 | 276:10 | 46:02 | 94.913 | 93.8135 | 1854:55 | 309:09 | 94.64 | 93.9807
31 | Sirsi | 5 | 5 | 2:55 | 203:08 | 13:50 | 28:00 | 41:50 | 385:59 | 44:45 | 8:57 | 98.8754 | 98.797 | 589:07 | 117:49 | 98.4969 | 97.7059
32 | Yellapur | 3 | 3 | 4:50 | 173:24 | 52:35 | 33:05 | 85:40 | 606:43 | 90:30 | 30:10 | 96.1619 | 95.9453 | 780:07 | 260:02 | 96.0623 | 94.9369
33 | Mundagod | 3 | 3 | 3:30 | 48:47 | 42:35 | 20:10 | 62:45 | 564:10 | 66:15 | 22:05 | 97.1886 | 97.0318 | 612:57 | 204:19 | 96.3385 | 96.0219
34 | Siddapur | 2 | 2 | 34:50 | 39:40 | 19:45 | 12:05 | 31:50 | 290:10 | 66:40 | 33:20 | 97.8607 | 95.5197 | 329:50 | 164:55 | 97.1752 | 96.789
35 | Dandeli | 8 | 8 | 19:04 | 264:08 | 91:32 | 171:59 | 263:31 | 1224:42 | 282:35 | 35:19 | 95.5726 | 95.2523 | 1488:50 | 186:06 | 97.0193 | 96.3765
36 | Haliyal | 3 | 3 | 0:25 | 16:47 | 19:10 | 11:51 | 31:01 | 286:13 | 31:26 | 10:29 | 98.6104 | 98.5917 | 303:00 | 101:00 | 98.1424 | 98.0335
37 | Ankola | 3 | 3 | 131:17 | 421:14 | 25:21 | 32:37 | 57:58 | 308:46 | 189:15 | 63:05 | 97.4029 | 91.5211 | 730:00 | 243:20 | 97.9961 | 95.2622
38 | Kumta | 3 | 3 | 8:30 | 55:24 | 37:49 | 20:13 | 58:02 | 386:39 | 66:32 | 22:11 | 97.3999 | 97.0191 | 442:03 | 147:21 | 97.4906 | 97.131
39 | Gokarna | 1 | 1 | 19:14 | 162:43 | 3:35 | 2:30 | 6:05 | 44:03 | 25:19 | 25:19 | 99.1823 | 96.5972 | 206:46 | 206:46 | 99.1423 | 95.9742
40 | Kasargod | 1 | 1 | 14:34 | 111:17 | 11:55 | 27:35 | 39:30 | 160:30 | 54:04 | 54:04 | 94.6909 | 92.733 | 271:47 | 271:47 | 96.875 | 94.7083
41 | Honnavar | 3 | 3 | 65:42 | 220:39 | 54:11 | 42:09 | 96:20 | 426:26 | 162:02 | 54:01 | 95.684 | 92.7404 | 647:05 | 215:42 | 97.2324 | 95.8003
42 | Murdeshwar | 4 | 4 | 88:12 | 303:20 | 88:22 | 71:30 | 159:52 | 754:48 | 248:04 | 62:01 | 94.6281 | 91.6644 | 1058:08 | 264:32 | 96.3259 | 94.8494
43 | Bhatkal | 3 | 3 | 39:06 | 160:24 | 41:35 | 52:31 | 94:06 | 383:39 | 133:12 | 44:24 | 95.7841 | 94.0323 | 544:03 | 181:21 | 97.5101 | 96.469
44 | Khanapur | 2 | 2 | 0:00 | 24:07 | 22:57 | 8:32 | 31:29 | 239:44 | 31:29 | 15:45 | 97.8842 | 97.8842 | 263:51 | 131:55 | 97.6661 | 97.4314
45 | Bailhongal | 3 | 3 | 2:54 | 34:45 | 25:40 | 17:05 | 42:45 | 407:08 | 45:39 | 15:13 | 98.0847 | 97.9547 | 441:53 | 147:18 | 97.3576 | 97.1321
46 | Soundatti | 3 | 3 | 1:06 | 21:23 | 20:09 | 10:57 | 31:06 | 888:33 | 32:12 | 10:44 | 98.6066 | 98.5573 | 909:56 | 303:19 | 94.2332 | 94.0944
47 | Ramdurg | 2 | 2 | 1:20 | 23:40 | 22:05 | 9:20 | 31:25 | 340:25 | 32:45 | 16:22 | 97.8887 | 97.7991 | 364:05 | 182:02 | 96.686 | 96.4556
48 | Gokak | 7 | 7 | 27:50 | 178:10 | 119:15 | 85:30 | 204:45 | 1731:45 | 232:35 | 33:14 | 96.0685 | 95.5341 | 1909:55 | 272:51 | 95.1832 | 94.6876
49 | Mudalagi | 2 | 2 | 1:30 | 57:20 | 38:10 | 49:15 | 87:25 | 298:25 | 88:55 | 44:28 | 94.1252 | 94.0244 | 355:45 | 177:52 | 97.0949 | 96.5367
50 | Konnur | 1 | 1 | 0:00 | 3:00 | 16:35 | 14:35 | 31:10 | 215:40 | 31:10 | 31:10 | 95.8109 | 95.8109 | 218:40 | 218:40 | 95.8009 | 95.7425
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 40:20 | 21:25 | 61:45 | 218:09 | 61:45 | 61:45 | 91.7003 | 91.7003 | 218:09 | 218:09 | 95.7525 | 95.7525
52 | Kudachi | 1 | 1 | 0:00 | 10:45 | 72:25 | 7:55 | 80:20 | 401:00 | 80:20 | 80:20 | 89.2025 | 89.2025 | 411:45 | 411:45 | 92.1924 | 91.9831
53 | Athani | 6 | 6 | 34:18 | 130:24 | 92:51 | 41:10 | 134:01 | 873:03 | 168:19 | 28:03 | 96.9978 | 96.2295 | 1003:27 | 167:14 | 97.1669 | 96.7437
54 | Chikkodi | 2 | 2 | 0:00 | 1:40 | 1:40 | 12:05 | 13:45 | 136:10 | 13:45 | 6:52 | 99.0759 | 99.0759 | 137:50 | 68:55 | 98.6744 | 98.6582
55 | Nippani | 5 | 5 | 0:00 | 79:35 | 34:20 | 31:37 | 65:57 | 578:22 | 65:57 | 13:11 | 98.2272 | 98.2272 | 657:57 | 131:35 | 97.7478 | 97.4379
56 | Sadalaga | 1 | 1 | 0:00 | 12:35 | 16:50 | 11:55 | 28:45 | 198:46 | 28:45 | 28:45 | 96.1358 | 96.1358 | 211:21 | 211:21 | 96.1299 | 95.8849
57 | Muddebihal | 2 | 2 | 5:10 | 68:05 | 32:40 | 7:50 | 40:30 | 473:40 | 45:40 | 22:50 | 97.2782 | 96.931 | 541:45 | 270:53 | 95.3888 | 94.726
58 | Talikot | 1 | 1 | 3:05 | 125:05 | 20:50 | 6:30 | 27:20 | 392:30 | 30:25 | 30:25 | 96.3262 | 95.9117 | 517:35 | 517:35 | 92.3579 | 89.9224
59 | B.Bagewadi | 1 | 1 | 4:39 | 37:35 | 5:49 | 2:10 | 7:59 | 94:09 | 12:38 | 12:38 | 98.927 | 98.302 | 131:44 | 131:44 | 98.1669 | 97.4351
60 | Indi | 1 | 1 | 3:48 | 11:23 | 9:19 | 4:52 | 14:11 | 119:19 | 17:59 | 17:59 | 98.0936 | 97.5829 | 130:42 | 130:42 | 97.6769 | 97.4552
61 | Sindagi | 2 | 2 | 10:30 | 146:50 | 9:40 | 4:50 | 14:30 | 180:25 | 25:00 | 12:30 | 99.0255 | 98.3199 | 327:15 | 163:38 | 98.2436 | 96.8142
62 | Guledgudda | 1 | 1 | 0:00 | 2:53 | 21:40 | 20:00 | 41:40 | 240:29 | 41:40 | 41:40 | 94.3996 | 94.3996 | 243:22 | 243:22 | 95.3177 | 95.2616
63 | Ilkal | 8 | 8 | 35:27 | 416:41 | 98:50 | 177:32 | 276:22 | 1587:40 | 311:49 | 38:59 | 95.3567 | 94.7611 | 2004:21 | 250:33 | 96.1359 | 95.1218
64 | Kerur | 2 | 2 | 0:20 | 17:00 | 21:52 | 19:26 | 41:18 | 213:53 | 41:38 | 20:49 | 97.2245 | 97.2021 | 230:53 | 115:26 | 97.9178 | 97.7523
65 | Hungund | 3 | 3 | 3:39 | 99:34 | 83:37 | 32:44 | 116:21 | 689:48 | 120:00 | 40:00 | 94.7872 | 94.6237 | 789:22 | 263:07 | 95.5231 | 94.8769
66 | GADDANKERI | 4 | 4 | 5:00 | 39:56 | 13:10 | 40:35 | 53:45 | 259:54 | 58:45 | 14:41 | 98.1939 | 98.0259 | 299:50 | 74:58 | 98.7349 | 98.5405
67 | RAMPUR | 1 | 1 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 100 | 100 | 0:00 | 0:00 | 100 | 100
68 | KALADAGI | 2 | 2 | 0:00 | 0:05 | 22:33 | 22:30 | 45:03 | 287:13 | 45:03 | 22:32 | 96.9724 | 96.9724 | 287:18 | 143:39 | 97.2039 | 97.2031
69 | ACHANUR | 1 | 1 | 3:04 | 12:04 | 18:06 | 150:01 | 168:07 | 455:55 | 171:11 | 171:11 | 77.4037 | 76.9915 | 467:59 | 467:59 | 91.1231 | 90.8882
70 | SHIRUR | 1 | 1 | 13:00 | 52:42 | 0:00 | 1:00 | 1:00 | 60:28 | 14:00 | 14:00 | 99.8656 | 98.1183 | 113:10 | 113:10 | 98.8227 | 97.7966
71 | BADAMI | 1 | 1 | 1:55 | 9:34 | 10:23 | 8:48 | 19:11 | 172:29 | 21:06 | 21:06 | 97.4216 | 97.164 | 182:03 | 182:03 | 96.6417 | 96.4554
72 | KULAGERI | 1 | 1 | 0:52 | 4:44 | 8:40 | 0:25 | 9:05 | 34:25 | 9:57 | 9:57 | 98.7791 | 98.6626 | 39:09 | 39:09 | 99.3299 | 99.2377
73 | Jamkhandi | 5 | 5 | 6:15 | 43:04 | 108:02 | 34:29 | 142:31 | 721:14 | 148:46 | 29:45 | 96.1689 | 96.0009 | 764:18 | 152:52 | 97.1915 | 97.0238
74 | Mahalingapur | 2 | 2 | 0:36 | 34:16 | 11:11 | 43:17 | 54:28 | 267:10 | 55:04 | 27:32 | 96.3396 | 96.2993 | 301:26 | 150:43 | 97.3991 | 97.0655
75 | Rabakavi | 2 | 2 | 0:20 | 28:20 | 19:40 | 5:05 | 24:45 | 194:34 | 25:05 | 12:32 | 98.3367 | 98.3143 | 222:54 | 111:27 | 98.1059 | 97.83
76 | Banhatti | 2 | 2 | 0:00 | 30:37 | 34:50 | 10:29 | 45:19 | 213:07 | 45:19 | 22:40 | 96.9545 | 96.9545 | 243:44 | 121:52 | 97.9253 | 97.6272
77 | Terdal | 1 | 1 | 16:25 | 34:17 | 31:45 | 6:15 | 38:00 | 183:25 | 54:25 | 54:25 | 94.8925 | 92.6859 | 217:42 | 217:42 | 96.4288 | 95.7613
78 | Mudhol | 3 | 3 | 13:37 | 35:13 | 37:34 | 19:52 | 57:26 | 440:45 | 71:03 | 23:41 | 97.4268 | 96.8168 | 475:58 | 158:39 | 97.1395 | 96.9109
79 | Bilagi | 1 | 1 | 4:05 | 13:45 | 8:20 | 5:35 | 13:55 | 158:52 | 18:00 | 18:00 | 98.1295 | 97.5806 | 172:37 | 172:37 | 96.9068 | 96.6391
80 | Lokapur | 2 | 2 | 15:25 | 22:55 | 94:45 | 60:45 | 155:30 | 544:30 | 170:55 | 85:27 | 89.5497 | 88.5137 | 567:25 | 283:43 | 94.6992 | 94.4761
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of November-2019
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of November-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 79 | 79 | 0:00 | 464:49 | 104:58 | 100:52 | 205:50 | 6659:14 | 205:50 | 2:36 | 99.6381 | 99.6381 | 7124:03 | 90:11 | 98.5606 | 98.4601
2 | Dharwad(R) | 18 | 18 | 8:15 | 169:28 | 123:13 | 101:39 | 224:52 | 3556:35 | 233:07 | 12:57 | 98.2649 | 98.2013 | 3726:03 | 207:00 | 96.6259 | 96.4651
3 | Kundagol | 1 | 1 | 1:35 | 173:35 | 5:25 | 1:15 | 6:40 | 114:45 | 8:15 | 8:15 | 99.0741 | 98.8542 | 288:20 | 288:20 | 98.0405 | 95.0763
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 2:11 | 2:46 | 4:57 | 173:25 | 4:57 | 4:57 | 99.3125 | 99.3125 | 173:25 | 173:25 | 97.0386 | 97.0386
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 7:05 | 4:11 | 11:16 | 259:24 | 11:16 | 11:16 | 98.4352 | 98.4352 | 259:24 | 259:24 | 95.5704 | 95.5704
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 18:00 | 15:25 | 33:25 | 617:30 | 33:25 | 16:42 | 97.6794 | 97.6794 | 617:30 | 308:45 | 94.7276 | 94.7276
7 | Alnavar | 1 | 1 | 4:00 | 69:00 | 8:30 | 19:50 | 28:20 | 217:50 | 32:20 | 32:20 | 96.0648 | 95.5093 | 286:50 | 286:50 | 96.2802 | 95.1019
8 | Naragund | 2 | 2 | 13:20 | 55:40 | 23:25 | 46:50 | 70:15 | 597:15 | 83:35 | 41:48 | 95.1215 | 94.1956 | 652:55 | 326:28 | 94.9005 | 94.4252
9 | Shirahatti | 2 | 2 | 0:00 | 0:00 | 11:15 | 7:25 | 18:40 | 360:50 | 18:40 | 9:20 | 98.7037 | 98.7037 | 360:50 | 180:25 | 96.9191 | 96.9191
10 | Laxmeshwar | 6 | 6 | 0:00 | 0:00 | 34:28 | 15:50 | 50:18 | 1391:40 | 50:18 | 8:23 | 98.8356 | 98.8356 | 1391:40 | 231:57 | 96.0392 | 96.0392
11 | Naregal | 1 | 1 | 0:00 | 27:30 | 4:30 | 1:40 | 6:10 | 120:55 | 6:10 | 6:10 | 99.1435 | 99.1435 | 148:25 | 148:25 | 97.9352 | 97.4656
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 18:15 | 2:20 | 20:35 | 397:40 | 20:35 | 10:18 | 98.5706 | 98.5706 | 397:40 | 198:50 | 96.6046 | 96.6046
13 | Ron | 3 | 3 | 0:00 | 59:50 | 38:40 | 40:10 | 78:50 | 420:16 | 78:50 | 26:17 | 96.3503 | 96.3503 | 480:06 | 160:02 | 97.6078 | 97.2672
14 | Mundaragi | 3 | 3 | 3:50 | 62:40 | 30:55 | 31:10 | 62:05 | 738:55 | 65:55 | 21:58 | 97.1258 | 96.9483 | 801:35 | 267:12 | 95.794 | 95.4373
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 27:13 | 30:08 | 57:21 | 413:43 | 57:21 | 57:21 | 92.0347 | 92.0347 | 413:43 | 413:43 | 92.9352 | 92.9352
16 | G.C.T.M | 1 | 1 | 10:45 | 112:40 | 12:45 | 2:15 | 15:00 | 252:35 | 25:45 | 25:45 | 97.9167 | 96.4236 | 365:15 | 365:15 | 95.6868 | 93.7628
17 | F.C.S.M | 2 | 2 | 18:20 | 196:05 | 7:25 | 1:05 | 8:30 | 258:35 | 26:50 | 13:25 | 99.4097 | 98.1366 | 454:40 | 227:20 | 97.7922 | 96.1179
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 9:01 | 3:38 | 12:39 | 154:43 | 12:39 | 12:39 | 98.2431 | 98.2431 | 154:43 | 154:43 | 97.358 | 97.358
19 | Hole-Alur | 1 | 1 | 8:50 | 61:40 | 6:10 | 0:05 | 6:15 | 221:05 | 15:05 | 15:05 | 99.1319 | 97.9051 | 282:45 | 282:45 | 96.2247 | 95.1716
20 | Savanur | 2 | 2 | 8:30 | 22:15 | 5:55 | 2:35 | 8:30 | 308:15 | 17:00 | 8:30 | 99.4097 | 98.8194 | 330:30 | 165:15 | 97.3681 | 97.1781
21 | Shiggaon | 2 | 2 | 8:35 | 108:25 | 15:25 | 7:15 | 22:40 | 322:35 | 31:15 | 15:38 | 98.4259 | 97.8299 | 431:00 | 215:30 | 97.2457 | 96.32
22 | Bankapur | 1 | 1 | 7:25 | 104:25 | 4:40 | 7:10 | 11:50 | 120:05 | 19:15 | 19:15 | 98.3565 | 97.3264 | 224:30 | 224:30 | 97.9494 | 96.1663
23 | Hangal | 2 | 2 | 6:40 | 35:50 | 23:50 | 8:45 | 32:35 | 507:15 | 39:15 | 19:38 | 97.7373 | 97.2743 | 543:05 | 271:33 | 95.669 | 95.363
24 | Ranebennur | 16 | 16 | 8:40 | 110:26 | 110:22 | 32:59 | 143:21 | 2477:15 | 152:01 | 9:30 | 98.7556 | 98.6804 | 2587:41 | 161:44 | 97.3561 | 97.2382
25 | Halageri | 2 | 2 | 9:10 | 174:30 | 20:35 | 1:40 | 22:15 | 100:45 | 31:25 | 15:42 | 98.4549 | 97.8183 | 275:15 | 137:38 | 99.1398 | 97.6498
26 | Tuminakatti | 3 | 3 | 2:30 | 19:25 | 46:00 | 1:00 | 47:00 | 599:05 | 49:30 | 16:30 | 97.8241 | 97.7083 | 618:30 | 206:10 | 96.5899 | 96.4794
27 | Kahanderayanahalli | 2 | 2 | 3:28 | 116:28 | 54:30 | 16:00 | 70:30 | 713:39 | 73:58 | 36:59 | 95.1042 | 94.8634 | 830:07 | 415:04 | 93.9067 | 92.9123
28 | Rattihalli | 1 | 1 | 0:50 | 8:35 | 7:40 | 4:15 | 11:55 | 151:40 | 12:45 | 12:45 | 98.3449 | 98.2292 | 160:15 | 160:15 | 97.4101 | 97.2635
29 | Hirekerur | 3 | 3 | 8:05 | 197:50 | 69:40 | 9:50 | 79:30 | 861:00 | 87:35 | 29:12 | 96.3194 | 95.9452 | 1058:50 | 352:57 | 95.099 | 93.9729
30 | Byadagi | 6 | 6 | 9:45 | 212:55 | 29:05 | 30:25 | 59:30 | 1711:15 | 69:15 | 11:33 | 98.6227 | 98.397 | 1924:10 | 320:42 | 95.1296 | 94.5236
31 | Sirsi | 5 | 5 | 25:50 | 228:58 | 46:30 | 23:30 | 70:00 | 455:59 | 95:50 | 19:10 | 98.0556 | 97.338 | 684:57 | 136:59 | 98.4427 | 97.6607
32 | Yellapur | 3 | 3 | 1:10 | 174:34 | 5:55 | 6:00 | 11:55 | 618:38 | 13:05 | 4:22 | 99.4483 | 99.3943 | 793:12 | 264:24 | 96.4786 | 95.485
33 | Mundagod | 3 | 3 | 7:15 | 56:02 | 56:10 | 62:40 | 118:50 | 683:00 | 126:05 | 42:02 | 94.4985 | 94.1628 | 739:02 | 246:21 | 96.1122 | 95.7933
34 | Siddapur | 2 | 2 | 36:30 | 76:10 | 3:55 | 4:25 | 8:20 | 298:30 | 44:50 | 22:25 | 99.4213 | 96.8866 | 374:40 | 187:20 | 97.4513 | 96.801
35 | Dandeli | 8 | 8 | 133:28 | 397:36 | 51:11 | 13:50 | 65:01 | 1289:43 | 198:29 | 24:49 | 98.8712 | 96.5541 | 1687:19 | 210:55 | 97.247 | 96.3983
36 | Haliyal | 3 | 3 | 6:55 | 23:42 | 11:47 | 3:10 | 14:57 | 301:10 | 21:52 | 7:17 | 99.3079 | 98.9877 | 324:52 | 108:17 | 98.2857 | 98.1508
37 | Ankola | 3 | 3 | 24:34 | 445:48 | 7:07 | 6:28 | 13:35 | 322:21 | 38:09 | 12:43 | 99.3711 | 98.2338 | 768:09 | 256:03 | 98.1651 | 95.6276
38 | Kumta | 3 | 3 | 3:09 | 58:33 | 10:53 | 7:09 | 18:02 | 404:41 | 21:11 | 7:04 | 99.1651 | 99.0193 | 463:14 | 154:25 | 97.6965 | 97.3632
39 | Gokarna | 1 | 1 | 23:48 | 186:31 | 1:40 | 0:05 | 1:45 | 45:48 | 25:33 | 25:33 | 99.7569 | 96.4514 | 232:19 | 232:19 | 99.2179 | 96.0328
40 | Kasargod | 1 | 1 | 13:01 | 124:18 | 5:10 | 1:35 | 6:45 | 167:15 | 19:46 | 19:46 | 99.0625 | 97.2546 | 291:33 | 291:33 | 97.144 | 95.0213
41 | Honnavar | 3 | 3 | 10:39 | 231:18 | 13:52 | 8:08 | 22:00 | 448:26 | 32:39 | 10:53 | 98.9815 | 98.4884 | 679:44 | 226:35 | 97.4474 | 96.1308
42 | Murdeshwar | 4 | 4 | 18:52 | 322:12 | 45:27 | 16:46 | 62:13 | 817:01 | 81:05 | 20:16 | 97.8397 | 97.1846 | 1139:13 | 284:48 | 96.5121 | 95.1365
43 | Bhatkal | 3 | 3 | 67:48 | 228:12 | 35:03 | 15:21 | 50:24 | 434:03 | 118:12 | 39:24 | 97.6667 | 94.5278 | 662:15 | 220:45 | 97.5293 | 96.2304
44 | Khanapur | 2 | 2 | 0:00 | 24:07 | 22:32 | 6:35 | 29:07 | 268:51 | 29:07 | 14:34 | 97.978 | 97.978 | 292:58 | 146:29 | 97.7045 | 97.4986
45 | Bailhongal | 3 | 3 | 1:00 | 35:45 | 37:45 | 9:55 | 47:40 | 454:48 | 48:40 | 16:13 | 97.7932 | 97.7469 | 490:33 | 163:31 | 97.4112 | 97.2077
46 | Soundatti | 3 | 3 | 0:00 | 21:23 | 64:26 | 112:28 | 176:54 | 1065:27 | 176:54 | 58:58 | 91.8102 | 91.8102 | 1086:50 | 362:17 | 93.9353 | 93.8136
47 | Ramdurg | 2 | 2 | 0:00 | 23:40 | 19:45 | 4:50 | 24:35 | 365:00 | 24:35 | 12:18 | 98.2928 | 98.2928 | 388:40 | 194:20 | 96.8835 | 96.6815
48 | Gokak | 7 | 7 | 0:00 | 178:10 | 78:20 | 29:55 | 108:15 | 1840:00 | 108:15 | 15:28 | 97.8522 | 97.8522 | 2018:10 | 288:19 | 95.5113 | 95.0767
49 | Mudalagi | 2 | 2 | 0:20 | 57:40 | 38:35 | 10:50 | 49:25 | 347:50 | 49:45 | 24:53 | 96.5683 | 96.5451 | 405:30 | 202:45 | 97.0301 | 96.5377
50 | Konnur | 1 | 1 | 0:00 | 3:00 | 22:25 | 3:25 | 25:50 | 241:30 | 25:50 | 25:50 | 96.412 | 96.412 | 244:30 | 244:30 | 95.876 | 95.8248
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 16:30 | 3:25 | 19:55 | 238:04 | 19:55 | 19:55 | 97.2338 | 97.2338 | 238:04 | 238:04 | 95.9347 | 95.9347
52 | Kudachi | 1 | 1 | 1:20 | 12:05 | 31:05 | 1:50 | 32:55 | 433:55 | 34:15 | 34:15 | 95.4282 | 95.2431 | 446:00 | 446:00 | 92.5902 | 92.3839
53 | Athani | 6 | 6 | 8:36 | 139:00 | 144:19 | 46:01 | 190:20 | 1063:23 | 198:56 | 33:09 | 95.5941 | 95.3951 | 1202:23 | 200:24 | 96.9735 | 96.5779
54 | Chikkodi | 2 | 2 | 0:00 | 1:40 | 1:55 | 8:25 | 10:20 | 146:30 | 10:20 | 5:10 | 99.2824 | 99.2824 | 148:10 | 74:05 | 98.7491 | 98.7349
55 | Nippani | 5 | 5 | 0:00 | 79:35 | 23:45 | 13:50 | 37:35 | 615:57 | 37:35 | 7:31 | 98.956 | 98.956 | 695:32 | 139:06 | 97.8963 | 97.6245
56 | Sadalaga | 1 | 1 | 0:00 | 12:35 | 6:00 | 4:20 | 10:20 | 209:06 | 10:20 | 10:20 | 98.5648 | 98.5648 | 221:41 | 221:41 | 96.4293 | 96.2144
57 | Muddebihal | 2 | 2 | 9:10 | 77:15 | 40:50 | 6:40 | 47:30 | 521:10 | 56:40 | 28:20 | 96.7014 | 96.0648 | 598:25 | 299:13 | 95.5501 | 94.8906
58 | Talikot | 1 | 1 | 2:25 | 127:30 | 9:30 | 6:05 | 15:35 | 408:05 | 18:00 | 18:00 | 97.8356 | 97.5 | 535:35 | 535:35 | 93.0314 | 90.8541
59 | B.Bagewadi | 1 | 1 | 5:16 | 42:51 | 1:10 | 1:52 | 3:02 | 97:11 | 8:18 | 8:18 | 99.5787 | 98.8472 | 140:02 | 140:02 | 98.3404 | 97.6087
60 | Indi | 1 | 1 | 2:06 | 13:29 | 11:07 | 1:13 | 12:20 | 131:39 | 14:26 | 14:26 | 98.287 | 97.9954 | 145:08 | 145:08 | 97.7519 | 97.5216
61 | Sindagi | 2 | 2 | 29:00 | 175:50 | 17:20 | 1:00 | 18:20 | 198:45 | 47:20 | 23:40 | 98.7269 | 96.713 | 374:35 | 187:17 | 98.303 | 96.8017
62 | Guledgudda | 1 | 1 | 0:20 | 3:13 | 13:55 | 3:20 | 17:15 | 257:44 | 17:35 | 17:35 | 97.6042 | 97.5579 | 260:57 | 260:57 | 95.5988 | 95.5439
63 | Ilkal | 8 | 8 | 75:19 | 492:00 | 74:37 | 124:02 | 198:39 | 1786:19 | 273:58 | 34:15 | 96.5512 | 95.2436 | 2278:19 | 284:47 | 96.187 | 95.1368
64 | Kerur | 2 | 2 | 0:00 | 17:00 | 9:30 | 5:12 | 14:42 | 228:35 | 14:42 | 7:21 | 98.9792 | 98.9792 | 245:35 | 122:48 | 98.0483 | 97.9031
65 | Hungund | 3 | 3 | 24:23 | 123:57 | 60:16 | 19:05 | 79:21 | 769:09 | 103:44 | 34:35 | 96.3264 | 95.1975 | 893:06 | 297:42 | 95.6219 | 94.9163
66 | GADDANKERI | 4 | 4 | 0:06 | 40:02 | 11:53 | 2:24 | 14:17 | 274:11 | 14:23 | 3:36 | 99.5041 | 99.5006 | 314:13 | 78:33 | 98.8295 | 98.6586
67 | RAMPUR | 1 | 1 | 0:00 | 0:00 | 0:18 | 0:00 | 0:18 | 0:18 | 0:18 | 0:18 | 99.9583 | 99.9583 | 0:18 | 0:18 | 99.9949 | 99.9949
68 | KALADAGI | 2 | 2 | 0:00 | 0:05 | 13:18 | 22:18 | 35:36 | 322:49 | 35:36 | 17:48 | 97.5278 | 97.5278 | 322:54 | 161:27 | 97.2437 | 97.243
69 | ACHANUR | 1 | 1 | 0:06 | 12:10 | 12:09 | 54:15 | 66:24 | 522:19 | 66:30 | 66:30 | 90.7778 | 90.7639 | 534:29 | 534:29 | 91.0807 | 90.8729
70 | SHIRUR | 1 | 1 | 18:09 | 70:51 | 16:18 | 3:09 | 19:27 | 79:55 | 37:36 | 37:36 | 97.2986 | 94.7778 | 150:46 | 150:46 | 98.6353 | 97.4254
71 | BADAMI | 1 | 1 | 0:00 | 9:34 | 13:28 | 6:08 | 19:36 | 192:05 | 19:36 | 19:36 | 97.2778 | 97.2778 | 201:39 | 201:39 | 96.7199 | 96.5565
72 | KULAGERI | 1 | 1 | 0:00 | 4:44 | 4:10 | 0:00 | 4:10 | 38:35 | 4:10 | 4:10 | 99.4213 | 99.4213 | 43:19 | 43:19 | 99.3411 | 99.2603
73 | Jamkhandi | 5 | 5 | 2:55 | 45:59 | 41:27 | 6:01 | 47:28 | 768:42 | 50:23 | 10:05 | 98.6815 | 98.6005 | 814:41 | 162:56 | 97.3747 | 97.2176
74 | Mahalingapur | 2 | 2 | 0:00 | 34:16 | 29:46 | 11:34 | 41:20 | 308:30 | 41:20 | 20:40 | 97.1296 | 97.1296 | 342:46 | 171:23 | 97.3659 | 97.0734
75 | Rabakavi | 2 | 2 | 0:30 | 28:50 | 8:01 | 4:00 | 12:01 | 206:35 | 12:31 | 6:16 | 99.1655 | 99.1308 | 235:25 | 117:42 | 98.2361 | 97.99
76 | Banahatti | 2 | 2 | 0:04 | 30:41 | 15:03 | 0:17 | 15:20 | 228:27 | 15:24 | 7:42 | 98.9352 | 98.9306 | 259:08 | 129:34 | 98.0494 | 97.7875
77 | Terdal | 1 | 1 | 0:00 | 34:17 | 17:02 | 8:00 | 25:02 | 208:27 | 25:02 | 25:02 | 96.5231 | 96.5231 | 242:44 | 242:44 | 96.4404 | 95.855
78 | Mudhol | 3 | 3 | 0:00 | 35:13 | 21:08 | 8:24 | 29:32 | 470:17 | 29:32 | 9:51 | 98.6327 | 98.6327 | 505:30 | 168:30 | 97.3231 | 97.1226
79 | Bilagi | 1 | 1 | 2:30 | 16:15 | 5:05 | 5:40 | 10:45 | 169:37 | 13:15 | 13:15 | 98.5069 | 98.1597 | 185:52 | 185:52 | 97.1035 | 96.826
80 | Lokapur | 2 | 2 | 5:10 | 28:05 | 76:20 | 2:45 | 79:05 | 623:35 | 84:15 | 42:08 | 94.5081 | 94.1493 | 651:40 | 325:50 | 94.6757 | 94.4359
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of December-2019
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of December-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 80 | 80 | 12:21 | 477:10 | 345:12 | 130:25 | 475:37 | 7134:51 | 487:58 | 6:06 | 99.2009 | 99.1802 | 7612:01 | 95:09 | 98.6487 | 98.5583
2 | Dharwad(R) | 18 | 18 | 32:50 | 202:18 | 282:46 | 105:18 | 388:04 | 3944:39 | 420:54 | 23:23 | 97.1023 | 96.8571 | 4146:57 | 230:23 | 96.6796 | 96.5093
3 | Kundagol | 1 | 1 | 1:35 | 175:10 | 3:55 | 0:20 | 4:15 | 119:00 | 5:50 | 5:50 | 99.4288 | 99.2159 | 294:10 | 294:10 | 98.197 | 95.5429
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 14:36 | 4:55 | 19:31 | 192:56 | 19:31 | 19:31 | 97.3768 | 97.3768 | 192:56 | 192:56 | 97.0768 | 97.0768
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 2:10 | 3:00 | 5:10 | 264:34 | 5:10 | 5:10 | 99.3056 | 99.3056 | 264:34 | 264:34 | 95.9914 | 95.9914
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 22:30 | 14:10 | 36:40 | 654:10 | 36:40 | 18:20 | 97.5358 | 97.5358 | 654:10 | 327:05 | 95.0442 | 95.0442
7 | Alnavar | 1 | 1 | 3:25 | 72:25 | 10:05 | 0:25 | 10:30 | 228:20 | 13:55 | 13:55 | 98.5887 | 98.1295 | 300:45 | 300:45 | 96.5404 | 95.4432
8 | Naragund | 2 | 2 | 2:50 | 58:30 | 21:05 | 18:05 | 39:10 | 636:25 | 42:00 | 21:00 | 97.3678 | 97.1774 | 694:55 | 347:28 | 95.1787 | 94.7355
9 | Shirahatti | 2 | 2 | 0:00 | 0:00 | 12:20 | 9:15 | 21:35 | 382:25 | 21:35 | 10:48 | 98.5495 | 98.5495 | 382:25 | 191:12 | 97.1029 | 97.1029
10 | Laxmeshwar | 6 | 6 | 0:00 | 0:00 | 84:25 | 17:39 | 102:04 | 1493:44 | 102:04 | 17:01 | 97.7136 | 97.7136 | 1493:44 | 248:57 | 96.2279 | 96.2279
11 | Naregal | 1 | 1 | 0:00 | 27:30 | 1:55 | 1:40 | 3:35 | 124:30 | 3:35 | 3:35 | 99.5184 | 99.5184 | 152:00 | 152:00 | 98.1136 | 97.697
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 17:05 | 6:15 | 23:20 | 421:00 | 23:20 | 11:40 | 98.4319 | 98.4319 | 421:00 | 210:30 | 96.8106 | 96.8106
13 | Ron | 3 | 3 | 1:15 | 61:05 | 12:35 | 5:25 | 18:00 | 438:16 | 19:15 | 6:25 | 99.1935 | 99.1375 | 499:21 | 166:27 | 97.7865 | 97.478
14 | Mundaragi | 3 | 3 | 3:00 | 65:40 | 37:40 | 10:05 | 47:45 | 786:40 | 50:45 | 16:55 | 97.8607 | 97.7263 | 852:20 | 284:07 | 96.0269 | 95.6953
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 30:10 | 9:45 | 39:55 | 453:38 | 39:55 | 39:55 | 94.6349 | 94.6349 | 453:38 | 453:38 | 93.1268 | 93.1268
16 | G.C.T.M | 1 | 1 | 3:15 | 115:55 | 9:05 | 0:55 | 10:00 | 262:35 | 13:15 | 13:15 | 98.6559 | 98.2191 | 378:30 | 378:30 | 96.0215 | 94.2652
17 | F.C.S.M | 2 | 2 | 4:20 | 200:25 | 3:25 | 0:00 | 3:25 | 262:00 | 7:45 | 3:52 | 99.7704 | 99.4792 | 462:25 | 231:13 | 98.0152 | 96.4968
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 4:06 | 0:05 | 4:11 | 158:54 | 4:11 | 4:11 | 99.4377 | 99.4377 | 158:54 | 158:54 | 97.5924 | 97.5924
19 | Hole-Alur | 1 | 1 | 1:30 | 63:10 | 14:15 | 1:20 | 15:35 | 236:40 | 17:05 | 17:05 | 97.9055 | 97.7039 | 299:50 | 299:50 | 96.4141 | 95.4571
20 | Savanur | 2 | 2 | 5:30 | 27:45 | 8:10 | 1:45 | 9:55 | 318:10 | 15:25 | 7:42 | 99.3336 | 98.9639 | 345:55 | 172:58 | 97.5896 | 97.3794
21 | Shiggaon | 2 | 2 | 16:45 | 125:10 | 10:35 | 11:30 | 22:05 | 344:40 | 38:50 | 19:25 | 98.5159 | 97.3902 | 469:50 | 234:55 | 97.3889 | 96.4407
22 | Bankapur | 1 | 1 | 9:15 | 113:40 | 5:35 | 6:15 | 11:50 | 131:55 | 21:05 | 21:05 | 98.4095 | 97.1662 | 245:35 | 245:35 | 98.0013 | 96.279
23 | Hangal | 2 | 2 | 2:10 | 38:00 | 41:45 | 9:55 | 51:40 | 558:55 | 53:50 | 26:55 | 96.5278 | 96.3822 | 596:55 | 298:28 | 95.7658 | 95.4779
24 | Ranebennur | 16 | 16 | 5:45 | 116:11 | 77:12 | 56:17 | 133:29 | 2610:44 | 139:14 | 8:42 | 98.8787 | 98.8304 | 2726:55 | 170:26 | 97.5277 | 97.4177
25 | Halageri | 2 | 2 | 6:10 | 180:40 | 6:25 | 0:40 | 7:05 | 107:50 | 13:15 | 6:38 | 99.524 | 99.1095 | 288:30 | 144:15 | 99.1831 | 97.8144
26 | Tuminakatti | 2 | 2 | 0:50 | 20:15 | 18:50 | 0:00 | 18:50 | 617:55 | 19:40 | 9:50 | 98.7343 | 98.6783 | 638:10 | 319:05 | 95.3188 | 95.1654
27 | Kahanderayanahalli | 2 | 2 | 8:15 | 124:43 | 61:40 | 1:25 | 63:05 | 776:44 | 71:20 | 35:40 | 95.7605 | 95.2061 | 901:27 | 450:44 | 94.1157 | 93.1708
28 | Rattihalli | 1 | 1 | 0:55 | 9:30 | 12:25 | 3:45 | 16:10 | 167:50 | 17:05 | 17:05 | 97.8271 | 97.7039 | 177:20 | 177:20 | 97.4571 | 97.3131
29 | Hirekerur | 3 | 3 | 12:40 | 210:30 | 59:40 | 13:10 | 72:50 | 933:50 | 85:30 | 28:30 | 96.7369 | 96.1694 | 1144:20 | 381:27 | 95.2837 | 94.2205
30 | Byadagi | 6 | 6 | 8:10 | 221:05 | 53:25 | 19:05 | 72:30 | 1783:45 | 80:40 | 13:27 | 98.3759 | 98.193 | 2004:50 | 334:08 | 95.4956 | 94.9373
31 | Sirsi | 5 | 5 | 0:50 | 229:48 | 12:55 | 6:25 | 19:20 | 475:19 | 20:10 | 4:02 | 99.4803 | 99.4579 | 705:07 | 141:01 | 98.5596 | 97.8633
32 | Yellapur | 3 | 3 | 14:41 | 189:15 | 18:00 | 1:40 | 19:40 | 638:18 | 34:21 | 11:27 | 99.1189 | 98.461 | 827:33 | 275:51 | 96.7763 | 95.8205
33 | Mundagod | 3 | 3 | 9:39 | 65:41 | 38:05 | 11:05 | 49:10 | 732:10 | 58:49 | 19:36 | 97.7972 | 97.3648 | 797:51 | 265:57 | 96.3022 | 95.9705
34 | Siddapur | 2 | 2 | 1:30 | 77:40 | 3:40 | 4:15 | 7:55 | 306:25 | 9:25 | 4:42 | 99.468 | 99.3672 | 384:05 | 192:02 | 97.6787 | 97.0903
35 | Dandeli | 8 | 8 | 32:36 | 430:12 | 89:53 | 21:53 | 111:46 | 1401:29 | 144:22 | 18:03 | 98.1222 | 97.5745 | 1831:41 | 228:58 | 97.3457 | 96.5309
36 | Haliyal | 3 | 3 | 0:00 | 23:42 | 10:02 | 5:30 | 15:32 | 316:42 | 15:32 | 5:11 | 99.3041 | 99.3041 | 340:24 | 113:28 | 98.4005 | 98.2808
37 | Ankola | 3 | 3 | 44:15 | 490:03 | 47:26 | 8:17 | 55:43 | 378:04 | 99:58 | 33:19 | 97.5037 | 95.5212 | 868:07 | 289:22 | 98.0906 | 95.6156
38 | Kumta | 3 | 3 | 3:48 | 62:21 | 7:26 | 10:42 | 18:08 | 422:49 | 21:56 | 7:19 | 99.1876 | 99.0173 | 485:10 | 161:43 | 97.8646 | 97.5497
39 | Gokarna | 1 | 1 | 4:40 | 191:11 | 8:15 | 0:10 | 8:25 | 54:13 | 13:05 | 13:05 | 98.8687 | 98.2415 | 245:24 | 245:24 | 99.1785 | 96.2818
40 | Kasargod | 1 | 1 | 5:28 | 129:46 | 1:40 | 0:55 | 2:35 | 169:50 | 8:03 | 8:03 | 99.6528 | 98.918 | 299:36 | 299:36 | 97.4268 | 95.4606
41 | Honnavar | 3 | 3 | 3:42 | 235:00 | 14:10 | 3:48 | 17:58 | 466:24 | 21:40 | 7:13 | 99.195 | 99.0293 | 701:24 | 233:48 | 97.6444 | 96.4576
42 | Murdeshwar | 4 | 4 | 6:12 | 328:24 | 23:22 | 6:57 | 30:19 | 847:20 | 36:31 | 9:08 | 98.9813 | 98.773 | 1175:44 | 293:56 | 96.7904 | 95.5465
43 | Bhatkal | 3 | 3 | 4:24 | 232:36 | 23:54 | 22:01 | 45:55 | 479:58 | 50:19 | 16:46 | 97.9428 | 97.7457 | 712:34 | 237:31 | 97.5759 | 96.4012
44 | Khanapur | 2 | 2 | 0:00 | 24:07 | 4:19 | 3:25 | 7:44 | 276:35 | 7:44 | 3:52 | 99.4803 | 99.4803 | 300:42 | 150:21 | 97.9047 | 97.722
45 | Bailhongal | 3 | 3 | 0:20 | 36:05 | 34:25 | 3:20 | 37:45 | 492:33 | 38:05 | 12:42 | 98.3087 | 98.2938 | 528:38 | 176:13 | 97.5124 | 97.3301
46 | Soundatti | 3 | 3 | 4:06 | 25:29 | 16:23 | 3:47 | 20:10 | 1085:37 | 24:16 | 8:05 | 99.0965 | 98.9128 | 1111:06 | 370:22 | 94.5171 | 94.3884
47 | Ramdurg | 2 | 2 | 2:10 | 25:50 | 7:25 | 4:05 | 11:30 | 376:30 | 13:40 | 6:50 | 99.2272 | 99.0815 | 402:20 | 201:10 | 97.1477 | 96.952
48 | Gokak | 7 | 7 | 28:45 | 206:55 | 132:00 | 21:05 | 153:05 | 1993:05 | 181:50 | 25:59 | 97.0606 | 96.5086 | 2200:00 | 314:17 | 95.686 | 95.2381
49 | Mudalagi | 2 | 2 | 1:40 | 59:20 | 13:35 | 8:00 | 21:35 | 369:25 | 23:15 | 11:38 | 98.5495 | 98.4375 | 428:45 | 214:22 | 97.2014 | 96.7519
50 | Konnur | 1 | 1 | 0:00 | 3:00 | 9:40 | 4:20 | 14:00 | 255:30 | 14:00 | 14:00 | 98.1183 | 98.1183 | 258:30 | 258:30 | 96.1288 | 96.0833
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 14:55 | 2:10 | 17:05 | 255:09 | 17:05 | 17:05 | 97.7039 | 97.7039 | 255:09 | 255:09 | 96.1341 | 96.1341
52 | Kudachi | 1 | 1 | 0:00 | 12:05 | 32:30 | 3:05 | 35:35 | 469:30 | 35:35 | 35:35 | 95.2173 | 95.2173 | 481:35 | 481:35 | 92.8864 | 92.7033
53 | Athani | 6 | 6 | 27:58 | 166:58 | 172:25 | 39:10 | 211:35 | 1274:58 | 239:33 | 39:56 | 95.2602 | 94.6337 | 1441:56 | 240:19 | 96.7804 | 96.3588
54 | Chikkodi | 2 | 2 | 0:00 | 1:40 | 13:15 | 3:55 | 17:10 | 163:40 | 17:10 | 8:35 | 98.8463 | 98.8463 | 165:20 | 82:40 | 98.7601 | 98.7475
55 | Nippani | 5 | 5 | 0:00 | 79:35 | 16:25 | 8:50 | 25:15 | 641:12 | 25:15 | 5:03 | 99.3212 | 99.3212 | 720:47 | 144:09 | 98.057 | 97.8158
56 | Sadalaga | 1 | 1 | 0:00 | 12:35 | 7:35 | 2:30 | 10:05 | 219:11 | 10:05 | 10:05 | 98.6447 | 98.6447 | 231:46 | 231:46 | 96.679 | 96.4884
57 | Muddebihal | 2 | 2 | 10:20 | 87:35 | 18:24 | 2:30 | 20:54 | 542:04 | 31:14 | 15:37 | 98.5954 | 97.901 | 629:39 | 314:50 | 95.8934 | 95.2299
58 | Talikot | 1 | 1 | 3:20 | 130:50 | 9:35 | 2:55 | 12:30 | 420:35 | 15:50 | 15:50 | 98.3199 | 97.8719 | 551:25 | 551:25 | 93.6275 | 91.6452
59 | B.Bagewadi | 1 | 1 | 2:40 | 45:31 | 3:30 | 1:28 | 4:58 | 102:09 | 7:38 | 7:38 | 99.3324 | 98.974 | 147:40 | 147:40 | 98.4523 | 97.7626
60 | Indi | 1 | 1 | 0:04 | 13:33 | 15:18 | 1:24 | 16:42 | 148:21 | 16:46 | 16:46 | 97.7554 | 97.7464 | 161:54 | 161:54 | 97.7523 | 97.547
61 | Sindagi | 2 | 2 | 1:40 | 177:30 | 11:05 | 3:55 | 15:00 | 213:45 | 16:40 | 8:20 | 98.9919 | 98.8799 | 391:15 | 195:38 | 98.3807 | 97.036
62 | Guledgudda | 1 | 1 | 0:00 | 3:13 | 3:30 | 1:39 | 5:09 | 262:53 | 5:09 | 5:09 | 99.3078 | 99.3078 | 266:06 | 266:06 | 96.0169 | 95.9682
63 | Ilkal | 8 | 8 | 10:15 | 502:15 | 88:35 | 72:06 | 160:41 | 1947:00 | 170:56 | 21:22 | 97.3003 | 97.1281 | 2449:15 | 306:09 | 96.3125 | 95.3613
64 | Kerur | 2 | 2 | 0:10 | 17:10 | 17:10 | 5:43 | 22:53 | 251:28 | 23:03 | 11:32 | 98.4621 | 98.4509 | 268:38 | 134:19 | 98.0949 | 97.9649
65 | Hungund | 3 | 3 | 3:18 | 127:15 | 24:01 | 9:35 | 33:36 | 802:45 | 36:54 | 12:18 | 98.4946 | 98.3468 | 930:00 | 310:00 | 95.9457 | 95.303
66 | GADDANKERI | 4 | 4 | 0:00 | 40:02 | 49:23 | 1:21 | 50:44 | 324:55 | 50:44 | 12:41 | 98.2953 | 98.2953 | 364:57 | 91:14 | 98.7693 | 98.6176
67 | RAMPUR | 1 | 1 | 0:00 | 0:00 | 2:24 | 0:06 | 2:30 | 2:48 | 2:30 | 2:30 | 99.664 | 99.664 | 2:48 | 2:48 | 99.9576 | 99.9576
68 | KALADAGI | 2 | 2 | 0:00 | 0:05 | 19:33 | 8:24 | 27:57 | 350:46 | 27:57 | 13:58 | 98.1216 | 98.1216 | 350:51 | 175:25 | 97.3427 | 97.342
69 | ACHANUR | 1 | 1 | 0:18 | 12:28 | 0:00 | 0:21 | 0:21 | 522:40 | 0:39 | 0:39 | 99.953 | 99.9126 | 535:08 | 535:08 | 92.0808 | 91.8919
70 | SHIRUR | 1 | 1 | 6:00 | 76:51 | 0:12 | 0:21 | 0:33 | 80:28 | 6:33 | 6:33 | 99.9261 | 99.1196 | 157:19 | 157:19 | 98.7808 | 97.6164
71 | BADAMI | 1 | 1 | 1:10 | 10:44 | 10:43 | 4:53 | 15:36 | 207:41 | 16:46 | 16:46 | 97.9032 | 97.7464 | 218:25 | 218:25 | 96.8533 | 96.6907
72 | KULAGERI | 1 | 1 | 0:07 | 4:51 | 3:54 | 5:00 | 8:54 | 47:29 | 9:01 | 9:01 | 98.8038 | 98.7881 | 52:20 | 52:20 | 99.2806 | 99.2071
73 | Jamkhandi | 5 | 5 | 0:00 | 45:59 | 49:23 | 5:10 | 54:33 | 823:15 | 54:33 | 10:55 | 98.5336 | 98.5336 | 869:14 | 173:51 | 97.5053 | 97.366
74 | Mahalingapur | 2 | 2 | 0:01 | 34:17 | 5:55 | 2:07 | 8:02 | 316:32 | 8:03 | 4:02 | 99.4601 | 99.459 | 350:49 | 175:24 | 97.602 | 97.3423
75 | Rabakavi | 2 | 2 | 0:00 | 28:50 | 8:20 | 2:35 | 10:55 | 217:30 | 10:55 | 5:28 | 99.2664 | 99.2664 | 246:20 | 123:10 | 98.3523 | 98.1338
76 | Banahatti | 2 | 2 | 0:00 | 30:41 | 19:18 | 0:50 | 20:08 | 248:35 | 20:08 | 10:04 | 98.647 | 98.647 | 279:16 | 139:38 | 98.1168 | 97.8843
77 | Terdal | 1 | 1 | 7:05 | 41:22 | 20:15 | 61:50 | 82:05 | 290:32 | 89:10 | 89:10 | 88.9673 | 88.0152 | 331:54 | 331:54 | 95.598 | 94.9712
78 | Mudhol | 3 | 3 | 0:00 | 35:13 | 62:26 | 4:30 | 66:56 | 537:13 | 66:56 | 22:19 | 97.0012 | 97.0012 | 572:26 | 190:49 | 97.2868 | 97.1089
79 | Bilagi | 1 | 1 | 2:30 | 18:45 | 6:05 | 5:40 | 11:45 | 181:22 | 14:15 | 14:15 | 98.4207 | 98.0847 | 200:07 | 200:07 | 97.252 | 96.9679
80 | Lokapur | 2 | 2 | 10:15 | 38:20 | 72:45 | 1:00 | 73:45 | 697:20 | 84:00 | 42:00 | 95.0437 | 94.3548 | 735:40 | 367:50 | 94.7172 | 94.4268
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of January-2020
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of January-2020 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 80 | 80 | 97:05 | 574:15 | 795:54 | 203:58 | 999:52 | 8134:43 | 1096:57 | 13:43 | 98.3201 | 98.157 | 8708:58 | 108:52 | 98.6154 | 98.5177
2 | Dharwad(R) | 18 | 18 | 1:15 | 203:33 | 99:23 | 85:04 | 184:27 | 4129:06 | 185:42 | 10:19 | 98.6227 | 98.6134 | 4332:39 | 240:42 | 96.8764 | 96.7225
3 | Kundagol | 1 | 1 | 1:30 | 176:40 | 1:10 | 0:15 | 1:25 | 120:25 | 2:55 | 2:55 | 99.8096 | 99.608 | 297:05 | 297:05 | 98.3603 | 95.9547
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 4:06 | 24:24 | 28:30 | 221:26 | 28:30 | 28:30 | 96.1694 | 96.1694 | 221:26 | 221:26 | 96.9848 | 96.9848
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 15:00 | 1:25 | 16:25 | 280:59 | 16:25 | 16:25 | 97.7935 | 97.7935 | 280:59 | 280:59 | 96.174 | 96.174
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 11:55 | 8:30 | 20:25 | 674:35 | 20:25 | 10:12 | 98.6279 | 98.6279 | 674:35 | 337:18 | 95.4072 | 95.4072
7 | Alnavar | 1 | 1 | 2:00 | 74:25 | 17:00 | 1:00 | 18:00 | 246:20 | 20:00 | 20:00 | 97.5806 | 97.3118 | 320:45 | 320:45 | 96.6458 | 95.6325
8 | Naragund | 2 | 2 | 4:50 | 63:20 | 17:55 | 17:40 | 35:35 | 672:00 | 40:25 | 20:12 | 97.6086 | 97.2838 | 735:20 | 367:40 | 95.4248 | 94.9936
9 | Shirahatti | 2 | 2 | 0:00 | 0:00 | 21:50 | 25:20 | 47:10 | 429:35 | 47:10 | 23:35 | 96.8302 | 96.8302 | 429:35 | 214:47 | 97.0753 | 97.0753
10 | Laxmeshwar | 6 | 6 | 0:00 | 0:00 | 69:20 | 11:36 | 80:56 | 1574:40 | 80:56 | 13:29 | 98.187 | 98.187 | 1574:40 | 262:27 | 96.4264 | 96.4264
11 | Naregal | 1 | 1 | 0:00 | 27:30 | 0:45 | 0:45 | 1:30 | 126:00 | 1:30 | 1:30 | 99.7984 | 99.7984 | 153:30 | 153:30 | 98.2843 | 97.9099
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 10:00 | 7:25 | 17:25 | 438:25 | 17:25 | 8:42 | 98.8295 | 98.8295 | 438:25 | 219:12 | 97.0151 | 97.0151
13 | Ron | 3 | 3 | 0:00 | 61:05 | 21:50 | 19:25 | 41:15 | 479:31 | 41:15 | 13:45 | 98.1519 | 98.1519 | 540:36 | 180:12 | 97.8235 | 97.5463
14 | Mundaragi | 3 | 3 | 3:15 | 68:55 | 20:50 | 14:05 | 34:55 | 821:35 | 38:10 | 12:43 | 98.4356 | 98.29 | 890:30 | 296:50 | 96.271 | 95.9582
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 6:25 | 9:13 | 15:38 | 469:16 | 15:38 | 15:38 | 97.8987 | 97.8987 | 469:16 | 469:16 | 93.6102 | 93.6102
16 | G.C.T.M | 1 | 1 | 11:15 | 127:10 | 10:55 | 1:15 | 12:10 | 274:45 | 23:25 | 23:25 | 98.3647 | 96.8526 | 401:55 | 401:55 | 96.2589 | 94.5273
17 | F.C.S.M | 2 | 2 | 16:00 | 216:25 | 10:15 | 1:40 | 11:55 | 273:55 | 27:55 | 13:58 | 99.1991 | 98.1239 | 490:20 | 245:10 | 98.1351 | 96.6617
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 18:30 | 0:40 | 19:10 | 178:04 | 19:10 | 19:10 | 97.4238 | 97.4238 | 178:04 | 178:04 | 97.5753 | 97.5753
19 | Hole-Alur | 1 | 1 | 0:00 | 63:10 | 1:50 | 1:50 | 3:40 | 240:20 | 3:40 | 3:40 | 99.5072 | 99.5072 | 303:30 | 303:30 | 96.7275 | 95.8674
20 | Savanur | 2 | 2 | 14:45 | 42:30 | 33:30 | 22:35 | 56:05 | 374:15 | 70:50 | 35:25 | 96.231 | 95.2397 | 416:45 | 208:22 | 97.452 | 97.1626
21 | Shiggaon | 2 | 2 | 24:00 | 149:10 | 12:00 | 5:03 | 17:03 | 361:43 | 41:03 | 20:32 | 98.8542 | 97.2413 | 510:53 | 255:26 | 97.5373 | 96.5218
22 | Bankapur | 1 | 1 | 36:15 | 149:55 | 12:55 | 6:45 | 19:40 | 151:35 | 55:55 | 55:55 | 97.3566 | 92.4843 | 301:30 | 301:30 | 97.936 | 95.8946
23 | Hangal | 2 | 2 | 3:55 | 41:55 | 20:55 | 7:40 | 28:35 | 587:30 | 32:30 | 16:15 | 98.0791 | 97.8159 | 629:25 | 314:42 | 96.0001 | 95.7148
24 | Ranebennur | 16 | 16 | 16:22 | 132:33 | 151:09 | 37:26 | 188:35 | 2799:19 | 204:57 | 12:49 | 98.4158 | 98.2783 | 2931:52 | 183:15 | 97.6177 | 97.5049
25 | Halageri | 2 | 2 | 21:40 | 202:20 | 10:25 | 1:10 | 11:35 | 119:25 | 33:15 | 16:37 | 99.2216 | 97.7655 | 321:45 | 160:52 | 99.187 | 97.8094
26 | Tuminakatti | 2 | 2 | 3:40 | 23:55 | 32:00 | 0:55 | 32:55 | 650:50 | 36:35 | 18:17 | 97.7879 | 97.5414 | 674:45 | 337:22 | 95.5689 | 95.4061
27 | Kahanderayanahalli | 2 | 2 | 22:20 | 147:03 | 62:50 | 8:40 | 71:30 | 848:14 | 93:50 | 46:55 | 95.1949 | 93.694 | 995:17 | 497:38 | 94.225 | 93.2238
28 | Rattihalli | 1 | 1 | 2:30 | 12:00 | 21:50 | 6:35 | 28:25 | 196:15 | 30:55 | 30:55 | 96.1806 | 95.8445 | 208:15 | 208:15 | 97.3278 | 97.1644
29 | Hirekerur | 2 | 2 | 22:15 | 232:45 | 10:30 | 12:25 | 22:55 | 956:45 | 45:10 | 22:35 | 98.4599 | 96.9646 | 1189:30 | 594:45 | 93.4862 | 91.9016
30 | Byadagi | 6 | 6 | 67:15 | 288:20 | 48:30 | 26:50 | 75:20 | 1859:05 | 142:35 | 23:46 | 98.3124 | 96.8059 | 2147:25 | 357:54 | 95.7809 | 95.1266
31 | Sirsi | 5 | 5 | 20:25 | 250:13 | 37:20 | 13:45 | 51:05 | 526:24 | 71:30 | 14:18 | 98.6268 | 98.078 | 776:37 | 155:19 | 98.5664 | 97.885
32 | Yellapur | 3 | 3 | 0:50 | 190:05 | 18:07 | 1:20 | 19:27 | 657:45 | 20:17 | 6:46 | 99.1286 | 99.0912 | 847:50 | 282:37 | 97.0146 | 96.1518
33 | Mundagod | 3 | 3 | 17:30 | 83:11 | 21:45 | 10:30 | 32:15 | 764:25 | 49:45 | 16:35 | 98.5551 | 97.7711 | 847:36 | 282:32 | 96.5304 | 96.1529
34 | Siddapur | 2 | 2 | 1:30 | 79:10 | 16:35 | 7:20 | 23:55 | 330:20 | 25:25 | 12:42 | 98.3927 | 98.2919 | 409:30 | 204:45 | 97.751 | 97.212
35 | Dandeli | 8 | 8 | 135:20 | 565:32 | 32:59 | 25:54 | 58:53 | 1460:22 | 194:13 | 24:17 | 99.0107 | 96.737 | 2025:54 | 253:14 | 97.5144 | 96.5518
36 | Haliyal | 3 | 3 | 0:00 | 23:42 | 7:51 | 4:15 | 12:06 | 328:48 | 12:06 | 4:02 | 99.4579 | 99.4579 | 352:30 | 117:30 | 98.5076 | 98.4001
37 | Ankola | 3 | 3 | 40:16 | 530:19 | 28:10 | 7:09 | 35:19 | 413:23 | 75:35 | 25:12 | 98.4177 | 96.6136 | 943:42 | 314:34 | 98.1237 | 95.7167
38 | Kumta | 3 | 3 | 0:00 | 62:21 | 8:39 | 12:52 | 21:31 | 444:20 | 21:31 | 7:10 | 99.036 | 99.036 | 506:41 | 168:54 | 97.9832 | 97.7002
39 | Gokarna | 1 | 1 | 11:25 | 202:36 | 5:20 | 0:50 | 6:10 | 60:23 | 17:35 | 17:35 | 99.1711 | 97.6366 | 262:59 | 262:59 | 99.1778 | 96.4191
40 | Kasarkod | 1 | 1 | 12:41 | 142:27 | 3:35 | 33:36 | 37:11 | 207:01 | 49:52 | 49:52 | 95.0022 | 93.2975 | 349:28 | 349:28 | 97.1811 | 95.2415
41 | Honnavar | 3 | 3 | 0:00 | 235:00 | 9:26 | 3:41 | 13:07 | 479:31 | 13:07 | 4:22 | 99.4123 | 99.4123 | 714:31 | 238:10 | 97.8235 | 96.7569
42 | Murdeshwar | 4 | 4 | 0:00 | 328:24 | 43:11 | 7:39 | 50:50 | 898:10 | 50:50 | 12:42 | 98.2919 | 98.2919 | 1226:34 | 306:38 | 96.9425 | 95.8246
43 | Bhatkal | 3 | 3 | 5:00 | 237:36 | 19:51 | 4:21 | 24:12 | 504:10 | 29:12 | 9:44 | 98.9158 | 98.6918 | 741:46 | 247:15 | 97.7117 | 96.6332
44 | Khanapur | 2 | 2 | 0:55 | 25:02 | 1:45 | 1:52 | 3:37 | 280:12 | 4:32 | 2:16 | 99.7569 | 99.6953 | 305:14 | 152:37 | 98.0923 | 97.9219
45 | Bailhongal | 3 | 3 | 1:54 | 37:59 | 7:10 | 5:14 | 12:24 | 504:57 | 14:18 | 4:46 | 99.4444 | 99.3593 | 542:56 | 180:59 | 97.7081 | 97.5357
46 | Soundatti | 3 | 3 | 0:00 | 25:29 | 17:27 | 3:06 | 20:33 | 1106:10 | 20:33 | 6:51 | 99.0793 | 99.0793 | 1131:39 | 377:13 | 94.9793 | 94.8636
47 | Ramdurg | 2 | 2 | 0:50 | 26:40 | 17:45 | 1:10 | 18:55 | 395:25 | 19:45 | 9:52 | 98.7287 | 98.6727 | 422:05 | 211:03 | 97.3079 | 97.1263
48 | Gokak | 7 | 7 | 0:35 | 207:30 | 159:30 | 17:30 | 177:00 | 2170:05 | 177:35 | 25:22 | 96.6014 | 96.5902 | 2377:35 | 339:39 | 95.7787 | 95.3751
49 | Mudalagi | 2 | 2 | 0:30 | 59:50 | 13:20 | 0:30 | 13:50 | 383:15 | 14:20 | 7:10 | 99.0703 | 99.0367 | 443:05 | 221:32 | 97.3907 | 96.9834
50 | Konnur | 1 | 1 | 0:00 | 3:00 | 10:15 | 0:55 | 11:10 | 266:40 | 11:10 | 11:10 | 98.4991 | 98.4991 | 269:40 | 269:40 | 96.3689 | 96.3281
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 9:30 | 1:55 | 11:25 | 266:34 | 11:25 | 11:25 | 98.4655 | 98.4655 | 266:34 | 266:34 | 96.3703 | 96.3703
52 | Kudachi | 1 | 1 | 0:00 | 12:05 | 23:45 | 8:30 | 32:15 | 501:45 | 32:15 | 32:15 | 95.6653 | 95.6653 | 513:50 | 513:50 | 93.1679 | 93.0034
53 | Athani | 6 | 6 | 7:00 | 173:58 | 60:40 | 15:03 | 75:43 | 1350:41 | 82:43 | 13:47 | 98.3038 | 98.147 | 1524:39 | 254:06 | 96.9347 | 96.5399
54 | Chikkodi | 2 | 2 | 0:00 | 1:40 | 17:50 | 3:40 | 21:30 | 185:10 | 21:30 | 10:45 | 98.5551 | 98.5551 | 186:50 | 93:25 | 98.7393 | 98.728
55 | Nippani | 5 | 5 | 53:20 | 132:55 | 48:40 | 21:25 | 70:05 | 711:17 | 123:25 | 24:41 | 98.116 | 96.6823 | 844:12 | 168:50 | 98.063 | 97.701
56 | Sadalaga | 1 | 1 | 0:00 | 12:35 | 2:40 | 0:50 | 3:30 | 222:41 | 3:30 | 3:30 | 99.5296 | 99.5296 | 235:16 | 235:16 | 96.9678 | 96.7965
57 | Muddebihal | 2 | 2 | 8:06 | 95:41 | 24:08 | 5:37 | 29:45 | 571:49 | 37:51 | 18:55 | 98.0007 | 97.4563 | 667:30 | 333:45 | 96.1069 | 95.4555
58 | Talikot | 1 | 1 | 3:05 | 133:55 | 11:25 | 4:30 | 15:55 | 436:30 | 19:00 | 19:00 | 97.8607 | 97.4462 | 570:25 | 570:25 | 94.0564 | 92.2329
59 | B.Bagewadi | 1 | 1 | 5:30 | 51:01 | 2:40 | 2:15 | 4:55 | 107:04 | 10:25 | 10:25 | 99.3392 | 98.5999 | 158:05 | 158:05 | 98.5421 | 97.8474
60 | Indi | 1 | 1 | 5:59 | 19:32 | 7:34 | 0:42 | 8:16 | 156:37 | 14:15 | 14:15 | 98.8889 | 98.0847 | 176:09 | 176:09 | 97.8674 | 97.6014
61 | Sindagi | 2 | 2 | 1:40 | 179:10 | 11:05 | 3:55 | 15:00 | 228:45 | 16:40 | 8:20 | 98.9919 | 98.8799 | 407:55 | 203:57 | 98.4426 | 97.2228
62 | Guledgudda | 1 | 1 | 0:07 | 3:20 | 6:00 | 2:17 | 8:17 | 271:10 | 8:24 | 8:24 | 98.8866 | 98.871 | 274:30 | 274:30 | 96.3076 | 96.2623
63 | Ilkal | 8 | 8 | 23:40 | 525:55 | 39:05 | 63:09 | 102:14 | 2049:14 | 125:54 | 15:44 | 98.2824 | 97.8847 | 2575:09 | 321:54 | 96.5121 | 95.6169
64 | Kerur | 2 | 2 | 4:42 | 21:52 | 14:26 | 3:56 | 18:22 | 269:50 | 23:04 | 11:32 | 98.7657 | 98.4498 | 291:42 | 145:51 | 98.1629 | 98.014
65 | Hungund | 3 | 3 | 3:09 | 130:24 | 41:43 | 1:30 | 43:13 | 845:58 | 46:22 | 15:27 | 98.0638 | 97.9226 | 976:22 | 325:27 | 96.1603 | 95.5684
66 | GADDANKERI | 4 | 4 | 0:00 | 40:02 | 45:55 | 16:42 | 62:37 | 387:32 | 62:37 | 15:39 | 97.8959 | 97.8959 | 427:34 | 106:54 | 98.6808 | 98.5445
67 | RAMPUR | 1 | 1 | 0:00 | 0:00 | 13:36 | 0:00 | 13:36 | 16:24 | 13:36 | 13:36 | 98.172 | 98.172 | 16:24 | 16:24 | 99.7767 | 99.7767
68 | KALADAGI | 2 | 2 | 0:00 | 0:05 | 6:30 | 0:57 | 7:27 | 358:13 | 7:27 | 3:44 | 99.4993 | 99.4993 | 358:18 | 179:09 | 97.5612 | 97.5606
69 | ACHANUR | 1 | 1 | 2:03 | 14:31 | 28:03 | 22:33 | 50:36 | 573:16 | 52:39 | 52:39 | 93.1989 | 92.9234 | 587:47 | 587:47 | 92.1941 | 91.9964
70 | SHIRUR | 1 | 1 | 3:15 | 80:06 | 5:45 | 0:30 | 6:15 | 86:43 | 9:30 | 9:30 | 99.1599 | 98.7231 | 166:49 | 166:49 | 98.8192 | 97.7285
71 | BADAMI | 1 | 1 | 0:45 | 11:29 | 14:49 | 2:18 | 17:07 | 224:48 | 17:52 | 17:52 | 97.6994 | 97.5986 | 236:17 | 236:17 | 96.939 | 96.7826
72 | KULAGERI | 1 | 1 | 0:45 | 5:36 | 0:40 | 0:00 | 0:40 | 48:09 | 1:25 | 1:25 | 99.9104 | 99.8096 | 53:45 | 53:45 | 99.3444 | 99.2681
73 | Jamkhandi | 5 | 5 | 17:55 | 63:54 | 17:17 | 4:21 | 21:38 | 844:53 | 39:33 | 7:55 | 99.4185 | 98.9368 | 908:47 | 181:45 | 97.6991 | 97.5251
74 | Mahalingapur | 2 | 2 | 3:06 | 37:23 | 23:09 | 2:06 | 25:15 | 341:47 | 28:21 | 14:10 | 98.3031 | 98.0948 | 379:10 | 189:35 | 97.673 | 97.4185
75 | Rabakavi | 2 | 2 | 6:30 | 35:20 | 7:46 | 0:25 | 8:11 | 225:41 | 14:41 | 7:20 | 99.45 | 99.0132 | 261:01 | 130:30 | 98.4635 | 98.2229
76 | Banahatti | 2 | 2 | 7:50 | 38:31 | 12:05 | 0:55 | 13:00 | 261:35 | 20:50 | 10:25 | 99.1263 | 98.5999 | 300:06 | 150:03 | 98.2191 | 97.9568
77 | Terdal | 1 | 1 | 0:00 | 41:22 | 43:35 | 2:45 | 46:20 | 336:52 | 46:20 | 46:20 | 93.7724 | 93.7724 | 378:14 | 378:14 | 95.413 | 94.8498
78 | Mudhol | 3 | 3 | 2:48 | 38:01 | 31:33 | 4:46 | 36:19 | 573:32 | 39:07 | 13:02 | 98.3729 | 98.2475 | 611:33 | 203:51 | 97.3968 | 97.2243
79 | Bilagi | 1 | 1 | 2:45 | 21:30 | 6:10 | 0:40 | 6:50 | 188:12 | 9:35 | 9:35 | 99.0815 | 98.7119 | 209:42 | 209:42 | 97.4374 | 97.1446
80 | Lokapur | 2 | 2 | 2:55 | 41:15 | 37:55 | 1:00 | 38:55 | 736:15 | 41:50 | 20:55 | 97.3846 | 97.1886 | 777:30 | 388:45 | 94.9874 | 94.7066
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of February-2020
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of February-2020 |  |  |  | Reliability for cumulative period from Apr-19 to Feb-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 80 | 80 | 33:21 | 607:36 | 1482:47 | 298:30 | 1781:17 | 9916:00 | 1814:38 | 22:41 | 96.8009 | 96.741 | 10523:36 | 131:33 | 98.4583 | 98.3639
2 | Dharwad(R) | 18 | 18 | 15:11 | 218:44 | 258:54 | 90:43 | 349:37 | 4478:43 | 364:48 | 20:16 | 97.2093 | 97.0881 | 4697:27 | 260:58 | 96.9053 | 96.7541
3 | Kundagol | 1 | 1 | 1:35 | 178:15 | 3:20 | 0:25 | 3:45 | 124:10 | 5:20 | 5:20 | 99.4612 | 99.2337 | 302:25 | 302:25 | 98.4556 | 96.2386
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 3:33 | 2:33 | 6:06 | 227:32 | 6:06 | 6:06 | 99.1236 | 99.1236 | 227:32 | 227:32 | 97.17 | 97.17
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 10:55 | 1:52 | 12:47 | 293:46 | 12:47 | 12:47 | 98.1633 | 98.1633 | 293:46 | 293:46 | 96.3462 | 96.3462
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 19:40 | 11:25 | 31:05 | 705:40 | 31:05 | 15:32 | 97.767 | 97.767 | 705:40 | 352:50 | 95.6115 | 95.6115
7 | Alnavar | 1 | 1 | 2:35 | 77:00 | 10:30 | 0:10 | 10:40 | 257:00 | 13:15 | 13:15 | 98.4674 | 98.0963 | 334:00 | 334:00 | 96.8035 | 95.8458
8 | Naragund | 2 | 2 | 18:40 | 82:00 | 17:15 | 51:55 | 69:10 | 741:10 | 87:50 | 43:55 | 95.0311 | 93.6901 | 823:10 | 411:35 | 95.3908 | 94.8808
9 | Shirahatti | 2 | 2 | 0:00 | 0:00 | 14:25 | 9:25 | 23:50 | 453:25 | 23:50 | 11:55 | 98.2878 | 98.2878 | 453:25 | 226:42 | 97.1802 | 97.1802
10 | Laxmeshwar | 6 | 6 | 0:00 | 0:00 | 42:58 | 22:19 | 65:17 | 1639:57 | 65:17 | 10:53 | 98.4367 | 98.4367 | 1639:57 | 273:20 | 96.6004 | 96.6004
11 | Naregal | 1 | 1 | 3:40 | 31:10 | 10:50 | 0:40 | 11:30 | 137:30 | 15:10 | 15:10 | 98.3477 | 97.8209 | 168:40 | 168:40 | 98.2898 | 97.9022
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 22:45 | 7:25 | 30:10 | 468:35 | 30:10 | 15:05 | 97.8329 | 97.8329 | 468:35 | 234:17 | 97.0859 | 97.0859
13 | Ron | 3 | 3 | 23:00 | 84:05 | 11:25 | 8:00 | 19:25 | 498:56 | 42:25 | 14:08 | 99.0701 | 97.9686 | 583:01 | 194:20 | 97.9315 | 97.5828
14 | Mundaragi | 3 | 3 | 1:30 | 70:25 | 21:55 | 11:55 | 33:50 | 855:25 | 35:20 | 11:47 | 98.3796 | 98.3078 | 925:50 | 308:37 | 96.4535 | 96.1616
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 25:00 | 5:04 | 30:04 | 499:20 | 30:04 | 30:04 | 95.6801 | 95.6801 | 499:20 | 499:20 | 93.7894 | 93.7894
16 | G.C.T.M | 1 | 1 | 5:30 | 132:40 | 6:25 | 0:35 | 7:00 | 281:45 | 12:30 | 12:30 | 98.9943 | 98.204 | 414:25 | 414:25 | 96.4956 | 94.8456
17 | F.C.S.M | 2 | 2 | 6:10 | 222:35 | 11:30 | 0:20 | 11:50 | 285:45 | 18:00 | 9:00 | 99.1499 | 98.7069 | 508:20 | 254:10 | 98.2229 | 96.8387
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 15:37 | 0:40 | 16:17 | 194:21 | 16:17 | 16:17 | 97.6604 | 97.6604 | 194:21 | 194:21 | 97.5827 | 97.5827
19 | Hole-Alur | 1 | 1 | 2:30 | 65:40 | 5:30 | 0:20 | 5:50 | 246:10 | 8:20 | 8:20 | 99.1619 | 98.8027 | 311:50 | 311:50 | 96.9382 | 96.1215
20 | Savanur | 2 | 2 | 6:30 | 49:00 | 21:00 | 14:05 | 35:05 | 409:20 | 41:35 | 20:48 | 97.4796 | 97.0127 | 458:20 | 229:10 | 97.4544 | 97.1497
21 | Shiggaon | 2 | 2 | 41:50 | 191:00 | 46:30 | 6:25 | 52:55 | 414:38 | 94:45 | 47:22 | 96.1985 | 93.1932 | 605:38 | 302:49 | 97.4214 | 96.2336
22 | Bankapur | 1 | 1 | 0:00 | 149:55 | 8:57 | 1:15 | 10:12 | 161:47 | 10:12 | 10:12 | 98.5345 | 98.5345 | 311:42 | 311:42 | 97.9878 | 96.1231
23 | Hangal | 2 | 2 | 0:30 | 42:25 | 21:15 | 3:15 | 24:30 | 612:00 | 25:00 | 12:30 | 98.2399 | 98.204 | 654:25 | 327:13 | 96.194 | 95.9302
24 | Ranebennur | 16 | 16 | 23:45 | 156:18 | 72:32 | 39:16 | 111:48 | 2911:07 | 135:33 | 8:28 | 98.996 | 98.7828 | 3067:25 | 191:43 | 97.737 | 97.6155
25 | Halageri | 2 | 2 | 17:50 | 220:10 | 9:15 | 0:55 | 10:10 | 129:35 | 28:00 | 14:00 | 99.2696 | 97.9885 | 349:45 | 174:52 | 99.1941 | 97.8249
26 | Tuminakatti | 2 | 2 | 1:20 | 25:15 | 104:55 | 0:15 | 105:10 | 756:00 | 106:30 | 53:15 | 92.4449 | 92.3491 | 781:15 | 390:37 | 95.2985 | 95.1415
27 | Kahanderayanahalli | 2 | 2 | 5:15 | 152:18 | 25:55 | 0:10 | 26:05 | 874:19 | 31:20 | 15:40 | 98.1262 | 97.749 | 1026:37 | 513:19 | 94.5627 | 93.6156
28 | Rattihalli | 1 | 1 | 0:30 | 12:30 | 9:00 | 6:10 | 15:10 | 211:25 | 15:40 | 15:40 | 97.8209 | 97.749 | 223:55 | 223:55 | 97.3704 | 97.215
29 | Hirekerur | 2 | 2 | 5:50 | 238:35 | 12:45 | 2:40 | 15:25 | 972:10 | 21:15 | 10:38 | 98.8925 | 98.4734 | 1210:45 | 605:22 | 93.9542 | 92.4705
30 | Byadagi | 6 | 6 | 30:10 | 318:30 | 50:45 | 21:00 | 71:45 | 1930:50 | 101:55 | 16:59 | 98.2818 | 97.5595 | 2249:20 | 374:53 | 95.9974 | 95.3372
31 | Sirsi | 5 | 5 | 2:30 | 252:43 | 50:25 | 12:40 | 63:05 | 589:29 | 65:35 | 13:07 | 98.1873 | 98.1154 | 842:12 | 168:26 | 98.5336 | 97.905
32 | Yellapur | 3 | 3 | 8:30 | 198:35 | 4:40 | 1:05 | 5:45 | 663:30 | 14:15 | 4:45 | 99.7246 | 99.3175 | 862:05 | 287:22 | 97.2492 | 96.4259
33 | Mundagod | 3 | 3 | 45:00 | 128:11 | 32:20 | 5:55 | 38:15 | 802:40 | 83:15 | 27:45 | 98.1681 | 96.0129 | 930:51 | 310:17 | 96.6722 | 96.1408
34 | Siddapur | 2 | 2 | 1:00 | 80:10 | 1:25 | 9:15 | 10:40 | 341:00 | 11:40 | 5:50 | 99.2337 | 99.1619 | 421:10 | 210:35 | 97.8794 | 97.3808
35 | Dandeli | 8 | 8 | 0:52 | 566:24 | 38:16 | 15:25 | 53:41 | 1514:03 | 54:33 | 6:49 | 99.0359 | 99.0203 | 2080:27 | 260:03 | 97.6461 | 96.7655
36 | Haliyal | 3 | 3 | 0:00 | 23:42 | 37:50 | 28:07 | 65:57 | 394:45 | 65:57 | 21:59 | 96.8415 | 96.8415 | 418:27 | 139:29 | 98.3634 | 98.2651
37 | Ankola | 3 | 3 | 25:58 | 556:17 | 9:01 | 5:27 | 14:28 | 427:51 | 40:26 | 13:29 | 99.3072 | 98.0635 | 984:08 | 328:03 | 98.2262 | 95.9198
38 | Kumta | 3 | 3 | 0:00 | 62:21 | 7:20 | 3:30 | 10:50 | 455:10 | 10:50 | 3:37 | 99.4812 | 99.4812 | 517:31 | 172:30 | 98.1129 | 97.8544
39 | Gokarna | 1 | 1 | 7:57 | 210:33 | 8:25 | 0:20 | 8:45 | 69:08 | 16:42 | 16:42 | 98.7428 | 97.6006 | 279:41 | 279:41 | 99.1401 | 96.5214
40 | Kasarkod | 1 | 1 | 11:05 | 153:32 | 2:25 | 0:30 | 2:55 | 209:56 | 14:00 | 14:00 | 99.5809 | 97.9885 | 363:28 | 363:28 | 97.3889 | 95.4793
41 | Honnavar | 3 | 3 | 0:00 | 235:00 | 4:51 | 3:21 | 8:12 | 487:43 | 8:12 | 2:44 | 99.6073 | 99.6073 | 722:43 | 240:54 | 97.978 | 97.0037
42 | Murdeshwar | 4 | 4 | 0:00 | 328:24 | 51:01 | 4:40 | 55:41 | 953:51 | 55:41 | 13:55 | 97.9999 | 97.9999 | 1282:15 | 320:34 | 97.034 | 96.0129
43 | Bhatkal | 3 | 3 | 32:06 | 269:42 | 37:29 | 22:32 | 60:01 | 564:11 | 92:07 | 30:42 | 97.1256 | 95.5883 | 833:53 | 277:58 | 97.6609 | 96.5428
44 | Khanapur | 2 | 2 | 0:00 | 25:02 | 9:15 | 3:25 | 12:40 | 292:52 | 12:40 | 6:20 | 99.09 | 99.09 | 317:54 | 158:57 | 98.1787 | 98.023
45 | Bailhongal | 3 | 3 | 0:00 | 37:59 | 13:00 | 4:10 | 17:10 | 522:07 | 17:10 | 5:43 | 99.1778 | 99.1778 | 560:06 | 186:42 | 97.8353 | 97.6779
46 | Soundatti | 3 | 3 | 19:48 | 45:17 | 13:15 | 2:35 | 15:50 | 1122:00 | 35:38 | 11:53 | 99.2417 | 98.2934 | 1167:17 | 389:06 | 95.3483 | 95.1605
47 | Ramdurg | 2 | 2 | 0:00 | 26:40 | 12:30 | 7:40 | 20:10 | 415:35 | 20:10 | 10:05 | 98.5512 | 98.5512 | 442:15 | 221:08 | 97.4155 | 97.2497
48 | Gokak | 7 | 7 | 1:10 | 208:40 | 120:05 | 12:35 | 132:40 | 2302:45 | 133:50 | 19:07 | 97.277 | 97.253 | 2511:25 | 358:46 | 95.9084 | 95.5376
49 | Mudalagi | 2 | 2 | 1:40 | 61:30 | 12:45 | 4:00 | 16:45 | 400:00 | 18:25 | 9:12 | 98.7967 | 98.677 | 461:30 | 230:45 | 97.5124 | 97.13
50 | Konnur | 1 | 1 | 0:00 | 3:00 | 9:20 | 0:55 | 10:15 | 276:55 | 10:15 | 10:15 | 98.5273 | 98.5273 | 279:55 | 279:55 | 96.5558 | 96.5184
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 7:10 | 3:20 | 10:30 | 277:04 | 10:30 | 10:30 | 98.4914 | 98.4914 | 277:04 | 277:04 | 96.5539 | 96.5539
52 | Kudachi | 1 | 1 | 0:30 | 12:35 | 42:10 | 4:05 | 46:15 | 548:00 | 46:45 | 46:45 | 93.3549 | 93.283 | 560:35 | 560:35 | 93.1841 | 93.0276
53 | Athani | 6 | 6 | 10:36 | 184:34 | 34:42 | 12:00 | 46:42 | 1397:23 | 57:18 | 9:33 | 98.8817 | 98.6279 | 1581:57 | 263:40 | 97.1033 | 96.7207
54 | Chikkodi | 2 | 2 | 0:00 | 1:40 | 4:00 | 2:25 | 6:25 | 191:35 | 6:25 | 3:12 | 99.539 | 99.539 | 193:15 | 96:37 | 98.8086 | 98.7982
55 | Nippani | 5 | 5 | 51:40 | 184:35 | 17:00 | 56:15 | 73:15 | 784:32 | 124:55 | 24:59 | 97.8951 | 96.4104 | 969:07 | 193:49 | 98.0484 | 97.5893
56 | Sadalaga | 1 | 1 | 0:00 | 12:35 | 5:45 | 1:30 | 7:15 | 229:56 | 7:15 | 7:15 | 98.9583 | 98.9583 | 242:31 | 242:31 | 97.1401 | 96.9836
57 | Muddebihal | 2 | 2 | 0:56 | 96:37 | 33:42 | 8:38 | 42:20 | 614:09 | 43:16 | 21:38 | 96.9588 | 96.8918 | 710:46 | 355:23 | 96.1807 | 95.5798
58 | Talikoti | 1 | 1 | 9:45 | 143:40 | 8:20 | 3:30 | 11:50 | 448:20 | 21:35 | 21:35 | 98.2998 | 96.8989 | 592:00 | 592:00 | 94.4237 | 92.6368
59 | B.Bagewadi | 1 | 1 | 1:00 | 52:01 | 2:22 | 0:40 | 3:02 | 110:06 | 4:02 | 4:02 | 99.5642 | 99.4205 | 162:07 | 162:07 | 98.6306 | 97.9836
60 | Indi | 1 | 1 | 0:35 | 20:07 | 9:49 | 1:42 | 11:31 | 168:08 | 12:06 | 12:06 | 98.3453 | 98.2615 | 188:15 | 188:15 | 97.9088 | 97.6586
61 | Sindagi | 2 | 2 | 0:10 | 179:20 | 5:15 | 2:00 | 7:15 | 236:00 | 7:25 | 3:42 | 99.4792 | 99.4672 | 415:20 | 207:40 | 98.5323 | 97.4171
62 | Guledgudda | 1 | 1 | 0:00 | 3:20 | 1:25 | 2:45 | 4:10 | 275:20 | 4:10 | 4:10 | 99.4013 | 99.4013 | 278:40 | 278:40 | 96.5755 | 96.534
63 | Ilkal | 8 | 8 | 11:00 | 536:55 | 110:10 | 91:53 | 202:03 | 2251:17 | 213:03 | 26:38 | 96.3712 | 96.1737 | 2788:12 | 348:32 | 96.4999 | 95.6651
64 | Kerur | 2 | 2 | 0:29 | 22:21 | 15:41 | 7:41 | 23:22 | 293:12 | 23:51 | 11:56 | 98.3214 | 98.2866 | 315:33 | 157:46 | 98.1766 | 98.0376
65 | Hungund | 3 | 3 | 3:36 | 134:00 | 37:00 | 0:00 | 37:00 | 882:58 | 40:36 | 13:32 | 98.228 | 98.0556 | 1016:58 | 338:59 | 96.3393 | 95.7837
66 | GADDANKERI | 4 | 4 | 6:48 | 46:50 | 76:26 | 2:29 | 78:55 | 466:27 | 85:43 | 21:26 | 97.1653 | 96.9211 | 513:17 | 128:19 | 98.5496 | 98.404
67 | RAMPUR | 1 | 1 | 0:00 | 0:00 | 15:03 | 0:15 | 15:18 | 31:42 | 15:18 | 15:18 | 97.8017 | 97.8017 | 31:42 | 31:42 | 99.6057 | 99.6057
68 | KALADAGI | 2 | 2 | 0:30 | 0:35 | 14:33 | 2:09 | 16:42 | 374:55 | 17:12 | 8:36 | 98.8003 | 98.7644 | 375:30 | 187:45 | 97.6684 | 97.6648
69 | ACHANUR | 1 | 1 | 0:00 | 14:31 | 41:30 | 0:09 | 41:39 | 614:55 | 41:39 | 41:39 | 94.0158 | 94.0158 | 629:26 | 629:26 | 92.3518 | 92.1712
70 | SHIRUR | 1 | 1 | 11:33 | 91:39 | 5:45 | 0:30 | 6:15 | 92:58 | 17:48 | 17:48 | 99.102 | 97.4425 | 184:37 | 184:37 | 98.8437 | 97.7038
71 | BADAMI | 1 | 1 | 0:50 | 12:19 | 17:30 | 4:00 | 21:30 | 246:18 | 22:20 | 22:20 | 96.9109 | 96.7912 | 258:37 | 258:37 | 96.9366 | 96.7834
72 | KULAGERI | 1 | 1 | 0:51 | 6:27 | 2:20 | 0:00 | 2:20 | 50:29 | 3:11 | 3:11 | 99.6648 | 99.5426 | 56:56 | 56:56 | 99.3721 | 99.2919
73 | Jamkhandi | 5 | 5 | 3:25 | 67:19 | 51:33 | 8:59 | 60:32 | 905:25 | 63:57 | 12:47 | 98.2605 | 98.1624 | 972:44 | 194:33 | 97.7477 | 97.5803
74 | Mahalingapur | 3 | 3 | 0:25 | 37:48 | 25:13 | 2:38 | 27:51 | 369:38 | 28:16 | 9:25 | 98.6662 | 98.6462 | 407:26 | 135:49 | 98.4675 | 98.3108
75 | Rabakavi | 2 | 2 | 4:10 | 39:30 | 4:45 | 2:00 | 6:45 | 232:26 | 10:55 | 5:28 | 99.5151 | 99.2158 | 271:56 | 135:58 | 98.5545 | 98.3089
76 | Banahatti | 2 | 2 | 1:33 | 40:04 | 3:13 | 1:48 | 5:01 | 266:36 | 6:34 | 3:17 | 99.6396 | 99.5283 | 306:40 | 153:20 | 98.342 | 98.0929
77 | Terdal | 1 | 1 | 6:03 | 47:25 | 11:15 | 1:55 | 13:10 | 350:02 | 19:13 | 19:13 | 98.1082 | 97.239 | 397:27 | 397:27 | 95.6464 | 95.0566
78 | Mudhol | 4 | 4 | 0:00 | 38:01 | 37:41 | 2:44 | 40:25 | 613:57 | 40:25 | 10:06 | 98.5483 | 98.5483 | 651:58 | 162:59 | 98.091 | 97.9727
79 | Bilagi | 1 | 1 | 0:25 | 21:55 | 10:45 | 0:50 | 11:35 | 199:47 | 12:00 | 12:00 | 98.3357 | 98.2759 | 221:42 | 221:42 | 97.5151 | 97.2425
80 | Lokapur | 2 | 2 | 5:25 | 46:40 | 69:20 | 0:45 | 70:05 | 806:20 | 75:30 | 37:45 | 94.9653 | 94.5761 | 853:00 | 426:30 | 94.9855 | 94.6953
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of March-2020
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of March-2020 |  |  |  | Reliability for cumulative period from Apr-19 to Mar-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 80 | 80 | 20:23 | 627:59 | 83:31 | 184:10 | 267:41 | 10183:41 | 288:04 | 3:36 | 99.5503 | 99.516 | 10811:40 | 135:09 | 98.5508 | 98.4615
2 | Dharwad(R) | 18 | 18 | 2:49 | 221:33 | 258:42 | 96:00 | 354:42 | 4833:25 | 357:31 | 19:52 | 97.3514 | 97.3304 | 5054:58 | 280:50 | 96.943 | 96.8029
3 | Kundagol | 1 | 1 | 2:45 | 181:00 | 3:15 | 9:36 | 12:51 | 137:01 | 15:36 | 15:36 | 98.2728 | 97.9032 | 318:01 | 318:01 | 98.4402 | 96.3796
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 9:00 | 4:55 | 13:55 | 241:27 | 13:55 | 13:55 | 98.1295 | 98.1295 | 241:27 | 241:27 | 97.2513 | 97.2513
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 11:15 | 3:25 | 14:40 | 308:26 | 14:40 | 14:40 | 98.0287 | 98.0287 | 308:26 | 308:26 | 96.4887 | 96.4887
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 14:10 | 6:30 | 20:40 | 726:20 | 20:40 | 10:20 | 98.6111 | 98.6111 | 726:20 | 363:10 | 95.8656 | 95.8656
7 | Alnavar | 1 | 1 | 5:45 | 82:45 | 12:55 | 9:25 | 22:20 | 279:20 | 28:05 | 28:05 | 96.9982 | 96.2254 | 362:05 | 362:05 | 96.82 | 95.8779
8 | Naragund | 2 | 2 | 18:40 | 100:40 | 17:15 | 51:55 | 69:10 | 810:20 | 87:50 | 43:55 | 95.3517 | 94.0972 | 911:00 | 455:30 | 95.3874 | 94.8144
9 | Shirahatti | 2 | 2 | 0:00 | 0:00 | 12:50 | 10:45 | 23:35 | 477:00 | 23:35 | 11:48 | 98.4151 | 98.4151 | 477:00 | 238:30 | 97.2848 | 97.2848
10 | Laxmeshwar | 6 | 6 | 0:00 | 0:00 | 35:25 | 18:26 | 53:51 | 1693:48 | 53:51 | 8:58 | 98.7937 | 98.7937 | 1693:48 | 282:18 | 96.7862 | 96.7862
11 | Naregal | 1 | 1 | 3:40 | 34:50 | 10:50 | 0:40 | 11:30 | 149:00 | 15:10 | 15:10 | 98.4543 | 97.9615 | 183:50 | 183:50 | 98.3037 | 97.9072
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 22:45 | 7:25 | 30:10 | 498:45 | 30:10 | 15:05 | 97.9727 | 97.9727 | 498:45 | 249:22 | 97.161 | 97.161
13 | Ron | 3 | 3 | 23:00 | 107:05 | 11:25 | 8:00 | 19:25 | 518:21 | 42:25 | 14:08 | 99.1301 | 98.0996 | 625:26 | 208:29 | 98.033 | 97.6266
14 | Mundaragi | 3 | 3 | 25:00 | 95:25 | 26:40 | 25:25 | 52:05 | 907:30 | 77:05 | 25:42 | 97.6665 | 96.5464 | 1002:55 | 334:18 | 96.5562 | 96.1942
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 9:00 | 7:07 | 16:07 | 515:27 | 16:07 | 16:07 | 97.8338 | 97.8338 | 515:27 | 515:27 | 94.1319 | 94.1319
16 | G.C.T.M | 1 | 1 | 8:25 | 141:05 | 22:50 | 2:50 | 25:40 | 307:25 | 34:05 | 34:05 | 96.5502 | 95.4189 | 448:30 | 448:30 | 96.5003 | 94.8941
17 | F.C.S.M | 2 | 2 | 4:00 | 226:35 | 8:30 | 0:35 | 9:05 | 294:50 | 13:05 | 6:33 | 99.3896 | 99.1207 | 521:25 | 260:43 | 98.3218 | 97.032
18 | KSRTC Colony | 1 | 1 | 0:00 | 0:00 | 8:40 | 1:53 | 10:33 | 204:54 | 10:33 | 10:33 | 98.582 | 98.582 | 204:54 | 204:54 | 97.6673 | 97.6673
19 | Hole-Alur | 1 | 1 | 2:30 | 68:10 | 5:30 | 0:20 | 5:50 | 252:00 | 8:20 | 8:20 | 99.2159 | 98.8799 | 320:10 | 320:10 | 97.1311 | 96.3551
20 | Savanur | 2 | 2 | 1:00 | 50:00 | 10:00 | 4:45 | 14:45 | 424:05 | 15:45 | 7:53 | 99.0087 | 98.9415 | 474:05 | 237:02 | 97.586 | 97.3014
21 | Shiggaon | 2 | 2 | 14:05 | 205:05 | 11:55 | 11:30 | 23:25 | 438:03 | 37:30 | 18:45 | 98.4263 | 97.4798 | 643:08 | 321:34 | 97.5065 | 96.3392
22 | Bankapur | 1 | 1 | 3:00 | 152:55 | 36:45 | 3:50 | 40:35 | 202:22 | 43:35 | 43:35 | 94.5453 | 94.142 | 355:17 | 355:17 | 97.6962 | 95.9553
23 | Hangal | 2 | 2 | 3:20 | 45:45 | 26:00 | 8:40 | 34:40 | 646:40 | 38:00 | 19:00 | 97.6703 | 97.4462 | 692:25 | 346:12 | 96.3191 | 96.0586
24 | Ranebennur | 16 | 16 | 19:50 | 176:08 | 67:59 | 35:26 | 103:25 | 3014:32 | 123:15 | 7:42 | 99.1312 | 98.9646 | 3190:40 | 199:25 | 97.8551 | 97.7298
25 | Halageri | 2 | 2 | 14:20 | 234:30 | 13:20 | 1:15 | 14:35 | 144:10 | 28:55 | 14:28 | 99.0199 | 98.0567 | 378:40 | 189:20 | 99.1794 | 97.8446
26 | Tuminakatti | 2 | 2 | 3:50 | 29:05 | 39:40 | 1:05 | 40:45 | 796:45 | 44:35 | 22:18 | 97.2614 | 97.0038 | 825:50 | 412:55 | 95.4648 | 95.2992
27 | Kahanderayanahalli | 1 | 1 | 1:40 | 153:58 | 3:35 | 15:25 | 19:00 | 893:19 | 20:40 | 20:40 | 97.4462 | 97.2222 | 1047:17 | 1047:17 | 89.8302 | 88.0774
28 | Rattihalli | 1 | 1 | 3:05 | 15:35 | 16:15 | 6:15 | 22:30 | 233:55 | 25:35 | 25:35 | 96.9758 | 96.5614 | 249:30 | 249:30 | 97.337 | 97.1596
29 | Hirekerur | 2 | 2 | 26:55 | 265:30 | 21:35 | 16:55 | 38:30 | 1010:40 | 65:25 | 32:43 | 97.4126 | 95.6037 | 1276:10 | 638:05 | 94.2471 | 92.7358
30 | Byadagi | 6 | 6 | 21:20 | 339:50 | 110:20 | 13:10 | 123:30 | 2054:20 | 144:50 | 24:08 | 97.2334 | 96.7555 | 2394:10 | 399:02 | 96.1021 | 95.4573
31 | Sirsi | 5 | 5 | 28:20 | 281:03 | 14:40 | 10:20 | 25:00 | 614:29 | 53:20 | 10:40 | 99.328 | 98.5663 | 895:32 | 179:06 | 98.6009 | 97.961
32 | Yellapur | 3 | 3 | 14:02 | 212:37 | 2:50 | 4:05 | 6:55 | 670:25 | 20:57 | 6:59 | 99.6901 | 99.0614 | 883:02 | 294:21 | 97.4559 | 96.6491
33 | Mundagod | 3 | 3 | 1:00 | 129:11 | 62:35 | 21:50 | 84:25 | 887:05 | 85:25 | 28:28 | 96.2179 | 96.1731 | 1016:16 | 338:45 | 96.6337 | 96.1435
34 | Siddapur | 2 | 2 | 7:26 | 87:36 | 4:45 | 6:27 | 11:12 | 352:12 | 18:38 | 9:19 | 99.2473 | 98.7478 | 439:48 | 219:54 | 97.9952 | 97.4966
35 | Dandeli | 8 | 8 | 89:44 | 656:08 | 117:58 | 166:27 | 284:25 | 1798:28 | 374:09 | 46:46 | 95.2215 | 93.7139 | 2454:36 | 306:50 | 97.4407 | 96.507
36 | Haliyal | 3 | 3 | 0:24 | 24:06 | 10:52 | 5:39 | 16:31 | 411:16 | 16:55 | 5:38 | 99.26 | 99.2421 | 435:22 | 145:07 | 98.4393 | 98.3479
37 | Ankola | 3 | 3 | 6:40 | 562:57 | 24:46 | 4:27 | 29:13 | 457:04 | 35:53 | 11:58 | 98.691 | 98.3923 | 1020:01 | 340:00 | 98.2655 | 96.1293
38 | Kumta | 3 | 3 | 0:00 | 62:21 | 23:21 | 4:27 | 27:48 | 482:58 | 27:48 | 9:16 | 98.7545 | 98.7545 | 545:19 | 181:46 | 98.1672 | 97.9306
39 | Gokarna | 1 | 1 | 2:11 | 212:44 | 5:00 | 5:00 | 10:00 | 79:08 | 12:11 | 12:11 | 98.6559 | 98.3625 | 291:52 | 291:52 | 99.0991 | 96.6773
40 | Kasarkod | 1 | 1 | 1:00 | 154:32 | 3:05 | 9:25 | 12:30 | 222:26 | 13:30 | 13:30 | 98.3199 | 98.1855 | 376:58 | 376:58 | 97.4677 | 95.7085
41 | Honnavar | 3 | 3 | 0:00 | 235:00 | 12:43 | 1:59 | 14:42 | 502:25 | 14:42 | 4:54 | 99.3414 | 99.3414 | 737:25 | 245:48 | 98.0934 | 97.2017
42 | Murdeshwar | 4 | 4 | 0:00 | 328:24 | 22:07 | 4:47 | 26:54 | 980:45 | 26:54 | 6:44 | 99.0961 | 99.0961 | 1309:09 | 327:17 | 97.2087 | 96.274
43 | Bhatkal | 3 | 3 | 9:09 | 278:51 | 9:04 | 4:00 | 13:04 | 577:15 | 22:13 | 7:24 | 99.4146 | 99.0046 | 856:06 | 285:22 | 97.8095 | 96.7513
44 | Khanapur | 2 | 2 | 9:20 | 34:22 | 16:20 | 11:10 | 27:30 | 320:22 | 36:50 | 18:25 | 98.1519 | 97.5246 | 354:44 | 177:22 | 98.1764 | 97.9808
45 | Bailhongal | 3 | 3 | 2:30 | 40:29 | 30:25 | 8:40 | 39:05 | 561:12 | 41:35 | 13:52 | 98.249 | 98.1369 | 601:41 | 200:34 | 97.8704 | 97.7167
46 | Soundatti | 3 | 3 | 0:00 | 45:17 | 22:18 | 3:53 | 26:11 | 1148:11 | 26:11 | 8:44 | 98.8269 | 98.8269 | 1193:28 | 397:49 | 95.6429 | 95.4711
47 | Ramdurg | 2 | 2 | 0:00 | 26:40 | 31:10 | 3:00 | 34:10 | 449:45 | 34:10 | 17:05 | 97.7039 | 97.7039 | 476:25 | 238:13 | 97.4399 | 97.2882
48 | Gokak | 7 | 7 | 0:00 | 208:40 | 232:30 | 28:50 | 261:20 | 2564:05 | 261:20 | 37:20 | 94.9821 | 94.9821 | 2772:45 | 396:06 | 95.8299 | 95.4906
49 | Mudalagi | 2 | 2 | 1:40 | 63:10 | 17:30 | 2:30 | 20:00 | 420:00 | 21:40 | 10:50 | 98.6559 | 98.5439 | 483:10 | 241:35 | 97.6093 | 97.2497
50 | Konnur | 1 | 1 | 0:00 | 3:00 | 25:35 | 2:20 | 27:55 | 304:50 | 27:55 | 27:55 | 96.2478 | 96.2478 | 307:50 | 307:50 | 96.5297 | 96.4955
51 | Raibag | 1 | 1 | 0:00 | 0:00 | 11:53 | 6:15 | 18:08 | 295:12 | 18:08 | 18:08 | 97.5627 | 97.5627 | 295:12 | 295:12 | 96.6393 | 96.6393
52 | Kudachi | 1 | 1 | 0:30 | 13:05 | 20:25 | 4:25 | 24:50 | 572:50 | 25:20 | 25:20 | 96.6622 | 96.595 | 585:55 | 585:55 | 93.4787 | 93.3297
53 | Athani | 6 | 6 | 20:38 | 205:12 | 42:30 | 44:15 | 86:45 | 1484:08 | 107:23 | 17:54 | 98.0567 | 97.5945 | 1689:20 | 281:33 | 97.184 | 96.7947
54 | Chikkodi | 2 | 2 | 0:00 | 1:40 | 20:20 | 5:25 | 25:45 | 217:20 | 25:45 | 12:52 | 98.2695 | 98.2695 | 219:00 | 109:30 | 98.7629 | 98.7534
55 | Nippani | 5 | 5 | 8:20 | 192:55 | 31:30 | 17:15 | 48:45 | 833:17 | 57:05 | 11:25 | 98.6895 | 98.4655 | 1026:12 | 205:14 | 98.1027 | 97.6635
56 | Sadalaga | 1 | 1 | 5:05 | 17:40 | 9:40 | 1:00 | 10:40 | 240:36 | 15:45 | 15:45 | 98.5663 | 97.8831 | 258:16 | 258:16 | 97.2609 | 97.0598
57 | Muddebihal | 2 | 2 | 3:50 | 100:27 | 34:42 | 14:05 | 48:47 | 662:56 | 52:37 | 26:19 | 96.7216 | 96.4639 | 763:23 | 381:42 | 96.2265 | 95.6547
58 | Talikoti | 1 | 1 | 6:00 | 149:40 | 10:35 | 1:10 | 11:45 | 460:05 | 17:45 | 17:45 | 98.4207 | 97.6142 | 609:45 | 609:45 | 94.7623 | 93.0584
59 | B.Bagewadi | 1 | 1 | 1:20 | 53:21 | 3:05 | 4:52 | 7:57 | 118:03 | 9:17 | 9:17 | 98.9315 | 98.7522 | 171:24 | 171:24 | 98.6561 | 98.0487
60 | Indi | 1 | 1 | 0:35 | 20:42 | 14:56 | 4:41 | 19:37 | 187:45 | 20:12 | 20:12 | 97.3634 | 97.2849 | 208:27 | 208:27 | 97.8626 | 97.6269
61 | Sindagi | 2 | 2 | 5:20 | 184:40 | 14:05 | 3:50 | 17:55 | 253:55 | 23:15 | 11:38 | 98.7959 | 98.4375 | 438:35 | 219:17 | 98.5547 | 97.5035
62 | Guledgudda | 1 | 1 | 0:07 | 3:27 | 6:00 | 2:17 | 8:17 | 283:37 | 8:24 | 8:24 | 98.8866 | 98.871 | 287:04 | 287:04 | 96.7712 | 96.7319
63 | Ilkal | 8 | 8 | 7:40 | 544:35 | 126:10 | 126:11 | 252:21 | 2503:38 | 260:01 | 32:30 | 95.7602 | 95.6314 | 3048:13 | 381:02 | 96.4372 | 95.6623
64 | Kerur | 2 | 2 | 0:53 | 23:14 | 14:49 | 6:07 | 20:56 | 314:08 | 21:49 | 10:54 | 98.5932 | 98.5338 | 337:22 | 168:41 | 98.2119 | 98.0797
65 | Hungund | 3 | 3 | 0:00 | 134:00 | 62:42 | 10:00 | 72:42 | 955:40 | 72:42 | 24:14 | 96.7428 | 96.7428 | 1089:40 | 363:13 | 96.3735 | 95.865
66 | GADDANKERI | 4 | 4 | 0:07 | 46:57 | 30:17 | 1:53 | 32:10 | 498:37 | 32:17 | 8:04 | 98.9191 | 98.9152 | 545:34 | 136:24 | 98.5809 | 98.4473
67 | RAMPUR | 1 | 1 | 0:30 | 0:30 | 4:18 | 1:03 | 5:21 | 37:03 | 5:51 | 5:51 | 99.2809 | 99.2137 | 37:33 | 37:33 | 99.5782 | 99.5725
68 | KALADAGI | 2 | 2 | 0:00 | 0:35 | 5:33 | 4:09 | 9:42 | 384:37 | 9:42 | 4:51 | 99.3481 | 99.3481 | 385:12 | 192:36 | 97.8107 | 97.8074
69 | ACHANUR | 1 | 1 | 0:15 | 14:46 | 10:09 | 18:18 | 28:27 | 643:22 | 28:42 | 28:42 | 96.1761 | 96.1425 | 658:08 | 658:08 | 92.6757 | 92.5076
70 | SHIRUR | 1 | 1 | 0:00 | 91:39 | 2:55 | 2:15 | 5:10 | 98:08 | 5:10 | 5:10 | 99.3056 | 99.3056 | 189:47 | 189:47 | 98.8828 | 97.8394
71 | BADAMI | 1 | 1 | 3:34 | 15:53 | 14:28 | 8:42 | 23:10 | 269:28 | 26:44 | 26:44 | 96.8862 | 96.4068 | 285:21 | 285:21 | 96.9323 | 96.7515
72 | KULAGERI | 1 | 1 | 0:37 | 7:04 | 6:03 | 0:20 | 6:23 | 56:52 | 7:00 | 7:00 | 99.142 | 99.0591 | 63:56 | 63:56 | 99.3526 | 99.2722
73 | Jamkhandi | 5 | 5 | 3:20 | 70:39 | 43:12 | 10:04 | 53:16 | 958:41 | 56:36 | 11:19 | 98.5681 | 98.4785 | 1029:20 | 205:52 | 97.8172 | 97.6563
74 | Mahalingapur | 3 | 3 | 0:35 | 38:23 | 27:31 | 5:32 | 33:03 | 402:41 | 33:38 | 11:13 | 98.5193 | 98.4931 | 441:04 | 147:01 | 98.4719 | 98.3262
75 | Rabakavi | 2 | 2 | 1:09 | 40:39 | 2:55 | 9:06 | 12:01 | 244:27 | 13:10 | 6:35 | 99.1924 | 99.1151 | 285:06 | 142:33 | 98.6085 | 98.3772
76 | Banahatti | 2 | 2 | 4:06 | 44:10 | 4:20 | 2:58 | 7:18 | 273:54 | 11:24 | 5:42 | 99.5094 | 99.2339 | 318:04 | 159:02 | 98.4409 | 98.1895
77 | Terdal | 1 | 1 | 0:50 | 48:15 | 3:23 | 0:15 | 3:38 | 353:40 | 4:28 | 4:28 | 99.5116 | 99.3996 | 401:55 | 401:55 | 95.9737 | 95.4244
78 | Mudhol | 4 | 4 | 13:28 | 51:29 | 85:40 | 5:14 | 90:54 | 704:51 | 104:22 | 26:05 | 96.9456 | 96.4931 | 756:20 | 189:05 | 97.9939 | 97.8474
79 | Bilagi | 1 | 1 | 9:50 | 31:45 | 10:00 | 0:15 | 10:15 | 210:02 | 20:05 | 20:05 | 98.6223 | 97.3006 | 241:47 | 241:47 | 97.6089 | 97.2475
80 | Lokapur | 2 | 2 | 1:55 | 48:35 | 45:30 | 0:35 | 46:05 | 852:25 | 48:00 | 24:00 | 96.903 | 96.7742 | 901:00 | 450:30 | 95.1479 | 94.8714
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]

## RURAL (Incl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2019
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2019 |  |  |  | Reliability for cumulative period from Apr-19
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 37 | 37 | 285:20 | 285:20 | 4651:04 | 1149:50 | 5800:54 | 5800:54 | 6086:14 | 164:30 | 78.2248 | 77.1538 | 6086:14 | 164:30 | 78.2248 | 77.1538
2 | Dharwad Rural | 64 | 64 | 605:49 | 605:49 | 10751:53 | 3169:22 | 13921:15 | 13921:15 | 14527:04 | 226:59 | 69.789 | 68.4742 | 14527:04 | 226:59 | 69.789 | 68.4742
3 | Gadag | 79 | 79 | 81:20 | 81:20 | 13412:09 | 2132:34 | 15544:43 | 15544:43 | 15626:03 | 197:48 | 72.671 | 72.528 | 15626:03 | 197:48 | 72.671 | 72.528
4 | Ron | 49 | 49 | 113:31 | 113:31 | 6006:15 | 1267:56 | 7274:11 | 7274:11 | 7387:42 | 150:46 | 79.3816 | 79.0598 | 7387:42 | 150:46 | 79.3816 | 79.0598
5 | Haveri | 185 | 185 | 1427:53 | 1427:53 | 2292.7792 | 5168:39 | 2508.1396 | 2508.1396 | 2567.6347 | 333:06 | 54.8083 | 53.7363 | 2567.6347 | 333:06 | 54.8083 | 53.7363
6 | Ranebennur | 169 | 169 | 608:08 | 608:08 | 2151.1201 | 3500:26 | 2296.9715 | 2296.9715 | 2322.3104 | 329:48 | 54.6948 | 54.1951 | 2322.3104 | 329:48 | 54.6948 | 54.1951
7 | Sirsi | 45 | 45 | 408:46 | 408:46 | 573:17 | 1467:32 | 2040:49 | 2040:49 | 2449:35 | 54:26 | 93.7012 | 92.4396 | 2449:35 | 54:26 | 93.7012 | 92.4396
8 | Dandeli | 18 | 18 | 21:40 | 21:40 | 349:19 | 535:37 | 884:56 | 884:56 | 906:36 | 50:22 | 93.1718 | 93.0046 | 906:36 | 50:22 | 93.1718 | 93.0046
9 | Karwar | 33 | 33 | 384:14 | 384:14 | 393:46 | 190:20 | 584:06 | 584:06 | 968:20 | 29:21 | 97.5417 | 95.9245 | 968:20 | 29:21 | 97.5417 | 95.9245
10 | Honnavar | 36 | 36 | 442:01 | 442:01 | 364:04 | 182:08 | 546:12 | 546:12 | 988:13 | 27:27 | 97.8927 | 96.1874 | 988:13 | 27:27 | 97.8927 | 96.1874
11 | Belagavi | 130 | 130 | 180:12 | 180:12 | 21115:48 | 2285:35 | 23401:23 | 23401:23 | 23581:35 | 181:24 | 74.9985 | 74.806 | 23581:35 | 181:24 | 74.9985 | 74.806
12 | Bailhongal | 173 | 173 | 1489:09 | 1489:09 | 1751.1188 | 3058:16 | 1878.5465 | 1878.5465 | 1940.5944 | 269:13 | 63.8045 | 62.609 | 1940.5944 | 269:13 | 63.8045 | 62.609
13 | Ramdurg | 69 | 69 | 673:10 | 673:10 | 22099:25 | 1071:05 | 23170:30 | 23170:30 | 23843:40 | 345:34 | 53.3605 | 52.0055 | 23843:40 | 345:34 | 53.3605 | 52.0055
14 | Ghataprabha | 153 | 153 | 269:34 | 269:34 | 1581.8667 | 860:20 | 1617.7139 | 1617.7139 | 1628.9458 | 255:31 | 64.7557 | 64.511 | 1628.9458 | 255:31 | 64.7557 | 64.511
15 | Raibag | 155 | 155 | 430:35 | 430:35 | 1702.5299 | 669:55 | 1730.4431 | 1730.4431 | 1748.384 | 270:43 | 62.7862 | 62.4003 | 1748.384 | 270:43 | 62.7862 | 62.4003
16 | Athani | 167 | 167 | 720:09 | 720:09 | 1621.1729 | 1036:42 | 1664.3688 | 1664.3688 | 1694.375 | 243:30 | 66.7791 | 66.1801 | 1694.375 | 243:30 | 66.7791 | 66.1801
17 | Chikkodi | 176 | 176 | 213:03 | 213:03 | 1856.316 | 742:01 | 1887.2333 | 1887.2333 | 1896.1104 | 258:34 | 64.2569 | 64.0888 | 1896.1104 | 258:34 | 64.2569 | 64.0888
18 | Vijayapur | 146 | 146 | 542:03 | 542:03 | 1448.6771 | 3610:46 | 1599.1257 | 1599.1257 | 1621.7111 | 266:35 | 63.4903 | 62.9746 | 1621.7111 | 266:35 | 63.4903 | 62.9746
19 | Indi | 222 | 222 | 1470:21 | 1470:21 | 2181.7965 | 3566:37 | 2330.4056 | 2330.4056 | 2391.6701 | 258:34 | 65.0089 | 64.089 | 2391.6701 | 258:34 | 65.0089 | 64.089
20 | B.Bagewadi | 110 | 110 | 591:36 | 591:36 | 1170.2771 | 1937:36 | 1251.0104 | 1251.0104 | 1275.6604 | 278:20 | 62.0906 | 61.3436 | 1275.6604 | 278:20 | 62.0906 | 61.3436
21 | Bagalkot | 156 | 156 | 528:32 | 528:32 | 1367.0972 | 3354:28 | 1506.8667 | 1506.8667 | 1528.8889 | 235:13 | 67.802 | 67.3314 | 1528.8889 | 235:13 | 67.802 | 67.3314
22 | Jamkhandi | 214 | 214 | 559:18 | 559:18 | 2450.5764 | 1412:33 | 2509.4326 | 2509.4326 | 2532.7368 | 284:03 | 60.9123 | 60.5493 | 2532.7368 | 284:03 | 60.9123 | 60.5493
23 | Mudhol | 154 | 154 | 168:23 | 168:23 | 2069.909 | 1135:34 | 2117.2243 | 2117.2243 | 2124.2403 | 331:03 | 54.1726 | 54.0208 | 2124.2403 | 331:03 | 54.1726 | 54.0208
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2019
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 37 | 37 | 208:00 | 493:20 | 4322:02 | 1287:46 | 5609:48 | 11410:42 | 5817:48 | 157:14 | 79.6215 | 78.8659 | 11904:02 | 321:44 | 78.9346 | 78.0239
2 | Dharwad Rural | 64 | 64 | 442:19 | 1048:08 | 11435:01 | 1813:10 | 13248:11 | 1132.0597 | 13690:30 | 213:55 | 72.177 | 71.2481 | 1175.7319 | 440:54 | 71.0026 | 69.8839
3 | Gadag | 79 | 79 | 225:20 | 306:40 | 14626:10 | 2223:23 | 16849:33 | 1349.7611 | 17074:53 | 216:08 | 71.3326 | 70.9492 | 1362.5389 | 413:56 | 71.9908 | 71.7257
4 | Ron | 49 | 49 | 335:02 | 448:33 | 5647:00 | 1391:59 | 7038:59 | 14313:10 | 7374:01 | 150:29 | 80.6918 | 79.7728 | 14761:43 | 301:16 | 80.0474 | 79.4222
5 | Haveri | 188 | 188 | 1271:35 | 2699:28 | 2414.4826 | 3173:56 | 2546.7299 | 5054.8694 | 2599.7125 | 331:53 | 56.3018 | 55.3927 | 5167.3472 | 659:40 | 55.922 | 54.9412
6 | Ranebennur | 169 | 169 | 916:10 | 1524:18 | 2281.8056 | 2844:26 | 2400.3236 | 4697.2951 | 2438.4972 | 346:18 | 54.1836 | 53.4549 | 4760.8076 | 676:05 | 54.435 | 53.8189
7 | Sirsi | 46 | 46 | 263:56 | 672:42 | 874:08 | 994:15 | 1868:23 | 3909:12 | 2132:19 | 46:21 | 94.5407 | 93.7695 | 4581:54 | 99:36 | 94.1952 | 93.1963
8 | Dandeli | 18 | 18 | 4:17 | 25:57 | 264:01 | 355:34 | 619:35 | 1504:31 | 623:52 | 34:40 | 95.3735 | 95.3415 | 1530:28 | 85:02 | 94.2907 | 94.1922
9 | Karwar | 33 | 33 | 607:36 | 991:50 | 561:52 | 465:44 | 1027:36 | 1611:42 | 1635:12 | 49:33 | 95.8146 | 93.3399 | 2603:32 | 78:54 | 96.664 | 94.611
10 | Honnavar | 36 | 36 | 714:19 | 1156:20 | 486:44 | 222:35 | 709:19 | 1255:31 | 1423:38 | 39:33 | 97.3517 | 94.6848 | 2411:51 | 67:00 | 97.6178 | 95.4238
11 | Belagavi | 131 | 131 | 325:31 | 505:43 | 21903:49 | 1755:04 | 23658:53 | 1960.8444 | 23984:24 | 183:05 | 75.7255 | 75.3915 | 1981.916 | 363:06 | 75.4618 | 75.1981
12 | Bailhongal | 175 | 175 | 1381:52 | 2871:01 | 1770.934 | 3044:45 | 1897.7986 | 3776.3451 | 1955.3764 | 268:10 | 65.0175 | 63.9562 | 3895.9708 | 534:18 | 64.6244 | 63.5038
13 | Ramdurg | 69 | 69 | 501:10 | 1174:20 | 22903:55 | 1594:10 | 1020.7535 | 1986.191 | 1041.6354 | 362:18 | 52.2789 | 51.3027 | 2035.1215 | 707:52 | 52.8109 | 51.6483
14 | Ghataprabha | 153 | 153 | 809:07 | 1078:41 | 1655.8194 | 1942:45 | 1736.7674 | 3354.4813 | 1770.4806 | 277:43 | 63.3825 | 62.6717 | 3399.4264 | 533:15 | 64.0578 | 63.5763
15 | Raibag | 156 | 156 | 658:43 | 1089:18 | 1710.2382 | 1215:26 | 1760.8812 | 3491.3243 | 1788.3278 | 275:08 | 63.5881 | 63.0205 | 3536.7118 | 544:07 | 63.311 | 62.834
16 | Athani | 167 | 167 | 721:12 | 1441:21 | 1603.6104 | 1833:02 | 1679.9868 | 3344.3556 | 1710.0368 | 245:45 | 67.549 | 66.9686 | 3404.4118 | 489:15 | 67.1704 | 66.5808
17 | Chikkodi | 176 | 176 | 677:58 | 891:01 | 2029.9576 | 1030:06 | 2072.8785 | 3960.1118 | 2101.1271 | 286:31 | 62.0074 | 61.4896 | 3997.2375 | 545:05 | 63.1137 | 62.7679
18 | Vijayapur | 146 | 146 | 786:04 | 1328:07 | 1456.5521 | 3319:33 | 1594.8667 | 3193.9924 | 1627.6194 | 267:33 | 64.7621 | 64.0385 | 3249.3306 | 534:08 | 64.1366 | 63.5153
19 | Indi | 223 | 223 | 1006:49 | 2477:10 | 2714.1229 | 2894:28 | 2834.7257 | 5165.1313 | 2876.6764 | 309:36 | 58.9943 | 58.3874 | 5268.3465 | 567:00 | 62.0295 | 61.2707
20 | B.Bagewadi | 110 | 110 | 965:25 | 1557:01 | 1212.6667 | 2629:02 | 1322.2097 | 2573.2201 | 1362.4354 | 297:16 | 61.2255 | 60.0459 | 2638.0958 | 575:35 | 61.651 | 60.6841
21 | Bagalkot | 156 | 156 | 1889:33 | 2418:05 | 1438.4764 | 3959:07 | 1603.4396 | 3110.3062 | 1682.1708 | 258:48 | 66.8437 | 65.2157 | 3211.0597 | 494:01 | 67.315 | 66.2562
22 | Jamkhandi | 214 | 214 | 1232:42 | 1792:00 | 2426.7694 | 2189:19 | 2517.991 | 5027.4236 | 2569.3535 | 288:09 | 62.0442 | 61.2699 | 5102.0903 | 572:12 | 61.4875 | 60.9155
23 | Mudhol | 155 | 155 | 112:58 | 281:21 | 2161.8285 | 1868:56 | 2239.7007 | 4356.925 | 2244.4076 | 347:31 | 53.3881 | 53.2902 | 4368.6479 | 676:26 | 53.9194 | 53.7954
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2019
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 37 | 37 | 321:45 | 815:05 | 4515:07 | 2052:41 | 6567:48 | 17978:30 | 6889:33 | 186:12 | 75.3461 | 74.1383 | 18793:35 | 507:56 | 77.7516 | 76.7429
2 | Dharwad Rural | 64 | 64 | 209:16 | 1257:24 | 10809:10 | 3564:30 | 14373:40 | 1730.9625 | 14582:56 | 227:52 | 68.8071 | 68.353 | 1783.3542 | 668:45 | 70.2788 | 69.3792
3 | Gadag | 79 | 79 | 195:30 | 502:10 | 13558:27 | 3296:09 | 16854:36 | 2052.0361 | 17050:06 | 215:49 | 70.3681 | 70.0244 | 2072.9597 | 629:46 | 71.4559 | 71.1648
4 | Ron | 49 | 49 | 218:50 | 667:23 | 5750:30 | 2257:40 | 8008:10 | 22321:20 | 8227:00 | 167:54 | 77.3011 | 76.6808 | 22988:43 | 469:09 | 79.1421 | 78.5184
5 | Haveri | 188 | 188 | 2289:36 | 4989:04 | 2202.8986 | 10062:26 | 2622.1667 | 7677.0361 | 2717.5667 | 346:55 | 53.5077 | 51.8162 | 7884.9139 | 1006:35 | 55.126 | 53.911
6 | Ranebennur | 169 | 169 | 1454:43 | 2979:01 | 2122.6986 | 7555:33 | 2437.5132 | 7134.8083 | 2498.1264 | 354:46 | 51.9228 | 50.7273 | 7258.934 | 1030:51 | 53.6068 | 52.7997
7 | Sirsi | 49 | 49 | 457:17 | 1129:59 | 1204:36 | 3034:24 | 4239:00 | 8148:12 | 4696:17 | 95:51 | 87.9847 | 86.6885 | 9278:11 | 189:21 | 92.386 | 91.3301
8 | Dandeli | 19 | 19 | 50:47 | 76:44 | 379:40 | 707:26 | 1087:06 | 2591:37 | 1137:53 | 59:53 | 92.0534 | 91.6821 | 2668:21 | 140:26 | 93.7545 | 93.5696
9 | Karwar | 33 | 33 | 861:25 | 1853:15 | 583:34 | 1324:37 | 1908:11 | 3519:53 | 2769:36 | 83:56 | 91.9689 | 88.3434 | 5373:08 | 162:49 | 95.1162 | 92.5448
10 | Honnavar | 36 | 36 | 846:53 | 2003:13 | 826:38 | 1502:34 | 2329:12 | 3584:43 | 3176:05 | 88:13 | 91.0139 | 87.7466 | 5587:56 | 155:13 | 95.4407 | 92.8928
11 | Belagavi | 131 | 131 | 689:53 | 1195:36 | 20014:36 | 3927:41 | 23942:17 | 2958.4396 | 1026.3403 | 188:02 | 74.6159 | 73.8845 | 3008.2562 | 551:08 | 75.183 | 74.7651
12 | Bailhongal | 175 | 175 | 2493:17 | 5364:18 | 1586.2354 | 7595:34 | 1902.7174 | 5679.0625 | 2006.6042 | 275:11 | 63.7578 | 61.779 | 5902.575 | 809:30 | 64.3387 | 62.9352
13 | Ramdurg | 69 | 69 | 931:10 | 2105:30 | 21614:38 | 3423:15 | 1043.2451 | 3029.4361 | 1082.0437 | 376:22 | 49.6017 | 47.7274 | 3117.1653 | 1084:14 | 51.7529 | 50.3557
14 | Ghataprabha | 153 | 153 | 580:16 | 1658:57 | 1608.9757 | 4562:42 | 1799.0882 | 5153.5694 | 1823.266 | 286:00 | 60.8042 | 60.2774 | 5222.6924 | 819:15 | 62.9852 | 62.4887
15 | Raibag | 154 | 154 | 357:10 | 1446:28 | 2017.541 | 5007:13 | 2226.175 | 5717.4993 | 2241.0569 | 349:15 | 51.8144 | 51.4923 | 5777.7688 | 900:26 | 59.2015 | 58.7715
16 | Athani | 168 | 168 | 704:43 | 2146:04 | 1617.6215 | 3424:59 | 1760.3292 | 5104.6847 | 1789.6924 | 255:40 | 65.0728 | 64.4902 | 5194.1042 | 742:01 | 66.6099 | 66.025
17 | Chikkodi | 176 | 176 | 411:10 | 1302:11 | 1987.1 | 3010:28 | 2112.5361 | 6072.6479 | 2129.6681 | 290:25 | 59.9898 | 59.6654 | 6126.9056 | 835:29 | 62.0839 | 61.7451
18 | Vijayapur | 146 | 146 | 1144:04 | 2472:11 | 1364.209 | 6807:51 | 1647.8694 | 4841.8618 | 1695.5389 | 278:43 | 62.3774 | 61.2891 | 4944.8694 | 812:51 | 63.5567 | 62.7814
19 | Indi | 223 | 223 | 1492:46 | 3969:56 | 2569.3813 | 7073:09 | 2864.0958 | 8029.2271 | 2926.2947 | 314:56 | 57.1884 | 56.2587 | 8194.6413 | 881:56 | 60.4335 | 59.6184
20 | B.Bagewadi | 111 | 111 | 2186:30 | 3743:31 | 1131.7118 | 7083:35 | 1426.8611 | 4000.0812 | 1517.9653 | 328:13 | 57.1513 | 54.4155 | 4156.0611 | 898:36 | 60.3992 | 58.855
21 | Bagalkot | 144 | 144 | 1279:42 | 3697:47 | 1176.9736 | 9642:06 | 1578.7278 | 4689.034 | 1632.0486 | 272:00 | 63.4554 | 62.2211 | 4843.1083 | 807:11 | 64.2168 | 63.041
22 | Jamkhandi | 214 | 214 | 3761:56 | 5553:56 | 2302.8889 | 4559:24 | 2492.8639 | 7520.2875 | 2649.6111 | 297:09 | 61.1703 | 58.7288 | 7751.7014 | 869:21 | 61.3829 | 60.1946
23 | Mudhol | 153 | 153 | 1211:26 | 1492:47 | 2073.025 | 4038:27 | 2241.2937 | 6598.2188 | 2291.7701 | 359:30 | 51.1701 | 50.0704 | 6660.4181 | 1044:46 | 52.6092 | 52.1625
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of July-2019
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 43 | 43 | 251:25 | 1066:30 | 4893:18 | 1324:28 | 6217:46 | 1008.1778 | 6469:11 | 150:27 | 80.5646 | 79.7787 | 1052.6153 | 587:30 | 80.782 | 79.9349
2 | Dharwad Rural | 64 | 64 | 144:55 | 1402:19 | 10682:54 | 3472:15 | 14155:09 | 2320.7604 | 14300:04 | 223:26 | 70.2723 | 69.9679 | 2379.1903 | 892:12 | 70.2771 | 69.5288
3 | Gadag | 79 | 79 | 271:55 | 774:05 | 12303:38 | 3448:17 | 15751:55 | 2708.366 | 16023:50 | 202:50 | 73.2001 | 72.7375 | 2740.6194 | 832:36 | 71.8991 | 71.5644
4 | Ron | 51 | 51 | 220:47 | 888:10 | 6516:05 | 1398:35 | 7914:40 | 1259.8333 | 8135:27 | 159:31 | 79.1412 | 78.5593 | 1296.8403 | 610:17 | 79.752 | 79.1572
5 | Haveri | 189 | 189 | 1491:19 | 6480:23 | 2175.009 | 10670:31 | 2619.6139 | 10296.65 | 2681.7521 | 340:32 | 55.2891 | 54.2285 | 10566.666 | 1341:48 | 55.3446 | 54.1735
6 | Ranebennur | 169 | 169 | 578:05 | 3557:06 | 2152.4208 | 6696:54 | 2431.4583 | 9566.2667 | 2455.5451 | 348:43 | 53.5893 | 53.1295 | 9714.4792 | 1379:34 | 53.6024 | 52.8835
7 | Sirsi | 51 | 51 | 220:30 | 1350:29 | 1184:12 | 2718:28 | 3902:40 | 12050:52 | 4123:10 | 80:51 | 89.7147 | 89.1335 | 13401:21 | 262:46 | 91.9299 | 91.0256
8 | Dandeli | 19 | 19 | 57:48 | 134:32 | 518:17 | 555:04 | 1073:21 | 3664:58 | 1131:09 | 59:32 | 92.407 | 91.9981 | 3799:30 | 199:58 | 93.4121 | 93.1703
9 | Karwar | 33 | 33 | 524:32 | 2377:47 | 571:17 | 1000:31 | 1571:48 | 5091:41 | 2096:20 | 63:32 | 93.5981 | 91.4617 | 7469:28 | 226:21 | 94.7304 | 92.2696
10 | Honnavar | 36 | 36 | 1132:30 | 3135:43 | 810:33 | 1206:13 | 2016:46 | 5601:29 | 3149:16 | 87:29 | 92.4703 | 88.242 | 8737:12 | 242:42 | 94.6859 | 91.7111
11 | Belagavi | 132 | 132 | 398:32 | 1594:08 | 20000:40 | 3772:54 | 23773:34 | 3949.0049 | 1007.1708 | 183:07 | 75.7926 | 75.3868 | 4015.4271 | 730:05 | 75.4781 | 75.0657
12 | Bailhongal | 179 | 179 | 381:16 | 5745:34 | 1643.9118 | 6320:04 | 1907.2479 | 7586.3104 | 1923.134 | 257:51 | 65.629 | 65.3427 | 7825.709 | 1049:15 | 65.261 | 64.1647
13 | Ramdurg | 69 | 69 | 209:10 | 2314:40 | 23504:31 | 1760:00 | 1052.6882 | 4082.1243 | 1061.4035 | 369:11 | 50.786 | 50.3785 | 4178.5687 | 1453:25 | 51.5072 | 50.3615
14 | Ghataprabha | 153 | 153 | 455:40 | 2114:37 | 1579.175 | 2160:38 | 1669.2014 | 6822.7708 | 1688.1875 | 264:49 | 64.8071 | 64.4068 | 6910.8799 | 1084:04 | 63.4481 | 62.9761
15 | Raibag | 154 | 154 | 445:34 | 1892:02 | 1664.5083 | 2557:15 | 1771.0604 | 7488.5597 | 1789.6257 | 278:54 | 62.902 | 62.5131 | 7567.3944 | 1179:20 | 60.1418 | 59.7222
16 | Athani | 173 | 173 | 549:05 | 2695:09 | 1556.1549 | 3180:37 | 1688.6806 | 6793.3653 | 1711.559 | 237:27 | 68.5124 | 68.0858 | 6905.6632 | 958:01 | 67.8131 | 67.281
17 | Chikkodi | 176 | 176 | 351:43 | 1653:54 | 1963.2264 | 1700:30 | 2034.0806 | 8106.7285 | 2048.7357 | 279:22 | 62.7185 | 62.4499 | 8175.6413 | 1114:52 | 62.2451 | 61.9242
18 | Vijayapur | 147 | 147 | 1119:11 | 3591:22 | 1392.6361 | 4815:48 | 1593.2944 | 6435.1562 | 1639.9271 | 267:45 | 65.0363 | 64.013 | 6584.7965 | 1075:04 | 64.1176 | 63.2832
19 | Indi | 225 | 225 | 944:39 | 4914:35 | 2558.2563 | 5104:33 | 2770.9458 | 10800.1729 | 2810.3063 | 299:46 | 60.2732 | 59.7089 | 11004.9475 | 1173:52 | 60.6551 | 59.9091
20 | B.Bagewadi | 111 | 111 | 347:56 | 4091:27 | 1213.9319 | 4016:30 | 1381.2861 | 5381.3674 | 1395.7833 | 301:47 | 59.858 | 59.4367 | 5551.8444 | 1200:24 | 60.2616 | 59.0028
21 | Bagalkot | 163 | 163 | 751:03 | 4448:50 | 1458.8986 | 8681:59 | 1820.6479 | 6509.6819 | 1851.9417 | 272:41 | 63.969 | 63.3497 | 6695.05 | 985:46 | 67.265 | 66.3328
22 | Jamkhandi | 214 | 214 | 315:20 | 5869:16 | 2348.9854 | 2067:59 | 2435.1514 | 9955.4389 | 2448.2903 | 274:34 | 63.2929 | 63.0948 | 10199.9917 | 1143:55 | 61.8682 | 60.9315
23 | Mudhol | 156 | 156 | 228:31 | 1721:18 | 2169.0312 | 2236:41 | 2262.2264 | 8860.4451 | 2271.7479 | 349:30 | 53.2211 | 53.0242 | 8932.166 | 1374:11 | 53.4445 | 53.0676
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of August-2019
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Aug-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 43 | 43 | 86:50 | 1153:20 | 4154:48 | 812:31 | 4967:19 | 1215.1493 | 5054:09 | 117:32 | 84.4733 | 84.2018 | 1263.2049 | 705:03 | 81.5299 | 80.7994
2 | Dharwad Rural | 64 | 64 | 149:10 | 1551:29 | 11174:32 | 5300:45 | 16475:17 | 3007.2306 | 16624:27 | 259:45 | 65.3997 | 65.0864 | 3071.8757 | 1151:57 | 69.2889 | 68.6287
3 | Gadag | 81 | 81 | 119:25 | 893:30 | 11596:46 | 5111:04 | 16707:50 | 3404.5257 | 16827:15 | 207:45 | 72.2756 | 72.0774 | 3441.7549 | 1019:47 | 72.5286 | 72.2282
4 | Ron | 51 | 51 | 160:21 | 1048:31 | 5742:40 | 1285:32 | 7028:12 | 1552.675 | 7188:33 | 140:57 | 81.4774 | 81.0548 | 1596.3632 | 751:14 | 80.1016 | 79.5417
5 | Haveri | 189 | 189 | 2131:41 | 8612:04 | 1997.6924 | 20887:56 | 2868.0229 | 13164.6729 | 2956.8431 | 375:28 | 51.0493 | 49.5333 | 13523.509 | 1717:16 | 54.4743 | 53.2334
6 | Ranebennur | 169 | 169 | 706:06 | 4263:12 | 2045.9959 | 13118:48 | 2592.6126 | 12158.8793 | 2622.0334 | 372:22 | 50.5132 | 49.9516 | 12336.5126 | 1751:56 | 52.9765 | 52.2895
7 | Sirsi | 51 | 51 | 998:07 | 2348:36 | 1252:18 | 3288:40 | 4540:58 | 16591:50 | 5539:05 | 108:37 | 88.0325 | 85.402 | 18940:26 | 371:23 | 91.1402 | 89.8861
8 | Dandeli | 19 | 19 | 26:18 | 160:50 | 980:15 | 777:28 | 1757:43 | 5422:41 | 1784:01 | 93:54 | 87.5657 | 87.3796 | 5583:31 | 293:52 | 92.2275 | 91.997
9 | Karwar | 33 | 33 | 993:38 | 3371:25 | 1128:39 | 1369:00 | 2497:39 | 7589:20 | 3491:17 | 105:48 | 89.8271 | 85.78 | 10960:45 | 332:09 | 93.7369 | 90.9547
10 | Honnavar | 36 | 36 | 1598:30 | 4734:13 | 1140:39 | 1615:48 | 2756:27 | 8357:56 | 4354:57 | 120:58 | 89.7086 | 83.7405 | 13092:09 | 363:40 | 93.6774 | 90.0961
11 | Belagavi | 132 | 132 | 1285:54 | 2880:02 | 21341:07 | 8408:10 | 1239.5535 | 5188.5583 | 1293.1326 | 235:07 | 69.7079 | 68.3985 | 5308.5597 | 965:12 | 74.309 | 73.7148
12 | Bailhongal | 179 | 179 | 2899:26 | 8645:00 | 1448.3611 | 13882:27 | 2026.7965 | 9613.1069 | 2147.6062 | 287:57 | 63.4746 | 61.2974 | 9973.3153 | 1337:12 | 64.899 | 63.5838
13 | Ramdurg | 69 | 69 | 174:05 | 2488:45 | 23210:25 | 3015:25 | 1092.7431 | 5174.8674 | 1099.9965 | 382:36 | 48.9134 | 48.5743 | 5278.5653 | 1836:01 | 50.9816 | 49.9994
14 | Ghataprabha | 155 | 155 | 637:15 | 2751:52 | 1337.8486 | 3162:55 | 1469.6368 | 8292.4076 | 1496.1889 | 231:40 | 69.4144 | 68.8618 | 8407.0688 | 1301:44 | 65.0331 | 64.5496
15 | Raibag | 154 | 154 | 525:02 | 2417:04 | 1263.9562 | 5690:43 | 1501.0694 | 8989.6292 | 1522.9458 | 237:21 | 68.5574 | 68.0992 | 9090.3403 | 1416:41 | 61.8469 | 61.4195
16 | Athani | 173 | 173 | 2146:13 | 4841:22 | 1318.3972 | 2008:01 | 1402.0646 | 8195.4299 | 1491.4903 | 206:55 | 73.8567 | 72.1893 | 8397.1535 | 1164:55 | 69.0376 | 68.2755
17 | Chikkodi | 176 | 176 | 372:21 | 2026:16 | 1991.6729 | 4145:28 | 2164.4007 | 10271.1292 | 2179.9156 | 297:16 | 60.3299 | 60.0455 | 10355.5568 | 1412:07 | 61.8571 | 61.5435
18 | Vijayapur | 147 | 147 | 285:17 | 3876:39 | 1213.2042 | 3600:46 | 1363.2361 | 7798.3924 | 1375.1229 | 224:31 | 70.0848 | 69.8239 | 7959.9194 | 1299:35 | 65.3266 | 64.6084
19 | Indi | 225 | 225 | 1147:41 | 6062:16 | 2436.1278 | 5454:38 | 2663.4042 | 13463.5771 | 2711.2243 | 289:12 | 61.815 | 61.1294 | 13716.1718 | 1463:03 | 60.8901 | 60.1564
20 | B.Bagewadi | 113 | 113 | 750:30 | 4841:57 | 1143.8368 | 3156:05 | 1275.3403 | 6656.7076 | 1306.6111 | 277:31 | 63.5929 | 62.7002 | 6858.4556 | 1456:40 | 61.4974 | 60.3305
21 | Bagalkot | 167 | 167 | 756:50 | 5205:40 | 1325.9785 | 4680:24 | 1520.9951 | 8030.6771 | 1552.5299 | 223:07 | 70.6201 | 70.011 | 8247.5799 | 1185:17 | 68.57 | 67.7211
22 | Jamkhandi | 214 | 214 | 587:39 | 6456:55 | 2019.5257 | 2185:34 | 2110.591 | 12066.0299 | 2135.0764 | 239:27 | 68.1852 | 67.8162 | 12335.0681 | 1383:22 | 63.1482 | 62.3265
23 | Mudhol | 158 | 158 | 506:48 | 2228:06 | 2067.225 | 2488:46 | 2170.9236 | 11031.3687 | 2192.0403 | 332:58 | 55.6773 | 55.2462 | 11124.2062 | 1689:45 | 54.3668 | 53.9828
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of September-2019
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Sept-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 92:25 | 1245:45 | 4628:00 | 1382:02 | 6010:02 | 1465.5674 | 6102:27 | 138:42 | 81.0289 | 80.7372 | 1517.4736 | 827:43 | 81.7987 | 81.1541
2 | Dharwad Rural | 64 | 64 | 99:10 | 1650:39 | 8738:50 | 2387:55 | 11126:45 | 3470.8451 | 11225:55 | 175:24 | 75.8534 | 75.6382 | 3539.6222 | 1327:22 | 70.3651 | 69.7778
3 | Gadag | 82 | 82 | 207:40 | 1101:10 | 12137:58 | 3105:09 | 15243:07 | 4039.6556 | 15450:47 | 188:25 | 74.1817 | 73.83 | 4085.5375 | 1195:46 | 73.0797 | 72.774
4 | Ron | 51 | 51 | 284:05 | 1332:36 | 5819:20 | 1869:35 | 7688:55 | 1873.0465 | 7973:00 | 156:20 | 79.0607 | 78.287 | 1928.5715 | 907:34 | 79.9309 | 79.336
5 | Haveri | 189 | 189 | 1445:28 | 10057:32 | 2024.1889 | 11531:50 | 2504.6819 | 15669.3549 | 2564.9097 | 325:42 | 55.8257 | 54.7635 | 16088.4188 | 2042:58 | 54.6958 | 53.4842
6 | Ranebennur | 170 | 170 | 292:53 | 4556:05 | 2132.4549 | 5585:20 | 2365.1771 | 14524.0564 | 2377.3806 | 335:38 | 53.624 | 53.3847 | 14713.8932 | 2077:15 | 53.3139 | 52.7037
7 | Sirsi | 51 | 51 | 666:10 | 3014:46 | 827:47 | 1665:51 | 2493:38 | 19085:28 | 3159:48 | 61:57 | 93.2091 | 91.3949 | 22100:14 | 433:20 | 91.4794 | 90.1335
8 | Dandeli | 19 | 19 | 66:34 | 227:24 | 256:32 | 371:55 | 628:27 | 6051:08 | 695:01 | 36:35 | 95.4061 | 94.9195 | 6278:32 | 330:27 | 92.7486 | 92.4761
9 | Karwar | 33 | 33 | 220:27 | 3591:52 | 333:36 | 389:26 | 723:02 | 8312:22 | 943:29 | 28:35 | 96.9569 | 96.0291 | 11904:14 | 360:44 | 94.2648 | 91.7866
10 | Honnavar | 36 | 36 | 484:18 | 5218:31 | 485:12 | 524:07 | 1009:19 | 9367:15 | 1493:37 | 41:29 | 96.106 | 94.2376 | 14585:46 | 405:10 | 94.0756 | 90.775
11 | Belagavi | 132 | 132 | 359:27 | 3239:29 | 16859:20 | 2980:29 | 19839:49 | 6015.2174 | 20199:16 | 153:01 | 79.1248 | 78.7466 | 6150.1958 | 1118:13 | 75.0985 | 74.5397
12 | Bailhongal | 179 | 179 | 1181:16 | 9826:16 | 1406.6083 | 4502:33 | 1594.2146 | 11207.3215 | 1643.434 | 220:21 | 70.3126 | 69.396 | 11616.7493 | 1557:33 | 65.7865 | 64.5366
13 | Ramdurg | 69 | 69 | 184:50 | 2673:35 | 21408:40 | 2036:10 | 23444:50 | 6151.7354 | 23629:40 | 342:28 | 52.8083 | 52.4363 | 6263.1347 | 2178:29 | 51.2811 | 50.3989
14 | Ghataprabha | 155 | 155 | 497:10 | 3249:02 | 1318.7639 | 2124:31 | 1407.2854 | 9699.6931 | 1428.0007 | 221:07 | 69.7358 | 69.2903 | 9835.0694 | 1522:51 | 65.804 | 65.3267
15 | Raibag | 156 | 156 | 491:20 | 2908:24 | 1518.616 | 1592:58 | 1584.9896 | 10574.6188 | 1605.4618 | 247:00 | 66.1327 | 65.6953 | 10695.8021 | 1645:30 | 62.9585 | 62.534
16 | Athani | 175 | 175 | 1043:50 | 5885:12 | 1340.1972 | 3895:15 | 1502.4993 | 9697.9292 | 1545.9924 | 212:01 | 71.381 | 70.5525 | 9943.1458 | 1363:38 | 69.7176 | 68.9519
17 | Chikkodi | 176 | 176 | 441:02 | 2467:18 | 1787.025 | 2511:59 | 1891.691 | 12162.8201 | 1910.0674 | 260:28 | 64.1725 | 63.8245 | 12265.6242 | 1672:35 | 62.2366 | 61.9175
18 | Vijayapur | 146 | 146 | 809:41 | 4686:20 | 1206.0354 | 5694:18 | 1443.2979 | 9241.6903 | 1477.0347 | 242:48 | 67.048 | 66.2777 | 9436.9542 | 1551:17 | 65.4102 | 64.6794
19 | Indi | 225 | 225 | 966:49 | 7029:05 | 2432.7007 | 7236:28 | 2734.2201 | 16197.7972 | 2774.5042 | 295:57 | 59.493 | 58.8962 | 16490.676 | 1759:00 | 60.6611 | 59.9498
20 | B.Bagewadi | 113 | 113 | 689:13 | 5531:10 | 1111.9472 | 4605:44 | 1303.8528 | 7960.5604 | 1332.5701 | 283:01 | 61.5383 | 60.6911 | 8191.0257 | 1739:41 | 61.5041 | 60.3896
21 | Bagalkot | 167 | 167 | 1141:27 | 6347:07 | 17201:54 | 5271:19 | 22473:13 | 8967.0611 | 23614:40 | 141:24 | 81.3097 | 80.3604 | 9231.5243 | 1326:41 | 70.6585 | 69.7931
22 | Jamkhandi | 214 | 214 | 407:30 | 6864:25 | 2085.9826 | 2875:43 | 2205.8042 | 14271.834 | 2222.7833 | 249:17 | 65.6417 | 65.3772 | 14557.8514 | 1632:39 | 63.5569 | 62.8266
23 | Mudhol | 160 | 160 | 52:02 | 2280:08 | 2037.2861 | 3628:10 | 2188.4597 | 13219.8285 | 2190.6278 | 328:36 | 54.4071 | 54.3619 | 13314.834 | 1997:14 | 54.8503 | 54.5258
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of October-2019
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Oct-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 256:40 | 1502:25 | 4575:57 | 3065:00 | 7640:57 | 1783.9403 | 7897:37 | 179:29 | 76.6589 | 75.8748 | 1846.541 | 1007:12 | 81.0542 | 80.3893
2 | Dharwad Rural | 64 | 64 | 128:25 | 1779:04 | 9092:51 | 3945:12 | 13038:03 | 4014.0972 | 13166:28 | 205:44 | 72.6183 | 72.3487 | 4088.225 | 1533:05 | 70.6915 | 70.1502
3 | Gadag | 83 | 83 | 151:40 | 1252:50 | 12590:51 | 5455:40 | 18046:31 | 4791.5937 | 18198:11 | 219:15 | 70.7758 | 70.5302 | 4843.7951 | 1400:37 | 73.0233 | 72.7294
4 | Ron | 51 | 51 | 119:30 | 1452:06 | 5727:10 | 3265:45 | 8992:55 | 2247.7514 | 9112:25 | 178:40 | 76.2995 | 75.9846 | 2308.2556 | 1086:14 | 79.4049 | 78.8505
5 | Haveri | 189 | 189 | 2166:20 | 12223:52 | 2044.0007 | 19190:28 | 2843.6035 | 18512.9583 | 2933.8674 | 372:33 | 51.4661 | 49.9255 | 19022.2861 | 2415:32 | 54.228 | 52.9687
6 | Ranebennur | 171 | 171 | 828:50 | 5384:55 | 2067.2083 | 13913:59 | 2646.9576 | 17171.014 | 2681.4924 | 376:21 | 50.0668 | 49.4153 | 17395.3855 | 2441:27 | 53.077 | 52.4638
7 | Sirsi | 51 | 51 | 178:35 | 3193:21 | 714:06 | 2669:42 | 3383:48 | 22469:16 | 3562:23 | 69:51 | 91.0821 | 90.6115 | 1069.2757 | 503:11 | 91.4218 | 90.2027
8 | Dandeli | 19 | 19 | 33:03 | 260:27 | 247:13 | 563:01 | 810:14 | 6861:22 | 843:17 | 44:23 | 94.2683 | 94.0345 | 7121:49 | 374:50 | 92.9688 | 92.7019
9 | Karwar | 33 | 33 | 1137:34 | 4729:26 | 620:18 | 1257:15 | 1877:33 | 10189:55 | 3015:07 | 91:22 | 92.3528 | 87.7195 | 14919:21 | 452:06 | 93.9878 | 91.1974
10 | Honnavar | 36 | 36 | 924:23 | 6142:54 | 680:58 | 1265:34 | 1946:32 | 11313:47 | 2870:55 | 79:45 | 92.7325 | 89.2812 | 17456:41 | 484:54 | 93.881 | 90.5586
11 | Belagavi | 132 | 132 | 494:04 | 3733:33 | 3284:35 | 4748:11 | 8032:46 | 6349.916 | 8526:50 | 64:36 | 91.8207 | 91.3176 | 6505.4806 | 1182:49 | 77.5208 | 76.9701
12 | Bailhongal | 183 | 183 | 921:27 | 10747:43 | 1431.4757 | 9041:42 | 1808.2132 | 13015.5347 | 1846.6069 | 242:11 | 68.126 | 67.4492 | 13463.3562 | 1765:41 | 66.7649 | 65.6214
13 | Ramdurg | 69 | 69 | 122:25 | 2796:00 | 19992:00 | 6068:40 | 1085.8611 | 7237.5965 | 1090.9618 | 379:28 | 49.2351 | 48.9966 | 7354.0965 | 2557:57 | 50.9847 | 50.1957
14 | Ghataprabha | 156 | 156 | 582:00 | 3831:02 | 1148.6194 | 5752:40 | 1388.3139 | 11088.0069 | 1412.5639 | 217:19 | 71.2921 | 70.7907 | 11247.6333 | 1730:24 | 66.7865 | 66.3083
15 | Raibag | 156 | 156 | 286:15 | 3194:39 | 1319.4319 | 5122:30 | 1532.8694 | 12107.4882 | 1544.7965 | 237:40 | 68.3029 | 68.0563 | 12240.5986 | 1883:10 | 63.7327 | 63.3339
16 | Athani | 175 | 175 | 930:58 | 6816:10 | 1325.9139 | 2770:46 | 1441.3625 | 11139.2917 | 1480.1528 | 203:00 | 73.4311 | 72.7161 | 11423.2986 | 1566:37 | 70.2556 | 69.4972
17 | Chikkodi | 176 | 176 | 261:57 | 2729:15 | 1720.7188 | 3263:07 | 1856.6819 | 14019.5021 | 1867.5965 | 254:40 | 65.9699 | 65.7699 | 14133.2207 | 1927:15 | 62.7774 | 62.4755
18 | Vijayapur | 147 | 147 | 994:38 | 5680:58 | 22308:31 | 8855:15 | 1298.4903 | 10540.1806 | 1339.9333 | 218:46 | 71.5056 | 70.5962 | 10776.8875 | 1759:30 | 66.4944 | 65.742
19 | Indi | 231 | 231 | 897:23 | 7926:28 | 2402.3826 | 11311:23 | 2873.6903 | 19071.4875 | 2911.0813 | 302:27 | 59.8703 | 59.3481 | 19401.7572 | 2015:46 | 61.4203 | 60.7522
20 | B.Bagewadi | 115 | 115 | 436:30 | 5967:40 | 13294:58 | 7866:34 | 21161:32 | 8842.291 | 21598:02 | 187:49 | 75.267 | 74.7569 | 9090.9438 | 1897:14 | 64.0703 | 63.06
21 | Bagalkot | 167 | 167 | 463:18 | 6810:25 | 1265.0625 | 8576:48 | 1622.4292 | 10589.4903 | 1641.7333 | 235:56 | 68.6608 | 68.2879 | 10873.2576 | 1562:37 | 70.3691 | 69.5751
22 | Jamkhandi | 214 | 214 | 736:24 | 7600:49 | 2070.5708 | 3900:18 | 2233.0833 | 16504.9174 | 2263.7667 | 253:53 | 66.3388 | 65.8763 | 16821.6181 | 1886:32 | 63.9599 | 63.2684
23 | Mudhol | 160 | 160 | 411:36 | 2691:44 | 2062.0819 | 3460:20 | 2206.2625 | 15426.091 | 2223.4125 | 333:31 | 55.5189 | 55.1731 | 15538.2465 | 2330:44 | 54.9472 | 54.6196
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of November-2019
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of November-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 49:20 | 1551:45 | 4685:49 | 784:41 | 5470:30 | 2011.8778 | 5519:50 | 125:27 | 82.732 | 82.5763 | 2076.534 | 1132:39 | 81.2605 | 80.6582
2 | Dharwad Rural | 64 | 64 | 59:55 | 1838:59 | 9470:33 | 1425:44 | 10896:17 | 4468.109 | 10956:12 | 171:11 | 76.3536 | 76.2235 | 4544.7333 | 1704:16 | 71.3876 | 70.8969
3 | Gadag | 83 | 83 | 152:30 | 1405:20 | 13932:53 | 2201:31 | 16134:24 | 5463.8604 | 16286:54 | 196:14 | 73.0013 | 72.7462 | 5522.416 | 1596:51 | 73.0206 | 72.7315
4 | Ron | 51 | 51 | 165:30 | 1617:36 | 6064:05 | 648:30 | 6712:35 | 2527.4424 | 6878:05 | 134:52 | 81.7195 | 81.2688 | 2594.8424 | 1221:06 | 79.6895 | 79.1478
5 | Haveri | 189 | 189 | 989:30 | 13213:22 | 2302.9368 | 5030:16 | 2512.5313 | 21025.4896 | 2553.7604 | 324:17 | 55.6873 | 54.9601 | 21576.0465 | 2739:49 | 54.4074 | 53.2135
6 | Ranebennur | 171 | 171 | 272:26 | 5657:21 | 2161.4687 | 4218:11 | 2337.2264 | 19508.2404 | 2348.5778 | 329:37 | 54.44 | 54.2188 | 19743.9633 | 2771:05 | 53.2446 | 52.6796
7 | Sirsi | 51 | 51 | 194:38 | 3387:59 | 624:44 | 1576:45 | 2201:29 | 1027.9479 | 2396:07 | 46:59 | 94.0047 | 93.4746 | 1169.1139 | 550:10 | 91.7394 | 90.605
8 | Dandeli | 19 | 19 | 74:00 | 334:27 | 314:57 | 231:54 | 546:51 | 7408:13 | 620:51 | 32:41 | 96.0026 | 95.4616 | 7742:40 | 407:31 | 93.3418 | 93.0412
9 | Karwar | 33 | 33 | 280:10 | 5009:36 | 432:10 | 188:56 | 621:06 | 10811:01 | 901:16 | 27:19 | 97.3859 | 96.2068 | 15820:37 | 479:25 | 94.4056 | 91.8133
10 | Honnavar | 37 | 37 | 439:05 | 6581:59 | 481:22 | 293:22 | 774:44 | 12088:31 | 1213:49 | 32:48 | 97.0918 | 95.4436 | 18670:30 | 504:36 | 94.4208 | 91.3831
11 | Belagavi | 132 | 132 | 159:49 | 3893:22 | 2989:12 | 1528:10 | 4517:22 | 6538.1396 | 4677:11 | 35:26 | 95.2469 | 95.0787 | 6700.3632 | 1218:15 | 79.7003 | 79.1966
12 | Bailhongal | 184 | 184 | 550:40 | 11298:23 | 1542.3604 | 2767:51 | 1657.6875 | 14673.2222 | 1680.6319 | 219:13 | 69.9694 | 69.5538 | 15143.9882 | 1975:18 | 67.3173 | 66.2687
13 | Ramdurg | 69 | 69 | 82:15 | 2878:15 | 22570:30 | 1366:44 | 23937:14 | 8234.9813 | 1000.8118 | 348:07 | 51.8172 | 51.6516 | 8354.9083 | 2906:03 | 51.0871 | 50.3747
14 | Ghataprabha | 156 | 156 | 251:45 | 4082:47 | 1348.8174 | 1113:33 | 1395.2153 | 12483.2222 | 1405.7049 | 216:16 | 70.1877 | 69.9636 | 12653.3382 | 1946:40 | 67.2046 | 66.7577
15 | Raibag | 162 | 162 | 265:27 | 3460:06 | 1446.7201 | 835:00 | 1481.5118 | 13589 | 1492.5722 | 221:07 | 69.5162 | 69.2886 | 13733.1708 | 2034:33 | 65.6218 | 65.2571
16 | Athani | 175 | 175 | 414:09 | 7230:19 | 1158.6292 | 916:10 | 1196.8028 | 12336.0944 | 1214.059 | 166:30 | 77.2038 | 76.8751 | 12637.3576 | 1733:07 | 71.1098 | 70.4043
17 | Chikkodi | 176 | 176 | 142:48 | 2872:03 | 1870.1208 | 862:59 | 1906.0785 | 15925.5806 | 1912.0285 | 260:44 | 63.9 | 63.7873 | 16045.2492 | 2187:59 | 62.9155 | 62.6368
18 | Vijayapur | 147 | 147 | 435:47 | 6116:45 | 1181.2132 | 8427:24 | 1532.3549 | 12072.5354 | 1550.5125 | 253:09 | 65.2527 | 64.841 | 12327.4 | 2012:38 | 66.3418 | 65.6312
19 | Indi | 231 | 231 | 1131:34 | 9058:02 | 2500.8729 | 3380:41 | 2641.7347 | 21713.2222 | 2688.8833 | 279:22 | 61.8797 | 61.1994 | 22090.6406 | 2295:08 | 61.4768 | 60.8072
20 | B.Bagewadi | 120 | 120 | 530:38 | 6498:18 | 1119.6604 | 2704:25 | 1232.3444 | 10074.6354 | 1254.4542 | 250:53 | 65.7682 | 65.1541 | 10345.3979 | 2069:05 | 65.5921 | 64.6674
21 | Bagalkot | 168 | 168 | 841:47 | 7652:12 | 1436.1125 | 3236:57 | 1570.9854 | 12160.4757 | 1606.0597 | 229:26 | 68.8297 | 68.1337 | 12479.3174 | 1782:46 | 70.3345 | 69.5567
22 | Jamkhandi | 214 | 214 | 303:00 | 7903:49 | 2119.8007 | 1005:02 | 2161.6771 | 18666.5944 | 2174.3021 | 243:51 | 66.329 | 66.1324 | 18995.9201 | 2130:23 | 64.2512 | 63.6205
23 | Mudhol | 160 | 160 | 89:50 | 2781:34 | 1812.5924 | 1093:48 | 1858.1674 | 17284.2583 | 1861.9104 | 279:17 | 61.2882 | 61.2102 | 17400.1569 | 2610:01 | 55.7268 | 55.4299
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of December-2019
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of December-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 68:40 | 1620:25 | 5338:49 | 509:51 | 5848:40 | 2255.5722 | 5917:20 | 134:29 | 82.1338 | 81.9241 | 2323.0896 | 1267:08 | 81.3589 | 80.8009
2 | Dharwad Rural | 64 | 64 | 155:05 | 1994:04 | 9977:56 | 1039:09 | 11017:05 | 4927.1542 | 11172:10 | 174:34 | 76.8626 | 76.5369 | 5010.2403 | 1878:50 | 72.0048 | 71.5327
3 | Gadag | 83 | 83 | 45:40 | 1451:00 | 13819:44 | 1838:12 | 15657:56 | 6116.2743 | 15703:36 | 189:12 | 74.6438 | 74.5699 | 6176.7326 | 1786:03 | 73.2036 | 72.9387
4 | Ron | 51 | 51 | 41:00 | 1658:36 | 6333:15 | 511:55 | 6845:10 | 2812.6576 | 6886:10 | 135:01 | 81.9598 | 81.8518 | 2881.766 | 1356:08 | 79.9454 | 79.4526
5 | Haveri | 191 | 191 | 808:40 | 14022:02 | 2480.0097 | 2689:20 | 2592.0653 | 23617.5549 | 2625.7597 | 329:56 | 56.2225 | 55.6534 | 24201.8063 | 3041:04 | 55.0356 | 53.9233
6 | Ranebennur | 172 | 172 | 344:25 | 6001:46 | 2394.9882 | 2020:52 | 2479.191 | 21987.4314 | 2493.5417 | 347:56 | 53.5035 | 53.2344 | 22237.505 | 3102:54 | 53.5149 | 52.9862
7 | Sirsi | 51 | 51 | 174:47 | 3562:46 | 434:35 | 507:28 | 942:03 | 1067.2 | 1116:50 | 21:54 | 97.5173 | 97.0566 | 1215.6486 | 572:04 | 92.3907 | 91.3323
8 | Dandeli | 19 | 19 | 18:29 | 352:56 | 277:25 | 216:17 | 493:42 | 7901:55 | 512:11 | 26:57 | 96.5075 | 96.3767 | 8254:51 | 434:28 | 93.6986 | 93.4172
9 | Karwar | 33 | 33 | 393:58 | 5403:34 | 432:10 | 242:40 | 674:50 | 11485:51 | 1068:48 | 32:23 | 97.2514 | 95.6468 | 16889:25 | 511:48 | 94.7264 | 92.2454
10 | Honnavar | 37 | 37 | 159:11 | 6741:10 | 289:53 | 181:50 | 471:43 | 12560:14 | 630:54 | 17:03 | 98.2864 | 97.7082 | 19301:24 | 521:40 | 94.8566 | 92.0961
11 | Belagavi | 132 | 132 | 591:53 | 4485:15 | 2243:40 | 1092:07 | 3335:47 | 6677.1306 | 3927:40 | 29:45 | 96.6033 | 96.0007 | 6864.016 | 1248:00 | 81.6057 | 81.0909
12 | Bailhongal | 186 | 186 | 886:29 | 12184:52 | 1563.1847 | 1848:46 | 1640.2167 | 16313.4389 | 1677.1535 | 216:24 | 71.5536 | 70.9131 | 16821.1417 | 2170:28 | 68.1067 | 67.1141
13 | Ramdurg | 69 | 69 | 241:50 | 3120:05 | 22722:00 | 1423:00 | 1006.0417 | 9241.0229 | 1016.1181 | 353:26 | 52.9667 | 52.4956 | 9371.0264 | 3259:29 | 51.299 | 50.6138
14 | Ghataprabha | 156 | 156 | 252:10 | 4334:57 | 1441.7222 | 1129:39 | 1488.791 | 13972.0132 | 1499.2979 | 230:40 | 69.2144 | 68.9971 | 14152.6361 | 2177:20 | 67.4312 | 67.0102
15 | Raibag | 163 | 163 | 68:40 | 3528:46 | 1581.2889 | 609:15 | 1606.6743 | 15195.6743 | 1609.5354 | 236:59 | 68.2036 | 68.1469 | 15342.7063 | 2259:03 | 66.1 | 65.772
16 | Athani | 176 | 176 | 749:28 | 7979:47 | 1233.1806 | 732:39 | 1263.7076 | 13599.8021 | 1294.9354 | 176:35 | 76.8382 | 76.2658 | 13932.2931 | 1899:51 | 71.9012 | 71.2143
17 | Chikkodi | 176 | 176 | 65:10 | 2937:13 | 1864.025 | 617:33 | 1889.7563 | 17815.3368 | 1892.4715 | 258:04 | 65.3637 | 65.3139 | 17937.7207 | 2446:03 | 63.1915 | 62.9386
18 | Vijayapur | 148 | 148 | 1311:49 | 7428:34 | 1274.3507 | 1987:32 | 1357.1646 | 13429.7 | 1411.8236 | 228:57 | 70.4193 | 69.2279 | 13739.2236 | 2227:59 | 67.0032 | 66.2427
19 | Indi | 231 | 231 | 301:35 | 9359:37 | 2592.1486 | 1648:12 | 2660.8236 | 24374.0458 | 2673.3896 | 277:45 | 62.8428 | 62.6674 | 24764.0302 | 2572:53 | 61.6308 | 61.0169
20 | B.Bagewadi | 120 | 120 | 222:40 | 6720:58 | 1285.3194 | 951:49 | 1324.9785 | 11399.6139 | 1334.2562 | 266:51 | 64.3823 | 64.1329 | 11679.6542 | 2335:56 | 65.4557 | 64.6071
21 | Bagalkot | 168 | 168 | 210:12 | 7862:24 | 1590.2847 | 1798:13 | 1665.2104 | 13825.6861 | 1673.9688 | 239:08 | 68.0259 | 67.8577 | 14153.2861 | 2021:54 | 70.0743 | 69.3652
22 | Jamkhandi | 214 | 214 | 167:29 | 8071:18 | 1977.4236 | 1008:26 | 2019.4417 | 20686.0361 | 2026.4201 | 227:16 | 69.5592 | 69.454 | 21022.3403 | 2357:39 | 64.8496 | 64.2781
23 | Mudhol | 160 | 160 | 151:37 | 2933:11 | 1654.6264 | 1146:01 | 1702.3771 | 18986.6354 | 1708.6944 | 256:18 | 65.6779 | 65.5505 | 19108.8514 | 2866:20 | 56.8486 | 56.5708
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of January-2020
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of January-2020 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 120:30 | 1740:55 | 5326:45 | 445:26 | 5772:11 | 2496.0799 | 5892:41 | 133:55 | 82.3675 | 81.9994 | 2568.6181 | 1401:04 | 81.4611 | 80.9223
2 | Dharwad Rural | 64 | 64 | 25:25 | 2019:29 | 10443:48 | 803:23 | 11247:11 | 5395.7868 | 11272:36 | 176:08 | 76.3794 | 76.326 | 5479.9319 | 2054:58 | 72.448 | 72.0183
3 | Gadag | 85 | 85 | 97:00 | 1548:00 | 11033:32 | 772:56 | 11806:28 | 6608.2104 | 11903:28 | 140:02 | 81.3307 | 81.1773 | 6672.7104 | 1884:04 | 74.5936 | 74.3456
4 | Ron | 51 | 51 | 54:45 | 1713:21 | 6401:40 | 269:20 | 6671:00 | 3090.616 | 6725:45 | 131:53 | 82.4188 | 82.2745 | 3162.0056 | 1488:00 | 80.196 | 79.7385
5 | Haveri | 192 | 192 | 1494:25 | 15516:27 | 2539.8285 | 2071:10 | 2626.1271 | 26243.6819 | 2688.3944 | 336:03 | 55.8782 | 54.8321 | 26890.2007 | 3361:17 | 55.3314 | 54.231
6 | Ranebennur | 176 | 176 | 1224:52 | 7226:38 | 2407.6146 | 2018:36 | 2491.7229 | 24479.1543 | 2542.759 | 346:44 | 54.3306 | 53.3952 | 24780.264 | 3379:08 | 54.547 | 53.9879
7 | Sirsi | 51 | 51 | 295:55 | 3858:41 | 500:58 | 679:56 | 1180:54 | 1116.4042 | 1476:49 | 28:57 | 96.8878 | 96.1079 | 1277.1826 | 601:02 | 92.8463 | 91.8161
8 | Dandeli | 19 | 19 | 42:20 | 395:16 | 261:20 | 233:52 | 495:12 | 8397:07 | 537:32 | 28:17 | 96.4969 | 96.1974 | 8792:23 | 462:45 | 93.9821 | 93.6988
9 | Karwar | 33 | 33 | 133:32 | 5537:06 | 391:30 | 134:29 | 525:59 | 12011:50 | 659:31 | 19:59 | 97.8577 | 97.3138 | 17548:56 | 531:47 | 95.0436 | 92.7589
10 | Honnavar | 37 | 37 | 226:48 | 6967:58 | 330:05 | 376:29 | 706:34 | 13266:48 | 933:22 | 25:14 | 97.4333 | 96.6094 | 20234:46 | 546:53 | 95.1176 | 92.5533
11 | Belagavi | 132 | 132 | 254:53 | 4740:08 | 18447:42 | 1060:24 | 19508:06 | 7489.9681 | 19762:59 | 149:43 | 80.1359 | 79.8764 | 7687.4736 | 1397:43 | 81.4568 | 80.9678
12 | Bailhongal | 187 | 187 | 465:06 | 12649:58 | 1628.3986 | 1332:03 | 1683.9007 | 17997.3396 | 1703.2799 | 218:36 | 70.9522 | 70.6179 | 18524.4215 | 2377:28 | 68.5482 | 67.6271
13 | Ramdurg | 69 | 69 | 56:00 | 3176:05 | 22625:15 | 784:45 | 23410:00 | 10216.4396 | 23466:00 | 340:05 | 54.3985 | 54.2894 | 10348.7764 | 3599:34 | 51.613 | 50.9862
14 | Ghataprabha | 156 | 156 | 200:57 | 4535:54 | 1537.9833 | 596:52 | 1562.8528 | 15534.866 | 1571.2257 | 241:44 | 67.6829 | 67.5098 | 15723.8618 | 2419:03 | 67.4567 | 67.0608
15 | Raibag | 164 | 164 | 289:25 | 3818:11 | 1565.3146 | 383:35 | 1581.2972 | 16776.9715 | 1593.3563 | 233:10 | 68.8966 | 68.6594 | 16936.0625 | 2478:27 | 66.5691 | 66.2521
16 | Athani | 179 | 179 | 428:10 | 8407:57 | 1397.8424 | 1256:00 | 1450.1757 | 15049.9778 | 1468.016 | 196:50 | 73.866 | 73.5445 | 15400.309 | 2064:51 | 72.5235 | 71.8839
17 | Chikkodi | 176 | 176 | 221:55 | 3159:08 | 1490.266 | 484:52 | 1510.4688 | 19325.8056 | 1519.7153 | 207:14 | 72.3155 | 72.146 | 19457.436 | 2653:17 | 64.1158 | 63.8714
18 | Vijayapur | 149 | 149 | 223:33 | 7652:07 | 1393.9 | 876:00 | 1430.4 | 14860.1 | 1439.7146 | 231:54 | 69.0323 | 68.8306 | 15178.9382 | 2444:56 | 67.4078 | 66.7085
19 | Indi | 231 | 231 | 431:01 | 9790:38 | 2765.6535 | 1536:21 | 2829.6681 | 27203.7139 | 2847.6271 | 295:51 | 60.485 | 60.2342 | 27611.6572 | 2868:45 | 61.5147 | 60.9376
20 | B.Bagewadi | 120 | 120 | 413:35 | 7134:33 | 1313.9965 | 833:47 | 1348.7375 | 12748.3514 | 1365.9701 | 273:12 | 63.7436 | 63.2804 | 13045.6243 | 2609:07 | 65.2823 | 64.4727
21 | Bagalkot | 169 | 169 | 424:01 | 8286:25 | 1635.0854 | 1181:15 | 1684.3042 | 15509.9903 | 1701.9715 | 241:42 | 67.8507 | 67.5134 | 15855.2576 | 2251:38 | 70.0081 | 69.3405
22 | Jamkhandi | 214 | 214 | 441:04 | 8512:22 | 2092.8556 | 703:16 | 2122.1583 | 22808.1944 | 2140.5361 | 240:04 | 68.0109 | 67.7339 | 23162.8764 | 2597:42 | 65.1698 | 64.6282
23 | Mudhol | 160 | 160 | 216:12 | 3149:23 | 1579.2299 | 425:37 | 1596.9639 | 20583.5993 | 1605.9722 | 240:54 | 67.8031 | 67.6215 | 20714.8236 | 3107:13 | 57.9583 | 57.6903
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of February-2020
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of February-2020 |  |  |  | Reliability for cumulative period from Apr-19 to Feb-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 48:45 | 1789:40 | 5060:18 | 396:26 | 5456:44 | 2723.4438 | 5505:29 | 125:07 | 82.1815 | 82.0223 | 2798.0132 | 1526:11 | 81.5234 | 81.0175
2 | Dharwad Rural | 64 | 64 | 220:22 | 2239:51 | 10440:36 | 682:24 | 11123:00 | 5859.2451 | 11343:22 | 177:14 | 75.0292 | 74.5345 | 5952.5722 | 2232:13 | 72.6714 | 72.2361
3 | Gadag | 85 | 85 | 70:40 | 1618:40 | 13686:57 | 827:27 | 14514:24 | 7212.9771 | 14585:04 | 171:35 | 75.4659 | 75.3464 | 7280.4215 | 2055:39 | 74.6691 | 74.4322
4 | Ron | 52 | 52 | 259:30 | 1972:51 | 5887:55 | 359:15 | 6247:10 | 3350.9146 | 6506:40 | 125:08 | 82.7388 | 82.0218 | 3433.1167 | 1584:31 | 80.764 | 80.2921
5 | Haveri | 192 | 192 | 1622:30 | 17138:57 | 2369.9542 | 1978:10 | 2452.3778 | 28696.0597 | 2519.9819 | 315:00 | 55.9559 | 54.7417 | 29410.1826 | 3676:16 | 55.3855 | 54.2752
6 | Ranebennur | 176 | 176 | 699:27 | 7926:05 | 2241.1785 | 1534:19 | 2305.1083 | 26784.2626 | 2334.2521 | 318:18 | 54.8372 | 54.2662 | 27114.5161 | 3697:26 | 54.5721 | 54.012
7 | Sirsi | 51 | 51 | 394:04 | 4252:45 | 724:49 | 677:22 | 1402:11 | 1174.8285 | 1796:15 | 35:13 | 96.0497 | 94.9396 | 1352.0264 | 636:15 | 93.1236 | 92.0865
8 | Dandeli | 19 | 19 | 0:08 | 395:24 | 324:32 | 320:24 | 644:56 | 9042:03 | 645:04 | 33:57 | 95.123 | 95.122 | 9437:27 | 496:42 | 94.0809 | 93.822
9 | Karwar | 33 | 33 | 450:19 | 5987:25 | 329:09 | 175:30 | 504:39 | 12516:29 | 954:58 | 28:56 | 97.8028 | 95.8422 | 18503:54 | 560:43 | 95.2825 | 93.0258
10 | Honnavar | 37 | 37 | 277:14 | 7245:12 | 387:19 | 147:09 | 534:28 | 13801:16 | 811:42 | 21:56 | 97.9246 | 96.848 | 21046:28 | 568:49 | 95.3606 | 92.9251
11 | Belagavi | 132 | 132 | 278:27 | 5018:35 | 19345:53 | 1170:27 | 20516:20 | 8344.8153 | 20794:47 | 157:32 | 77.6686 | 77.3655 | 8553.9229 | 1555:16 | 81.1289 | 80.656
12 | Bailhongal | 188 | 188 | 1161:53 | 13811:51 | 1582.8785 | 1400:50 | 1641.2465 | 19638.5861 | 1689.6583 | 215:42 | 69.8964 | 69.0085 | 20214.0799 | 2580:31 | 68.8177 | 67.904
13 | Ramdurg | 69 | 69 | 288:00 | 3464:05 | 20880:15 | 500:45 | 21381:00 | 11107.3146 | 21669:00 | 314:03 | 55.4785 | 54.8788 | 11251.6514 | 3913:37 | 51.9476 | 51.3232
14 | Ghataprabha | 157 | 157 | 128:15 | 4664:09 | 1475.2208 | 727:35 | 1505.5368 | 17040.4028 | 1510.8806 | 230:58 | 66.9331 | 66.8157 | 17234.7424 | 2634:37 | 67.6007 | 67.2312
15 | Raibag | 164 | 164 | 659:33 | 4477:44 | 1490.2889 | 425:53 | 1508.034 | 18285.0056 | 1535.5153 | 224:43 | 68.292 | 67.7141 | 18471.5778 | 2703:09 | 66.7182 | 66.3786
16 | Athani | 180 | 180 | 537:55 | 8945:52 | 1347.3354 | 455:24 | 1366.3104 | 16416.2882 | 1388.7236 | 185:10 | 73.8255 | 73.3961 | 16789.0326 | 2238:32 | 72.7756 | 72.1575
17 | Chikkodi | 179 | 179 | 227:52 | 3387:00 | 1771.3236 | 665:40 | 1799.0597 | 21124.8653 | 1808.5542 | 242:29 | 65.3427 | 65.1598 | 21265.9902 | 2851:18 | 64.7713 | 64.536
18 | Vijayapur | 149 | 149 | 181:06 | 7833:13 | 1332.0917 | 714:52 | 1361.8778 | 16221.9778 | 1369.4236 | 220:35 | 68.4823 | 68.3077 | 16548.3618 | 2665:30 | 67.5008 | 66.8469
19 | Indi | 231 | 231 | 469:45 | 10260:23 | 2508.2826 | 880:33 | 2544.9722 | 29748.6861 | 2564.5451 | 266:27 | 62.0097 | 61.7175 | 30176.2024 | 3135:11 | 61.5576 | 61.0051
20 | B.Bagewadi | 121 | 121 | 339:41 | 7474:14 | 1257.909 | 596:25 | 1282.7597 | 14031.1111 | 1296.9132 | 257:14 | 63.4437 | 63.0404 | 14342.5375 | 2844:48 | 65.3852 | 64.6169
21 | Bagalkot | 172 | 172 | 461:41 | 8748:06 | 1535.3611 | 1009:54 | 1577.4403 | 17087.4306 | 1596.6771 | 222:48 | 68.3753 | 67.9896 | 17451.9347 | 2435:09 | 70.3446 | 69.712
22 | Jamkhandi | 217 | 217 | 287:11 | 8799:33 | 2116.0146 | 570:42 | 2139.7938 | 24947.9882 | 2151.7597 | 237:59 | 65.9972 | 65.8071 | 25314.6361 | 2799:47 | 65.6813 | 65.1769
23 | Mudhol | 160 | 160 | 168:54 | 3318:17 | 1507.8153 | 574:48 | 1531.7653 | 22115.3646 | 1538.8028 | 230:49 | 66.9878 | 66.8361 | 22253.6264 | 3338:03 | 58.74 | 58.482
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of March-2020
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of March-2020 |  |  |  | Reliability for cumulative period from Apr-19 to Mar-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 54:15 | 1843:55 | 5156:08 | 564:47 | 5720:55 | 2961.8153 | 5775:10 | 131:15 | 82.5241 | 82.3584 | 3038.6451 | 1657:27 | 81.6082 | 81.1311
2 | Dharwad Rural | 64 | 64 | 126:42 | 2366:33 | 11760:29 | 1135:22 | 12895:51 | 6396.5722 | 13022:33 | 203:29 | 72.917 | 72.6509 | 6495.1785 | 2435:42 | 72.6922 | 72.2713
3 | Gadag | 85 | 85 | 266:05 | 1884:45 | 15086:44 | 922:04 | 16008:48 | 7880.0104 | 16274:53 | 191:28 | 74.6856 | 74.2649 | 7958.5417 | 2247:07 | 74.6705 | 74.4181
4 | Ron | 53 | 53 | 217:10 | 2190:01 | 4075:50 | 617:55 | 4693:45 | 3546.4875 | 4910:55 | 92:40 | 88.0966 | 87.5459 | 3637.7382 | 1647:17 | 81.7173 | 81.2468
5 | Haveri | 192 | 192 | 894:52 | 18033:49 | 2468.416 | 1534:45 | 2532.3639 | 31228.4236 | 2569.65 | 321:12 | 57.4536 | 56.8271 | 31979.8326 | 3997:29 | 55.5606 | 54.4914
6 | Ranebennur | 177 | 177 | 816:45 | 8742:50 | 2421.6583 | 1741:37 | 2494.2257 | 29278.4883 | 2528.2569 | 342:49 | 54.543 | 53.9228 | 29642.773 | 4019:22 | 54.8046 | 54.2423
7 | Sirsi | 51 | 51 | 150:14 | 4402:59 | 671:33 | 862:22 | 1533:55 | 1238.7417 | 1684:09 | 33:01 | 95.9574 | 95.5615 | 1422.1993 | 669:16 | 93.3636 | 92.3808
8 | Dandeli | 19 | 19 | 44:34 | 439:58 | 398:54 | 425:54 | 824:48 | 9866:51 | 869:22 | 45:45 | 94.1653 | 93.85 | 10306:49 | 542:28 | 94.088 | 93.8244
9 | Karwar | 33 | 33 | 166:41 | 6154:06 | 395:42 | 307:26 | 703:08 | 13219:37 | 869:49 | 26:21 | 97.1361 | 96.4572 | 19373:43 | 587:05 | 95.4395 | 93.3165
10 | Honnavar | 37 | 37 | 116:01 | 7361:13 | 363:16 | 219:32 | 582:48 | 14384:04 | 698:49 | 18:53 | 97.8829 | 97.4614 | 21745:17 | 587:43 | 95.5742 | 93.3093
11 | Belagavi | 131 | 131 | 302:20 | 5320:55 | 20608:43 | 1588:06 | 22196:49 | 9269.6826 | 22499:09 | 171:45 | 77.2256 | 76.9154 | 9491.3875 | 1738:53 | 80.6664 | 80.204
12 | Bailhongal | 189 | 189 | 644:55 | 14456:46 | 1710.3375 | 2599:00 | 1818.6292 | 21457.2153 | 1845.5007 | 234:21 | 68.9601 | 68.5014 | 22059.5806 | 2801:13 | 68.9808 | 68.11
13 | Ramdurg | 69 | 69 | 266:10 | 3730:15 | 21761:10 | 961:15 | 22722:25 | 12054.0819 | 22988:35 | 333:10 | 55.7379 | 55.2194 | 12209.509 | 4246:47 | 52.2686 | 51.6532
14 | Ghataprabha | 157 | 157 | 126:41 | 4790:50 | 1572.7062 | 1001:12 | 1614.4229 | 18654.8257 | 1619.7014 | 247:36 | 66.8292 | 66.7207 | 18854.4437 | 2882:12 | 67.5354 | 67.188
15 | Raibag | 164 | 164 | 473:39 | 4951:23 | 1670.084 | 762:12 | 1701.8424 | 19986.8479 | 1721.5778 | 251:56 | 66.5255 | 66.1373 | 20193.1556 | 2955:06 | 66.7019 | 66.3582
16 | Athani | 180 | 180 | 1066:44 | 10012:36 | 1508.6861 | 760:35 | 1540.3771 | 17956.6653 | 1584.8243 | 211:19 | 72.3947 | 71.5981 | 18373.8569 | 2449:51 | 72.7434 | 72.1101
17 | Chikkodi | 179 | 179 | 249:31 | 3636:31 | 1976.7278 | 845:15 | 2011.9465 | 23136.8118 | 2022.3431 | 271:09 | 63.7422 | 63.5548 | 23288.3332 | 3122:27 | 64.6842 | 64.4529
18 | Vijayapur | 149 | 149 | 205:13 | 8038:26 | 1396.7528 | 1439:02 | 1456.7125 | 17678.6903 | 1465.2632 | 236:01 | 68.4626 | 68.2775 | 18013.625 | 2901:31 | 67.5823 | 66.9681
19 | Indi | 231 | 231 | 999:04 | 11259:27 | 2804.8375 | 2321:57 | 2901.5854 | 32650.2715 | 2943.2132 | 305:47 | 59.4807 | 58.8994 | 33119.4156 | 3440:59 | 61.3816 | 60.8268
20 | B.Bagewadi | 123 | 123 | 496:56 | 7971:10 | 1348.2118 | 1127:15 | 1395.1806 | 15426.2917 | 1415.8861 | 276:16 | 63.4099 | 62.8669 | 15758.4236 | 3074:49 | 65.7331 | 64.9953
21 | Bagalkot | 181 | 181 | 346:05 | 9094:11 | 1712.9368 | 1973:12 | 1795.1535 | 18882.584 | 1809.5736 | 239:57 | 68.0065 | 67.7495 | 19261.5083 | 2554:01 | 71.4963 | 70.9243
22 | Jamkhandi | 219 | 219 | 495:54 | 9295:27 | 2377.2861 | 806:05 | 2410.8729 | 27358.8611 | 2431.5354 | 266:28 | 64.4885 | 64.1842 | 27746.1715 | 3040:41 | 65.8671 | 65.3839
23 | Mudhol | 161 | 161 | 851:21 | 4169:38 | 2031.2222 | 837:14 | 2066.1069 | 24181.4715 | 2101.5799 | 313:17 | 58.6033 | 57.8926 | 24355.2062 | 3630:35 | 58.963 | 58.6681
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]

## RURAL(Excl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2019 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of April-2019 |  |  |  | Reliability for cumulative period from Apr-19
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 37 | 37 | 285:20 | 285:20 | 1286:35 | 1149:50 | 2436:25 | 2436:25 | 2721:45 | 73:34 | 90.8543 | 89.7832 | 2721:45 | 73:34 | 90.8543 | 89.7832
2 | Dharwad Rural | 64 | 64 | 605:49 | 605:49 | 1590:28 | 3169:22 | 4759:50 | 4759:50 | 5365:39 | 83:50 | 89.6705 | 88.3558 | 5365:39 | 83:50 | 89.6705 | 88.3558
3 | Gadag | 79 | 79 | 81:20 | 81:20 | 1967:07 | 2132:34 | 4099:41 | 4099:41 | 4181:01 | 52:55 | 92.7924 | 92.6494 | 4181:01 | 52:55 | 92.7924 | 92.6494
4 | Ron | 49 | 49 | 113:31 | 113:31 | 807:40 | 1267:56 | 2075:36 | 2075:36 | 2189:07 | 44:41 | 94.1168 | 93.795 | 2189:07 | 44:41 | 94.1168 | 93.795
5 | Haveri | 185 | 185 | 1427:53 | 1427:53 | 3163:52 | 5168:39 | 8332:31 | 8332:31 | 9760:24 | 52:46 | 93.7444 | 92.6724 | 9760:24 | 52:46 | 93.7444 | 92.6724
6 | Ranebennur | 169 | 169 | 608:08 | 608:08 | 3777:11 | 3500:26 | 7277:37 | 7277:37 | 7885:45 | 46:40 | 94.0191 | 93.5193 | 7885:45 | 46:40 | 94.0191 | 93.5193
7 | Sirsi | 45 | 45 | 408:46 | 408:46 | 570:24 | 1467:32 | 2037:56 | 2037:56 | 2446:42 | 54:22 | 93.7101 | 92.4485 | 2446:42 | 54:22 | 93.7101 | 92.4485
8 | Dandeli | 18 | 18 | 21:40 | 21:40 | 349:19 | 535:37 | 884:56 | 884:56 | 906:36 | 50:22 | 93.1718 | 93.0046 | 906:36 | 50:22 | 93.1718 | 93.0046
9 | Karwar | 33 | 33 | 384:14 | 384:14 | 393:46 | 190:20 | 584:06 | 584:06 | 968:20 | 29:21 | 97.5417 | 95.9245 | 968:20 | 29:21 | 97.5417 | 95.9245
10 | Honnavar | 36 | 36 | 442:01 | 442:01 | 364:04 | 182:08 | 546:12 | 546:12 | 988:13 | 27:27 | 97.8927 | 96.1874 | 988:13 | 27:27 | 97.8927 | 96.1874
11 | Belagavi | 130 | 130 | 180:12 | 180:12 | 2874:44 | 2285:35 | 5160:19 | 5160:19 | 5340:31 | 41:05 | 94.4868 | 94.2943 | 5340:31 | 41:05 | 94.4868 | 94.2943
12 | Bailhongal | 173 | 173 | 1489:09 | 1489:09 | 2919:05 | 3058:16 | 5977:21 | 5977:21 | 7466:30 | 43:10 | 95.2012 | 94.0057 | 7466:30 | 43:10 | 95.2012 | 94.0057
13 | Ramdurg | 69 | 69 | 673:10 | 673:10 | 1829:05 | 1071:05 | 2900:10 | 2900:10 | 3573:20 | 51:47 | 94.1623 | 92.8073 | 3573:20 | 51:47 | 94.1623 | 92.8073
14 | Ghataprabha | 153 | 153 | 269:34 | 269:34 | 1473:41 | 860:20 | 2334:01 | 2334:01 | 2603:35 | 17:01 | 97.8812 | 97.6365 | 2603:35 | 17:01 | 97.8812 | 97.6365
15 | Raibag | 155 | 155 | 430:35 | 430:35 | 3357:39 | 669:55 | 4027:34 | 4027:34 | 4458:09 | 28:46 | 96.3911 | 96.0052 | 4458:09 | 28:46 | 96.3911 | 96.0052
16 | Athani | 167 | 167 | 720:09 | 720:09 | 2533:03 | 1036:42 | 3569:45 | 3569:45 | 4289:54 | 25:41 | 97.0311 | 96.4322 | 4289:54 | 25:41 | 97.0311 | 96.4322
17 | Chikkodi | 176 | 176 | 213:03 | 213:03 | 1296:20 | 742:01 | 2038:21 | 2038:21 | 2251:24 | 12:48 | 98.3915 | 98.2233 | 2251:24 | 12:48 | 98.3915 | 98.2233
18 | Vijayapur | 146 | 146 | 542:03 | 542:03 | 2625:53 | 3610:46 | 6236:39 | 6236:39 | 6778:42 | 46:26 | 94.0671 | 93.5515 | 6778:42 | 46:26 | 94.0671 | 93.5515
19 | Indi | 222 | 222 | 1470:21 | 1470:21 | 2253:02 | 3566:37 | 5819:39 | 5819:39 | 7290:00 | 32:50 | 96.3591 | 95.4392 | 7290:00 | 32:50 | 96.3591 | 95.4392
20 | B.Bagewadi | 110 | 110 | 591:36 | 591:36 | 1488:10 | 1937:36 | 3425:46 | 3425:46 | 4017:22 | 36:31 | 95.6745 | 94.9276 | 4017:22 | 36:31 | 95.6745 | 94.9276
21 | Bagalkot | 156 | 156 | 528:32 | 528:32 | 2432:58 | 3354:28 | 5787:26 | 5787:26 | 6315:58 | 40:29 | 94.8474 | 94.3768 | 6315:58 | 40:29 | 94.8474 | 94.3768
22 | Jamkhandi | 214 | 214 | 559:18 | 559:18 | 1710:56 | 1412:33 | 3123:29 | 3123:29 | 3682:47 | 17:13 | 97.9728 | 97.6098 | 3682:47 | 17:13 | 97.9728 | 97.6098
23 | Mudhol | 154 | 154 | 168:23 | 168:23 | 1111:01 | 1135:34 | 2246:35 | 2246:35 | 2414:58 | 15:41 | 97.9739 | 97.822 | 2414:58 | 15:41 | 97.9739 | 97.822
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2019 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of May-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 37 | 37 | 208:00 | 493:20 | 1022:55 | 1287:46 | 2310:41 | 4747:06 | 2518:41 | 68:04 | 91.6061 | 90.8505 | 5240:26 | 141:38 | 91.2363 | 90.3256
2 | Dharwad Rural | 64 | 64 | 442:19 | 1048:08 | 1781:40 | 1813:10 | 3594:50 | 8354:40 | 4037:09 | 63:05 | 92.4504 | 91.5214 | 9402:48 | 146:55 | 91.0832 | 89.9646
3 | Gadag | 79 | 79 | 225:20 | 306:40 | 2050:55 | 2223:23 | 4274:18 | 8373:59 | 4499:38 | 56:57 | 92.7278 | 92.3444 | 8680:39 | 109:53 | 92.7596 | 92.4944
4 | Ron | 49 | 49 | 335:02 | 448:33 | 808:35 | 1391:59 | 2200:34 | 4276:10 | 2535:36 | 51:45 | 93.9638 | 93.0448 | 4724:43 | 96:25 | 94.039 | 93.4137
5 | Haveri | 188 | 188 | 1271:35 | 2699:28 | 3289:04 | 3173:56 | 6463:00 | 14795:31 | 7734:35 | 41:08 | 95.3793 | 94.4702 | 17494:59 | 93:04 | 94.6243 | 93.6436
6 | Ranebennur | 169 | 169 | 916:10 | 1524:18 | 3677:23 | 2844:26 | 6521:49 | 13799:26 | 7437:59 | 44:01 | 94.8131 | 94.0844 | 15323:44 | 90:40 | 94.4226 | 93.8065
7 | Sirsi | 46 | 46 | 263:56 | 672:42 | 873:58 | 994:15 | 1868:13 | 3906:09 | 2132:09 | 46:21 | 94.5412 | 93.77 | 4578:51 | 99:32 | 94.1997 | 93.2008
8 | Dandeli | 18 | 18 | 4:17 | 25:57 | 264:01 | 355:34 | 619:35 | 1504:31 | 623:52 | 34:40 | 95.3735 | 95.3415 | 1530:28 | 85:02 | 94.2907 | 94.1922
9 | Karwar | 33 | 33 | 607:36 | 991:50 | 561:12 | 465:44 | 1026:56 | 1611:02 | 1634:32 | 49:32 | 95.8173 | 93.3426 | 2602:52 | 78:52 | 96.6654 | 94.6124
10 | Honnavar | 36 | 36 | 714:19 | 1156:20 | 486:44 | 222:35 | 709:19 | 1255:31 | 1423:38 | 39:33 | 97.3517 | 94.6848 | 2411:51 | 67:00 | 97.6178 | 95.4238
11 | Belagavi | 131 | 131 | 325:31 | 505:43 | 2547:14 | 1755:04 | 4302:18 | 9462:37 | 4627:49 | 35:20 | 95.5858 | 95.2518 | 9968:20 | 76:06 | 95.066 | 94.8023
12 | Bailhongal | 175 | 175 | 1381:52 | 2871:01 | 2993:20 | 3044:45 | 6038:05 | 12015:26 | 7419:57 | 42:24 | 95.3625 | 94.3011 | 14886:27 | 85:04 | 95.3101 | 94.1895
13 | Ramdurg | 69 | 69 | 501:10 | 1174:20 | 1933:40 | 1594:10 | 3527:50 | 6428:00 | 4029:00 | 58:23 | 93.128 | 92.1517 | 7602:20 | 110:11 | 93.6367 | 92.4741
14 | Ghataprabha | 153 | 153 | 809:07 | 1078:41 | 1577:56 | 1942:45 | 3520:41 | 5854:42 | 4329:48 | 28:18 | 96.9071 | 96.1963 | 6933:23 | 45:19 | 97.3862 | 96.9046
15 | Raibag | 156 | 156 | 658:43 | 1089:18 | 3438:07 | 1215:26 | 4653:33 | 8681:07 | 5312:16 | 34:03 | 95.9905 | 95.423 | 9770:25 | 62:38 | 96.1989 | 95.7219
16 | Athani | 167 | 167 | 721:12 | 1441:21 | 2618:19 | 1833:02 | 4451:21 | 8021:06 | 5172:33 | 30:58 | 96.4174 | 95.8369 | 9462:27 | 56:40 | 96.7192 | 96.1297
17 | Chikkodi | 176 | 176 | 677:58 | 891:01 | 1500:36 | 1030:06 | 2530:42 | 4569:03 | 3208:40 | 18:14 | 98.0673 | 97.5496 | 5460:04 | 31:01 | 98.2267 | 97.8809
18 | Vijayapur | 146 | 146 | 786:04 | 1328:07 | 2165:03 | 3319:33 | 5484:36 | 11721:15 | 6270:40 | 42:57 | 94.9508 | 94.2272 | 13049:22 | 89:23 | 94.5162 | 93.8949
19 | Indi | 223 | 223 | 1006:49 | 2477:10 | 2726:00 | 2894:28 | 5620:28 | 11440:07 | 6627:17 | 29:43 | 96.6124 | 96.0055 | 13917:17 | 62:25 | 96.4958 | 95.7371
20 | B.Bagewadi | 110 | 110 | 965:25 | 1557:01 | 1715:50 | 2629:02 | 4344:52 | 7770:38 | 5310:17 | 48:17 | 94.691 | 93.5114 | 9327:39 | 84:48 | 95.1747 | 94.2079
21 | Bagalkot | 156 | 156 | 1889:33 | 2418:05 | 3011:19 | 3959:07 | 6970:26 | 12757:52 | 8859:59 | 56:48 | 93.9943 | 92.3663 | 15175:57 | 97:17 | 94.4139 | 93.3551
22 | Jamkhandi | 214 | 214 | 1232:42 | 1792:00 | 2002:48 | 2189:19 | 4192:07 | 7315:36 | 5424:49 | 25:21 | 97.367 | 96.5928 | 9107:36 | 42:34 | 97.665 | 97.093
23 | Mudhol | 155 | 155 | 112:58 | 281:21 | 1385:26 | 1868:56 | 3254:22 | 5500:57 | 3367:20 | 21:43 | 97.178 | 97.08 | 5782:18 | 37:18 | 97.5758 | 97.4518
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2019 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of Jun-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 37 | 37 | 321:45 | 815:05 | 1256:02 | 2052:41 | 3308:43 | 8055:49 | 3630:28 | 98:07 | 87.5799 | 86.3721 | 8870:54 | 239:45 | 90.0309 | 89.0223
2 | Dharwad Rural | 64 | 64 | 209:16 | 1257:24 | 2471:34 | 3564:30 | 6036:04 | 14390:44 | 6245:20 | 97:35 | 86.9009 | 86.4468 | 15648:08 | 244:30 | 89.7044 | 88.8048
3 | Gadag | 79 | 79 | 195:30 | 502:10 | 2518:04 | 3296:09 | 5814:13 | 14188:12 | 6009:43 | 76:04 | 89.7781 | 89.4344 | 14690:22 | 185:57 | 91.7767 | 91.4856
4 | Ron | 49 | 49 | 218:50 | 667:23 | 1289:55 | 2257:40 | 3547:35 | 7823:45 | 3766:25 | 76:52 | 89.9445 | 89.3242 | 8491:08 | 173:17 | 92.6892 | 92.0655
5 | Haveri | 188 | 188 | 2289:36 | 4989:04 | 4973:52 | 10062:26 | 15036:18 | 1242.9924 | 17325:54 | 92:10 | 88.8916 | 87.2001 | 1450.8701 | 185:13 | 92.7344 | 91.5193
6 | Ranebennur | 169 | 169 | 1454:43 | 2979:01 | 5270:18 | 7555:33 | 12825:51 | 1109.3868 | 14280:34 | 84:30 | 89.4594 | 88.2638 | 1233.5125 | 175:10 | 92.7864 | 91.9792
7 | Sirsi | 49 | 49 | 457:17 | 1129:59 | 1204:36 | 3034:24 | 4239:00 | 8145:09 | 4696:17 | 95:51 | 87.9847 | 86.6885 | 9275:08 | 189:17 | 92.3888 | 91.3329
8 | Dandeli | 19 | 19 | 50:47 | 76:44 | 379:40 | 707:26 | 1087:06 | 2591:37 | 1137:53 | 59:53 | 92.0534 | 91.6821 | 2668:21 | 140:26 | 93.7545 | 93.5696
9 | Karwar | 33 | 33 | 861:25 | 1853:15 | 583:34 | 1324:37 | 1908:11 | 3519:13 | 2769:36 | 83:56 | 91.9689 | 88.3434 | 5372:28 | 162:48 | 95.1171 | 92.5457
10 | Honnavar | 36 | 36 | 846:53 | 2003:13 | 826:38 | 1502:34 | 2329:12 | 3584:43 | 3176:05 | 88:13 | 91.0139 | 87.7466 | 5587:56 | 155:13 | 95.4407 | 92.8928
11 | Belagavi | 131 | 131 | 689:53 | 1195:36 | 2635:28 | 3927:41 | 6563:09 | 16025:46 | 7253:02 | 55:22 | 93.0416 | 92.3102 | 17221:22 | 131:28 | 94.3986 | 93.9807
12 | Bailhongal | 175 | 175 | 2493:17 | 5364:18 | 3877:57 | 7595:34 | 11473:31 | 23488:57 | 13966:48 | 79:49 | 90.894 | 88.9152 | 1202.2188 | 164:53 | 93.8543 | 92.4507
13 | Ramdurg | 69 | 69 | 931:10 | 2105:30 | 2016:40 | 3423:15 | 5439:55 | 11867:55 | 6371:05 | 92:20 | 89.0501 | 87.1758 | 13973:25 | 202:31 | 92.1246 | 90.7274
14 | Ghataprabha | 153 | 153 | 580:16 | 1658:57 | 2038:56 | 4562:42 | 6601:38 | 12456:20 | 7181:54 | 46:56 | 94.0072 | 93.4805 | 14115:17 | 92:15 | 96.2723 | 95.7758
15 | Raibag | 154 | 154 | 357:10 | 1446:28 | 4245:51 | 5007:13 | 9253:04 | 17934:11 | 9610:14 | 62:24 | 91.6549 | 91.3328 | 19380:39 | 125:51 | 94.6678 | 94.2377
16 | Athani | 168 | 168 | 704:43 | 2146:04 | 6202:44 | 3424:59 | 9627:43 | 17648:49 | 10332:26 | 61:30 | 92.0406 | 91.458 | 19794:53 | 117:50 | 95.1899 | 94.605
17 | Chikkodi | 176 | 176 | 411:10 | 1302:11 | 1912:01 | 3010:28 | 4922:29 | 9491:32 | 5333:39 | 30:18 | 96.1155 | 95.791 | 10793:43 | 61:20 | 97.5307 | 97.1919
18 | Vijayapur | 146 | 146 | 1144:04 | 2472:11 | 2465:43 | 6807:51 | 9273:34 | 20994:49 | 10417:38 | 71:21 | 91.1781 | 90.0898 | 23467:00 | 160:44 | 93.4157 | 92.6404
19 | Indi | 223 | 223 | 1492:46 | 3969:56 | 3892:13 | 7073:09 | 10965:22 | 22405:29 | 12458:08 | 55:52 | 93.1705 | 92.2408 | 1098.976 | 118:17 | 95.3996 | 94.5845
20 | B.Bagewadi | 111 | 111 | 2186:30 | 3743:31 | 2472:35 | 7083:35 | 9556:10 | 17326:48 | 11742:40 | 105:47 | 88.0428 | 85.307 | 21070:19 | 189:49 | 92.8527 | 91.3085
21 | Bagalkot | 144 | 144 | 1279:42 | 3697:47 | 4090:41 | 9642:06 | 13732:47 | 1103.7771 | 15012:29 | 104:15 | 86.7546 | 85.5204 | 1257.8514 | 209:39 | 91.5768 | 90.401
22 | Jamkhandi | 214 | 214 | 3761:56 | 5553:56 | 2545:13 | 4559:24 | 7104:37 | 14420:13 | 10866:33 | 50:47 | 95.389 | 92.9475 | 19974:09 | 93:20 | 96.9146 | 95.7263
23 | Mudhol | 153 | 153 | 1211:26 | 1492:47 | 1966:52 | 4038:27 | 6005:19 | 11506:16 | 7216:45 | 47:10 | 94.5486 | 93.4488 | 12999:03 | 84:58 | 96.5566 | 96.1098
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of July-2019 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of July-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 43 | 43 | 251:25 | 1066:30 | 1291:19 | 1324:28 | 2615:47 | 10671:36 | 2867:12 | 66:41 | 91.8236 | 91.0378 | 11738:06 | 272:59 | 91.524 | 90.6769
2 | Dharwad Rural | 64 | 64 | 144:55 | 1402:19 | 2024:36 | 3472:15 | 5496:51 | 19887:35 | 5641:46 | 88:09 | 88.4559 | 88.1515 | 21289:54 | 332:39 | 89.3872 | 88.6388
3 | Gadag | 79 | 79 | 271:55 | 774:05 | 1785:35 | 3448:17 | 5233:52 | 19422:04 | 5505:47 | 69:42 | 91.0952 | 90.6326 | 20196:09 | 255:39 | 91.6035 | 91.2689
4 | Ron | 51 | 51 | 220:47 | 888:10 | 1045:05 | 1398:35 | 2443:40 | 10267:25 | 2664:27 | 52:15 | 93.5598 | 92.9779 | 11155:35 | 218:44 | 93.1243 | 92.5295
5 | Haveri | 189 | 189 | 1491:19 | 6480:23 | 4809:39 | 10670:31 | 15480:10 | 1887.9993 | 16971:29 | 89:48 | 88.9912 | 87.9306 | 2158.0153 | 274:02 | 91.812 | 90.6409
6 | Ranebennur | 169 | 169 | 578:05 | 3557:06 | 4267:31 | 6696:54 | 10964:25 | 1566.2375 | 11542:30 | 68:18 | 91.2798 | 90.8201 | 1714.45 | 243:28 | 92.4035 | 91.6847
7 | Sirsi | 51 | 51 | 220:30 | 1350:29 | 1184:12 | 2718:28 | 3902:40 | 12047:49 | 4123:10 | 80:51 | 89.7147 | 89.1335 | 13398:18 | 262:43 | 91.932 | 91.0276
8 | Dandeli | 19 | 19 | 57:48 | 134:32 | 518:17 | 555:04 | 1073:21 | 3664:58 | 1131:09 | 59:32 | 92.407 | 91.9981 | 3799:30 | 199:58 | 93.4121 | 93.1703
9 | Karwar | 33 | 33 | 524:32 | 2377:47 | 571:17 | 1000:31 | 1571:48 | 5091:01 | 2096:20 | 63:32 | 93.5981 | 91.4617 | 7468:48 | 226:20 | 94.7311 | 92.2702
10 | Honnavar | 36 | 36 | 1132:30 | 3135:43 | 810:33 | 1206:13 | 2016:46 | 5601:29 | 3149:16 | 87:29 | 92.4703 | 88.242 | 8737:12 | 242:42 | 94.6859 | 91.7111
11 | Belagavi | 132 | 132 | 398:32 | 1594:08 | 3617:14 | 3772:54 | 7390:08 | 23415:54 | 7788:40 | 59:00 | 92.475 | 92.0692 | 1042.0847 | 189:28 | 93.9415 | 93.529
12 | Bailhongal | 179 | 179 | 381:16 | 5745:34 | 4382:19 | 6320:04 | 10702:23 | 1424.6389 | 11083:39 | 61:55 | 91.9637 | 91.6774 | 1664.0375 | 223:07 | 93.4763 | 92.3801
13 | Ramdurg | 69 | 69 | 209:10 | 2314:40 | 1704:40 | 1760:00 | 3464:40 | 15332:35 | 3673:50 | 53:15 | 93.251 | 92.8436 | 17647:15 | 255:45 | 92.4108 | 91.2651
14 | Ghataprabha | 153 | 153 | 455:40 | 2114:37 | 1877:30 | 2160:38 | 4038:08 | 16494:28 | 4493:48 | 29:22 | 96.4525 | 96.0523 | 18609:05 | 121:38 | 96.3181 | 95.846
15 | Raibag | 154 | 154 | 445:34 | 1892:02 | 4662:30 | 2557:15 | 7219:45 | 1048.0806 | 7665:19 | 49:46 | 93.6987 | 93.3098 | 1126.9153 | 175:37 | 94.4215 | 94.0019
16 | Athani | 173 | 173 | 549:05 | 2695:09 | 4032:13 | 3180:37 | 7212:50 | 1035.9021 | 7761:55 | 44:52 | 94.3961 | 93.9695 | 1148.2 | 159:17 | 95.0919 | 94.5598
17 | Chikkodi | 176 | 176 | 351:43 | 1653:54 | 2343:47 | 1700:30 | 4044:17 | 13535:49 | 4396:00 | 24:59 | 96.9114 | 96.6428 | 15189:43 | 86:18 | 97.3734 | 97.0524
18 | Vijayapur | 147 | 147 | 1119:11 | 3591:22 | 2179:08 | 4815:48 | 6994:56 | 1166.2396 | 8114:07 | 55:12 | 93.6042 | 92.5809 | 1315.8799 | 214:50 | 93.497 | 92.6627
19 | Indi | 225 | 225 | 944:39 | 4914:35 | 4201:13 | 5104:33 | 9305:46 | 1321.3021 | 10250:25 | 45:33 | 94.441 | 93.8767 | 1526.0767 | 162:47 | 95.1865 | 94.4405
20 | B.Bagewadi | 111 | 111 | 347:56 | 4091:27 | 2732:35 | 4016:30 | 6749:05 | 1003.1618 | 7097:01 | 63:56 | 91.8276 | 91.4063 | 1173.6389 | 253:46 | 92.5922 | 91.3333
21 | Bagalkot | 163 | 163 | 751:03 | 4448:50 | 4070:27 | 8681:59 | 12752:26 | 1635.1285 | 13503:29 | 82:51 | 89.4844 | 88.8651 | 1820.4965 | 268:03 | 91.7775 | 90.8453
22 | Jamkhandi | 214 | 214 | 315:20 | 5869:16 | 2496:10 | 2067:59 | 4564:09 | 18984:22 | 4879:29 | 22:48 | 97.1334 | 96.9353 | 1035.5681 | 116:08 | 96.9702 | 96.0335
23 | Mudhol | 156 | 156 | 228:31 | 1721:18 | 1657:33 | 2236:41 | 3894:14 | 15400:30 | 4122:45 | 26:26 | 96.6448 | 96.4479 | 17121:48 | 109:45 | 96.6284 | 96.2515
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of August-2019 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of Aug-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 43 | 43 | 86:50 | 1153:20 | 2963:46 | 812:31 | 3776:17 | 14447:53 | 3863:07 | 89:50 | 88.1962 | 87.9247 | 15601:13 | 362:49 | 90.8497 | 90.1193
2 | Dharwad Rural | 64 | 64 | 149:10 | 1551:29 | 4683:29 | 5300:45 | 9984:14 | 1244.659 | 10133:24 | 158:20 | 79.0318 | 78.7185 | 1309.3042 | 490:59 | 87.289 | 86.6288
3 | Gadag | 81 | 81 | 119:25 | 893:30 | 3569:10 | 5111:04 | 8680:14 | 1170.9292 | 8799:39 | 108:38 | 85.5963 | 85.3982 | 1208.1583 | 357:58 | 90.5517 | 90.2513
4 | Ron | 51 | 51 | 160:21 | 1048:31 | 2368:25 | 1285:32 | 3653:57 | 13921:22 | 3814:18 | 74:47 | 90.3702 | 89.9476 | 14969:53 | 293:32 | 92.5662 | 92.0063
5 | Haveri | 189 | 189 | 2131:41 | 8612:04 | 10328:28 | 20887:56 | 1300.6833 | 3188.6826 | 1389.5035 | 176:27 | 77.8003 | 76.2843 | 3547.5187 | 450:29 | 88.973 | 87.7321
6 | Ranebennur | 169 | 169 | 706:06 | 4263:12 | 7577:01 | 13118:48 | 20695:49 | 2428.5633 | 21401:55 | 126:38 | 83.5403 | 82.9787 | 2606.1966 | 370:07 | 90.6077 | 89.9207
7 | Sirsi | 51 | 51 | 998:07 | 2348:36 | 1252:18 | 3288:40 | 4540:58 | 16588:47 | 5539:05 | 108:37 | 88.0325 | 85.402 | 18937:23 | 371:19 | 91.1419 | 89.8878
8 | Dandeli | 19 | 19 | 26:18 | 160:50 | 980:15 | 777:28 | 1757:43 | 5422:41 | 1784:01 | 93:54 | 87.5657 | 87.3796 | 5583:31 | 293:52 | 92.2275 | 91.997
9 | Karwar | 33 | 33 | 993:38 | 3371:25 | 1128:39 | 1369:00 | 2497:39 | 7588:40 | 3491:17 | 105:48 | 89.8271 | 85.78 | 10960:05 | 332:07 | 93.7375 | 90.9552
10 | Honnavar | 36 | 36 | 1598:30 | 4734:13 | 1140:39 | 1615:48 | 2756:27 | 8357:56 | 4354:57 | 120:58 | 89.7086 | 83.7405 | 13092:09 | 363:40 | 93.6774 | 90.0961
11 | Belagavi | 132 | 132 | 1285:54 | 2880:02 | 10029:30 | 8408:10 | 18437:40 | 1743.8986 | 19723:34 | 149:25 | 81.2259 | 79.9165 | 1863.9 | 338:53 | 91.3651 | 90.7709
12 | Bailhongal | 179 | 179 | 2899:26 | 8645:00 | 6478:15 | 13882:27 | 20360:42 | 2273.0014 | 23260:08 | 129:57 | 84.7114 | 82.5343 | 2633.2097 | 353:03 | 91.7004 | 90.3852
13 | Ramdurg | 69 | 69 | 174:05 | 2488:45 | 1794:30 | 3015:25 | 4809:55 | 20142:30 | 4984:00 | 72:14 | 90.6305 | 90.2914 | 22631:15 | 327:59 | 92.0501 | 91.0678
14 | Ghataprabha | 155 | 155 | 637:15 | 2751:52 | 5014:04 | 3162:55 | 8176:59 | 1027.9771 | 8814:14 | 56:52 | 92.9093 | 92.3567 | 1142.6382 | 176:55 | 95.6653 | 95.1818
15 | Raibag | 154 | 154 | 525:02 | 2417:04 | 7307:44 | 5690:43 | 12998:27 | 1589.6826 | 13523:29 | 87:49 | 88.6552 | 88.1969 | 1690.3938 | 263:26 | 93.2532 | 92.8258
16 | Athani | 173 | 173 | 2146:13 | 4841:22 | 5016:59 | 2008:01 | 7025:00 | 1328.6104 | 9171:13 | 53:01 | 94.5421 | 92.8746 | 1530.334 | 212:18 | 94.9805 | 94.2184
17 | Chikkodi | 176 | 176 | 372:21 | 2026:16 | 4235:32 | 4145:28 | 8381:00 | 21916:49 | 8753:21 | 49:44 | 93.5996 | 93.3152 | 23943:05 | 136:02 | 96.6087 | 96.2952
18 | Vijayapur | 147 | 147 | 285:17 | 3876:39 | 2893:56 | 3600:46 | 6494:42 | 1436.8521 | 6779:59 | 46:07 | 94.0616 | 93.8008 | 1598.3792 | 260:58 | 93.6114 | 92.8932
19 | Indi | 225 | 225 | 1147:41 | 6062:16 | 4008:19 | 5454:38 | 9462:57 | 1715.5917 | 10610:38 | 47:10 | 94.3471 | 93.6615 | 1968.1864 | 209:56 | 95.0164 | 94.2827
20 | B.Bagewadi | 113 | 113 | 750:30 | 4841:57 | 2259:45 | 3156:05 | 5415:50 | 1228.8215 | 6166:20 | 54:34 | 93.5581 | 92.6654 | 1430.5694 | 303:50 | 92.8925 | 91.7256
21 | Bagalkot | 167 | 167 | 756:50 | 5205:40 | 8320:09 | 4680:24 | 13000:33 | 2176.8181 | 13757:23 | 82:23 | 89.5366 | 88.9275 | 2393.7208 | 344:00 | 91.4805 | 90.6316
22 | Jamkhandi | 214 | 214 | 587:39 | 6456:55 | 8663:14 | 2185:34 | 10848:48 | 1243.0486 | 11436:27 | 53:26 | 93.1861 | 92.817 | 1512.0868 | 169:35 | 96.2035 | 95.3818
23 | Mudhol | 158 | 158 | 506:48 | 2228:06 | 7676:15 | 2488:46 | 10165:01 | 1065.2299 | 10671:49 | 67:33 | 91.3527 | 90.9216 | 1158.0674 | 175:55 | 95.5935 | 95.2095
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of September-2019 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of Sept-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 92:25 | 1245:45 | 1410:09 | 1382:02 | 2792:11 | 17240:04 | 2884:36 | 65:34 | 91.1863 | 90.8946 | 18485:49 | 420:08 | 91.0788 | 90.4341
2 | Dharwad Rural | 64 | 64 | 99:10 | 1650:39 | 2316:03 | 2387:55 | 4703:58 | 1440.6576 | 4803:08 | 75:03 | 89.7917 | 89.5765 | 1509.4347 | 566:02 | 87.6993 | 87.1121
3 | Gadag | 82 | 82 | 207:40 | 1101:10 | 1780:02 | 3105:09 | 4885:11 | 1374.4785 | 5092:51 | 62:06 | 91.7256 | 91.3739 | 1420.3604 | 415:43 | 90.8405 | 90.5347
4 | Ron | 51 | 51 | 284:05 | 1332:36 | 1296:20 | 1869:35 | 3165:55 | 17087:17 | 3450:00 | 67:39 | 91.3782 | 90.6046 | 18419:53 | 361:10 | 92.3715 | 91.7765
5 | Haveri | 189 | 189 | 1445:28 | 10057:32 | 4323:43 | 11531:50 | 15855:33 | 3849.3306 | 17301:01 | 91:32 | 88.3484 | 87.2861 | 4268.3944 | 542:01 | 88.8706 | 87.659
6 | Ranebennur | 170 | 170 | 292:53 | 4556:05 | 4600:07 | 5585:20 | 10185:27 | 2852.9571 | 10478:20 | 61:38 | 91.6786 | 91.4393 | 3042.7939 | 429:34 | 90.8295 | 90.2192
7 | Sirsi | 51 | 51 | 666:10 | 3014:46 | 827:47 | 1665:51 | 2493:38 | 19082:25 | 3159:48 | 61:57 | 93.2091 | 91.3949 | 22097:11 | 433:17 | 91.4808 | 90.1348
8 | Dandeli | 19 | 19 | 66:34 | 227:24 | 256:32 | 371:55 | 628:27 | 6051:08 | 695:01 | 36:35 | 95.4061 | 94.9195 | 6278:32 | 330:27 | 92.7486 | 92.4761
9 | Karwar | 33 | 33 | 220:27 | 3591:52 | 333:36 | 389:26 | 723:02 | 8311:42 | 943:29 | 28:35 | 96.9569 | 96.0291 | 11903:34 | 360:43 | 94.2653 | 91.787
10 | Honnavar | 36 | 36 | 484:18 | 5218:31 | 485:12 | 524:07 | 1009:19 | 9367:15 | 1493:37 | 41:29 | 96.106 | 94.2376 | 14585:46 | 405:10 | 94.0756 | 90.775
11 | Belagavi | 132 | 132 | 359:27 | 3239:29 | 2844:50 | 2980:29 | 5825:19 | 1986.6201 | 6184:46 | 46:51 | 93.8707 | 93.4925 | 2121.5986 | 385:45 | 91.7759 | 91.2171
12 | Bailhongal | 179 | 179 | 1181:16 | 9826:16 | 4901:05 | 4502:33 | 9403:38 | 2664.8194 | 10584:54 | 59:08 | 92.7036 | 91.787 | 3074.2472 | 412:11 | 91.8649 | 90.615
13 | Ramdurg | 69 | 69 | 184:50 | 2673:35 | 1330:20 | 2036:10 | 3366:30 | 23509:00 | 3551:20 | 51:28 | 93.2236 | 92.8516 | 1090.941 | 379:27 | 92.2425 | 91.3603
14 | Ghataprabha | 155 | 155 | 497:10 | 3249:02 | 1806:01 | 2124:31 | 3930:32 | 1191.7493 | 4427:42 | 28:34 | 96.478 | 96.0325 | 1327.1257 | 205:29 | 95.7985 | 95.3213
15 | Raibag | 156 | 156 | 491:20 | 2908:24 | 6190:05 | 1592:58 | 7783:03 | 1913.9764 | 8274:23 | 53:02 | 93.0706 | 92.6332 | 2035.1597 | 313:06 | 93.2956 | 92.8711
16 | Athani | 175 | 175 | 1043:50 | 5885:12 | 6782:13 | 3895:15 | 10677:28 | 1773.5049 | 11721:18 | 66:59 | 91.5258 | 90.6974 | 2018.7215 | 276:51 | 94.4621 | 93.6964
17 | Chikkodi | 176 | 176 | 441:02 | 2467:18 | 2145:58 | 2511:59 | 4657:57 | 1107.2819 | 5098:59 | 28:58 | 96.3242 | 95.9762 | 1210.086 | 165:01 | 96.5621 | 96.2429
18 | Vijayapur | 146 | 146 | 809:41 | 4686:20 | 2018:34 | 5694:18 | 7712:52 | 1758.2215 | 8522:33 | 58:22 | 92.6628 | 91.8926 | 1953.4854 | 321:07 | 93.4193 | 92.6885
19 | Indi | 225 | 225 | 966:49 | 7029:05 | 3803:06 | 7236:28 | 11039:34 | 2175.5736 | 12006:23 | 53:22 | 93.1855 | 92.5887 | 2468.4524 | 263:18 | 94.7163 | 94.005
20 | B.Bagewadi | 113 | 113 | 689:13 | 5531:10 | 2231:41 | 4605:44 | 6837:25 | 1513.7139 | 7526:38 | 66:36 | 91.5961 | 90.749 | 1744.1792 | 370:27 | 92.6799 | 91.5655
21 | Bagalkot | 167 | 167 | 1141:27 | 6347:07 | 3717:49 | 5271:19 | 8989:08 | 2551.3653 | 10130:35 | 60:40 | 92.524 | 91.5747 | 2815.8285 | 404:40 | 91.6516 | 90.7862
22 | Jamkhandi | 214 | 214 | 407:30 | 6864:25 | 3474:01 | 2875:43 | 6349:44 | 1507.6208 | 6757:14 | 31:35 | 95.8789 | 95.6145 | 1793.6382 | 201:09 | 96.1503 | 95.42
23 | Mudhol | 160 | 160 | 52:02 | 2280:08 | 3240:20 | 3628:10 | 6868:30 | 1351.4174 | 6920:32 | 43:15 | 94.0378 | 93.9926 | 1446.4229 | 216:58 | 95.3845 | 95.06
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of October-2019 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of Oct-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 256:40 | 1502:25 | 1594:44 | 3065:00 | 4659:44 | 21899:48 | 4916:24 | 111:44 | 85.7657 | 84.9817 | 23402:13 | 531:52 | 90.3091 | 89.6443
2 | Dharwad Rural | 64 | 64 | 128:25 | 1779:04 | 3200:28 | 3945:12 | 7145:40 | 1738.3937 | 7274:05 | 113:39 | 84.9931 | 84.7234 | 1812.5215 | 679:42 | 87.3073 | 86.7661
3 | Gadag | 83 | 83 | 151:40 | 1252:50 | 2403:39 | 5455:40 | 7859:19 | 1701.95 | 8010:59 | 96:31 | 87.2728 | 87.0272 | 1754.1514 | 507:13 | 90.418 | 90.1241
4 | Ron | 51 | 51 | 119:30 | 1452:06 | 1474:35 | 3265:45 | 4740:20 | 21827:37 | 4859:50 | 95:17 | 87.507 | 87.1921 | 23279:43 | 456:28 | 91.6668 | 91.1124
5 | Haveri | 189 | 189 | 2166:20 | 12223:52 | 4016:18 | 19190:28 | 23206:46 | 4816.2792 | 1057.2125 | 134:15 | 83.4964 | 81.9558 | 5325.6069 | 676:16 | 88.0921 | 86.8328
6 | Ranebennur | 171 | 171 | 828:50 | 5384:55 | 4571:15 | 13913:59 | 18485:14 | 3623.1751 | 19314:04 | 112:57 | 85.4703 | 84.8188 | 3847.5466 | 540:00 | 90.099 | 89.4859
7 | Sirsi | 51 | 51 | 178:35 | 3193:21 | 714:06 | 2669:42 | 3383:48 | 22466:13 | 3562:23 | 69:51 | 91.0821 | 90.6115 | 1069.1486 | 503:08 | 91.423 | 90.2039
8 | Dandeli | 19 | 19 | 33:03 | 260:27 | 247:13 | 563:01 | 810:14 | 6861:22 | 843:17 | 44:23 | 94.2683 | 94.0345 | 7121:49 | 374:50 | 92.9688 | 92.7019
9 | Karwar | 33 | 33 | 1137:34 | 4729:26 | 620:18 | 1257:15 | 1877:33 | 10189:15 | 3015:07 | 91:22 | 92.3528 | 87.7195 | 14918:41 | 452:05 | 93.9882 | 91.1978
10 | Honnavar | 36 | 36 | 924:23 | 6142:54 | 680:58 | 1265:34 | 1946:32 | 11313:47 | 2870:55 | 79:45 | 92.7325 | 89.2812 | 17456:41 | 484:54 | 93.881 | 90.5586
11 | Belagavi | 132 | 132 | 494:04 | 3733:33 | 3181:35 | 4748:11 | 7929:46 | 2317.0271 | 8423:50 | 63:49 | 91.9255 | 91.4225 | 2472.5917 | 449:34 | 91.7976 | 91.2468
12 | Bailhongal | 183 | 183 | 921:27 | 10747:43 | 3514:31 | 9041:42 | 12556:13 | 3187.9951 | 13477:40 | 73:39 | 90.7778 | 90.101 | 3635.8167 | 476:50 | 91.8595 | 90.716
13 | Ramdurg | 69 | 69 | 122:25 | 2796:00 | 1626:15 | 6068:40 | 7694:55 | 1300.1632 | 7817:20 | 113:18 | 85.0107 | 84.7722 | 1416.6632 | 492:45 | 91.1949 | 90.4059
14 | Ghataprabha | 156 | 156 | 582:00 | 3831:02 | 2695:11 | 5752:40 | 8447:51 | 1543.7431 | 9029:51 | 57:53 | 92.7214 | 92.2199 | 1703.3694 | 262:03 | 95.3758 | 94.8976
15 | Raibag | 156 | 156 | 286:15 | 3194:39 | 6064:22 | 5122:30 | 11186:52 | 2380.0958 | 11473:07 | 73:33 | 90.3615 | 90.1148 | 2513.2063 | 386:39 | 92.8705 | 92.4718
16 | Athani | 175 | 175 | 930:58 | 6816:10 | 3540:34 | 2770:46 | 6311:20 | 2036.4771 | 7242:18 | 41:23 | 95.1526 | 94.4376 | 2320.484 | 318:14 | 94.5621 | 93.8038
17 | Chikkodi | 176 | 176 | 261:57 | 2729:15 | 1885:20 | 3263:07 | 5148:27 | 1321.8007 | 5410:24 | 30:44 | 96.0682 | 95.8682 | 1435.5193 | 195:45 | 96.4905 | 96.1886
18 | Vijayapur | 147 | 147 | 994:38 | 5680:58 | 3262:11 | 8855:15 | 12117:26 | 2263.1146 | 13112:04 | 89:12 | 88.9205 | 88.0111 | 2499.8215 | 408:08 | 92.8059 | 92.0535
19 | Indi | 231 | 231 | 897:23 | 7926:28 | 4488:55 | 11311:23 | 15800:18 | 2833.9194 | 16697:41 | 72:17 | 90.8065 | 90.2844 | 3164.1892 | 328:45 | 94.2673 | 93.5992
20 | B.Bagewadi | 115 | 115 | 436:30 | 5967:40 | 4392:33 | 7866:34 | 12259:07 | 2024.5104 | 12695:37 | 110:24 | 85.6719 | 85.1617 | 2273.1632 | 474:24 | 91.7736 | 90.7633
21 | Bagalkot | 167 | 167 | 463:18 | 6810:25 | 5812:59 | 8576:48 | 14389:47 | 3150.9396 | 14853:05 | 88:56 | 88.4185 | 88.0456 | 3434.7069 | 493:37 | 91.1832 | 90.3892
22 | Jamkhandi | 214 | 214 | 736:24 | 7600:49 | 3324:42 | 3900:18 | 7225:00 | 1808.6625 | 7961:24 | 37:12 | 95.4621 | 94.9996 | 2125.3632 | 238:22 | 96.0506 | 95.3591
23 | Mudhol | 160 | 160 | 411:36 | 2691:44 | 1958:30 | 3460:20 | 5418:50 | 1577.2021 | 5830:26 | 36:26 | 95.4479 | 95.1021 | 1689.3576 | 253:24 | 95.3937 | 95.0661
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of November-2019 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of November-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 49:20 | 1551:45 | 1507:34 | 784:41 | 2292:15 | 1008.0021 | 2341:35 | 53:13 | 92.7644 | 92.6086 | 1072.6583 | 585:05 | 90.611 | 90.0088
2 | Dharwad Rural | 64 | 64 | 59:55 | 1838:59 | 1605:06 | 1425:44 | 3030:50 | 1864.6785 | 3090:45 | 48:18 | 93.4227 | 93.2926 | 1941.3028 | 727:59 | 88.0592 | 87.5685
3 | Gadag | 83 | 83 | 152:30 | 1405:20 | 1474:54 | 2201:31 | 3676:25 | 1855.134 | 3828:55 | 46:08 | 93.848 | 93.5928 | 1913.6896 | 553:21 | 90.8397 | 90.5506
4 | Ron | 51 | 51 | 165:30 | 1617:36 | 1154:50 | 648:30 | 1803:20 | 23630:57 | 1968:50 | 38:36 | 95.089 | 94.6383 | 1052.0229 | 495:04 | 92.0876 | 91.5459
5 | Haveri | 189 | 189 | 989:30 | 13213:22 | 3592:01 | 5030:16 | 8622:17 | 5175.541 | 9611:47 | 50:51 | 93.6638 | 92.9367 | 5726.0979 | 727:07 | 88.7771 | 87.5833
6 | Ranebennur | 171 | 171 | 272:26 | 5657:21 | 3727:32 | 4218:11 | 7945:43 | 3954.2466 | 8218:09 | 48:04 | 93.5464 | 93.3251 | 4189.9696 | 588:04 | 90.5228 | 89.9579
7 | Sirsi | 51 | 51 | 194:38 | 3387:59 | 624:44 | 1576:45 | 2201:29 | 1027.8208 | 2396:07 | 46:59 | 94.0047 | 93.4746 | 1168.9868 | 550:07 | 91.7404 | 90.606
8 | Dandeli | 19 | 19 | 74:00 | 334:27 | 314:57 | 231:54 | 546:51 | 7408:13 | 620:51 | 32:41 | 96.0026 | 95.4616 | 7742:40 | 407:31 | 93.3418 | 93.0412
9 | Karwar | 33 | 33 | 280:10 | 5009:36 | 432:10 | 188:56 | 621:06 | 10810:21 | 901:16 | 27:19 | 97.3859 | 96.2068 | 15819:57 | 479:24 | 94.406 | 91.8137
10 | Honnavar | 37 | 37 | 439:05 | 6581:59 | 481:22 | 293:22 | 774:44 | 12088:31 | 1213:49 | 32:48 | 97.0918 | 95.4436 | 18670:30 | 504:36 | 94.4208 | 91.3831
11 | Belagavi | 132 | 132 | 159:49 | 3893:22 | 2886:12 | 1528:10 | 4414:22 | 2500.959 | 4574:11 | 34:39 | 95.3553 | 95.1871 | 2663.1826 | 484:13 | 92.235 | 91.7313
12 | Bailhongal | 184 | 184 | 550:40 | 11298:23 | 2314:32 | 2767:51 | 5082:23 | 3399.7611 | 5633:03 | 30:37 | 96.1637 | 95.748 | 3870.5271 | 504:51 | 92.4275 | 91.3789
13 | Ramdurg | 69 | 69 | 82:15 | 2878:15 | 1449:15 | 1366:44 | 2815:59 | 1417.4958 | 2898:14 | 42:00 | 94.3318 | 94.1662 | 1537.4229 | 534:45 | 91.5806 | 90.8682
14 | Ghataprabha | 156 | 156 | 251:45 | 4082:47 | 1191:15 | 1113:33 | 2304:48 | 1639.7764 | 2556:33 | 16:23 | 97.948 | 97.7239 | 1809.8924 | 278:27 | 95.6921 | 95.2451
15 | Raibag | 156 | 156 | 265:27 | 3460:06 | 5282:40 | 835:00 | 6117:40 | 2634.9986 | 6383:07 | 40:55 | 94.5534 | 94.317 | 2779.1694 | 427:34 | 93.0775 | 92.6987
16 | Athani | 175 | 175 | 414:09 | 7230:19 | 4704:45 | 916:10 | 5620:55 | 2270.6819 | 6035:04 | 34:29 | 95.539 | 95.2103 | 2571.9451 | 352:43 | 94.6822 | 93.9767
17 | Chikkodi | 176 | 176 | 142:48 | 2872:03 | 1409:24 | 862:59 | 2272:23 | 1416.4833 | 2415:11 | 13:43 | 98.2068 | 98.0941 | 1536.152 | 209:29 | 96.7016 | 96.4229
18 | Vijayapur | 147 | 147 | 435:47 | 6116:45 | 1814:37 | 8427:24 | 10242:01 | 2689.8653 | 10677:48 | 72:38 | 90.3231 | 89.9114 | 2944.7299 | 480:46 | 92.5007 | 91.7901
19 | Indi | 231 | 231 | 1131:34 | 9058:02 | 2179:44 | 3380:41 | 5560:25 | 3065.6035 | 6691:59 | 28:58 | 96.6568 | 95.9764 | 3443.0218 | 357:43 | 94.5611 | 93.8915
20 | B.Bagewadi | 120 | 120 | 530:38 | 6498:18 | 1428:23 | 2704:25 | 4132:48 | 2196.7104 | 4663:26 | 38:52 | 95.2167 | 94.6025 | 2467.4729 | 493:30 | 92.4976 | 91.5728
21 | Bagalkot | 168 | 168 | 841:47 | 7652:12 | 2674:58 | 3236:57 | 5911:55 | 3397.2694 | 6753:42 | 40:12 | 95.1125 | 94.4166 | 3716.1111 | 530:52 | 91.7124 | 90.9345
22 | Jamkhandi | 214 | 214 | 303:00 | 7903:49 | 1904:54 | 1005:02 | 2909:56 | 1929.9097 | 3212:56 | 15:01 | 98.1114 | 97.9148 | 2259.2354 | 253:22 | 96.304 | 95.6733
23 | Mudhol | 160 | 160 | 89:50 | 2781:34 | 1124:46 | 1093:48 | 2218:34 | 1669.6424 | 2308:24 | 14:26 | 98.0742 | 97.9962 | 1785.541 | 267:50 | 95.7233 | 95.4264
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of December-2019 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of December-2019 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 68:40 | 1620:25 | 844:18 | 509:51 | 1354:09 | 1064.425 | 1422:49 | 32:20 | 95.8634 | 95.6537 | 1131.9424 | 617:25 | 91.2031 | 90.6451
2 | Dharwad Rural | 64 | 64 | 155:05 | 1994:04 | 1651:21 | 1039:09 | 2690:30 | 1976.7826 | 2845:35 | 44:28 | 94.3496 | 94.0239 | 2059.8688 | 772:27 | 88.7683 | 88.2962
3 | Gadag | 83 | 83 | 45:40 | 1451:00 | 1555:56 | 1838:12 | 3394:08 | 1996.5562 | 3439:48 | 41:27 | 94.5036 | 94.4297 | 2057.0146 | 594:48 | 91.2528 | 90.9879
4 | Ron | 51 | 51 | 41:00 | 1658:36 | 653:00 | 511:55 | 1164:55 | 1033.1611 | 1205:55 | 23:39 | 96.9299 | 96.8219 | 1102.2694 | 518:43 | 92.6334 | 92.1407
5 | Haveri | 191 | 191 | 808:40 | 14022:02 | 3179:10 | 2689:20 | 5868:30 | 5420.0618 | 6677:10 | 34:58 | 95.8703 | 95.3012 | 6004.3132 | 754:28 | 89.681 | 88.5687
6 | Ranebennur | 172 | 172 | 344:25 | 6001:46 | 3725:04 | 2020:52 | 5745:56 | 4193.6605 | 6090:21 | 35:25 | 95.5099 | 95.2407 | 4443.7341 | 620:03 | 91.1339 | 90.6052
7 | Sirsi | 51 | 51 | 174:47 | 3562:46 | 434:35 | 507:28 | 942:03 | 1067.0729 | 1116:50 | 21:54 | 97.5173 | 97.0566 | 1215.5215 | 572:01 | 92.3916 | 91.3332
8 | Dandeli | 19 | 19 | 18:29 | 352:56 | 277:25 | 216:17 | 493:42 | 7901:55 | 512:11 | 26:57 | 96.5075 | 96.3767 | 8254:51 | 434:28 | 93.6986 | 93.4172
9 | Karwar | 33 | 33 | 393:58 | 5403:34 | 432:10 | 242:40 | 674:50 | 11485:11 | 1068:48 | 32:23 | 97.2514 | 95.6468 | 16888:45 | 511:47 | 94.7267 | 92.2458
10 | Honnavar | 37 | 37 | 159:11 | 6741:10 | 289:53 | 181:50 | 471:43 | 12560:14 | 630:54 | 17:03 | 98.2864 | 97.7082 | 19301:24 | 521:40 | 94.8566 | 92.0961
11 | Belagavi | 132 | 132 | 591:53 | 4485:15 | 2140:40 | 1092:07 | 3232:47 | 2635.6583 | 3824:40 | 28:58 | 96.7082 | 96.1055 | 2822.5437 | 513:11 | 92.7392 | 92.2244
12 | Bailhongal | 186 | 186 | 886:29 | 12184:52 | 2372:16 | 1848:46 | 4221:02 | 3575.6375 | 5107:31 | 27:28 | 96.9498 | 96.3092 | 4083.3403 | 526:53 | 93.0095 | 92.0169
13 | Ramdurg | 69 | 69 | 241:50 | 3120:05 | 1470:20 | 1423:00 | 2893:20 | 1538.0514 | 3135:10 | 45:26 | 94.3639 | 93.8928 | 1668.0549 | 580:12 | 91.8943 | 91.2092
14 | Ghataprabha | 156 | 156 | 252:10 | 4334:57 | 1680:59 | 1129:39 | 2810:38 | 1756.8861 | 3062:48 | 19:38 | 97.5784 | 97.3611 | 1937.509 | 298:05 | 95.9047 | 95.4837
15 | Raibag | 163 | 163 | 68:40 | 3528:46 | 5076:08 | 609:15 | 5685:23 | 2871.8896 | 5754:03 | 35:18 | 95.3119 | 95.2553 | 3018.9215 | 444:30 | 93.5931 | 93.2651
16 | Athani | 176 | 176 | 749:28 | 7979:47 | 4922:15 | 732:39 | 5654:54 | 2506.3028 | 6404:22 | 36:23 | 95.6814 | 95.1091 | 2838.7938 | 387:06 | 94.8217 | 94.1347
17 | Chikkodi | 176 | 176 | 65:10 | 2937:13 | 1040:36 | 617:33 | 1658:09 | 1485.5729 | 1723:19 | 9:47 | 98.7337 | 98.6839 | 1607.9568 | 219:16 | 96.9306 | 96.6778
18 | Vijayapur | 148 | 148 | 1311:49 | 7428:34 | 1418:04 | 1987:32 | 3405:36 | 2831.7653 | 4717:25 | 31:52 | 96.9071 | 95.7158 | 3141.2889 | 509:24 | 93.0423 | 92.2818
19 | Indi | 231 | 231 | 301:35 | 9359:37 | 1931:46 | 1648:12 | 3579:58 | 3214.7688 | 3881:33 | 16:48 | 97.917 | 97.7415 | 3604.7531 | 374:31 | 94.9394 | 94.3255
20 | B.Bagewadi | 120 | 120 | 222:40 | 6720:58 | 1113:04 | 951:49 | 2064:53 | 2282.7472 | 2287:33 | 19:04 | 97.6872 | 97.4378 | 2562.7875 | 512:33 | 93.0826 | 92.234
21 | Bagalkot | 168 | 168 | 210:12 | 7862:24 | 3340:02 | 1798:13 | 5138:15 | 3611.3632 | 5348:27 | 31:50 | 95.8891 | 95.721 | 3938.9632 | 562:43 | 92.1832 | 91.4741
22 | Jamkhandi | 214 | 214 | 167:29 | 8071:18 | 1865:16 | 1008:26 | 2873:42 | 2049.6472 | 3041:11 | 14:13 | 98.1951 | 98.0899 | 2385.9514 | 267:35 | 96.5172 | 95.9457
23 | Mudhol | 160 | 160 | 151:37 | 2933:11 | 1066:26 | 1146:01 | 2212:27 | 1761.8278 | 2364:04 | 14:47 | 98.1414 | 98.0141 | 1884.0438 | 282:36 | 95.9958 | 95.7181
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of January-2020 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of January-2020 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 120:30 | 1740:55 | 705:09 | 445:26 | 1150:35 | 1112.366 | 1271:05 | 28:53 | 96.4853 | 96.1172 | 1184.9042 | 646:19 | 91.7382 | 91.1995
2 | Dharwad Rural | 64 | 64 | 25:25 | 2019:29 | 1521:50 | 803:23 | 2325:13 | 2073.6667 | 2350:38 | 36:44 | 95.1167 | 95.0634 | 2157.8118 | 809:11 | 89.4114 | 88.9818
3 | Gadag | 85 | 85 | 97:00 | 1548:00 | 1080:37 | 772:56 | 1853:33 | 2073.7875 | 1950:33 | 22:57 | 97.069 | 96.9156 | 2138.2875 | 603:45 | 92.027 | 91.779
4 | Ron | 51 | 51 | 54:45 | 1713:21 | 540:00 | 269:20 | 809:20 | 1066.8833 | 864:05 | 16:57 | 97.867 | 97.7227 | 1138.2729 | 535:39 | 93.1636 | 92.7062
5 | Haveri | 192 | 192 | 1494:25 | 15516:27 | 4447:33 | 2071:10 | 6518:43 | 5691.675 | 8013:08 | 41:44 | 95.4366 | 94.3904 | 6338.1938 | 792:16 | 90.3124 | 89.212
6 | Ranebennur | 176 | 176 | 1224:52 | 7226:38 | 4165:28 | 2018:36 | 6184:04 | 4451.33 | 7408:56 | 42:06 | 95.2773 | 94.3419 | 4752.4397 | 648:04 | 91.7348 | 91.1757
7 | Sirsi | 51 | 51 | 295:55 | 3858:41 | 500:58 | 679:56 | 1180:54 | 1116.2771 | 1476:49 | 28:57 | 96.8878 | 96.1079 | 1277.0556 | 600:58 | 92.8471 | 91.8169
8 | Dandeli | 19 | 19 | 42:20 | 395:16 | 261:20 | 233:52 | 495:12 | 8397:07 | 537:32 | 28:17 | 96.4969 | 96.1974 | 8792:23 | 462:45 | 93.9821 | 93.6988
9 | Karwar | 33 | 33 | 133:32 | 5537:06 | 391:30 | 134:29 | 525:59 | 12011:10 | 659:31 | 19:59 | 97.8577 | 97.3138 | 17548:16 | 531:46 | 95.0439 | 92.7592
10 | Honnavar | 37 | 37 | 226:48 | 6967:58 | 330:05 | 376:29 | 706:34 | 13266:48 | 933:22 | 25:14 | 97.4333 | 96.6094 | 20234:46 | 546:53 | 95.1176 | 92.5533
11 | Belagavi | 132 | 132 | 254:53 | 4740:08 | 1987:20 | 1060:24 | 3047:44 | 2762.6472 | 3302:37 | 25:01 | 96.8967 | 96.6371 | 2960.1528 | 538:13 | 93.1604 | 92.6714
12 | Bailhongal | 187 | 187 | 465:06 | 12649:58 | 1973:22 | 1332:03 | 3305:25 | 3713.3632 | 3770:31 | 20:10 | 97.6242 | 97.2899 | 4240.4451 | 544:14 | 93.5106 | 92.5895
13 | Ramdurg | 69 | 69 | 56:00 | 3176:05 | 1042:14 | 784:45 | 1826:59 | 1614.1757 | 1882:59 | 27:17 | 96.4411 | 96.332 | 1746.5125 | 607:29 | 92.355 | 91.7282
14 | Ghataprabha | 156 | 156 | 200:57 | 4535:54 | 1905:58 | 596:52 | 2502:50 | 1861.1708 | 2703:47 | 17:20 | 97.8436 | 97.6704 | 2050.1667 | 315:25 | 96.1011 | 95.7052
15 | Raibag | 164 | 164 | 289:25 | 3818:11 | 4399:03 | 383:35 | 4782:38 | 3071.166 | 5072:03 | 30:56 | 96.0803 | 95.8431 | 3230.2569 | 472:43 | 93.8802 | 93.5632
16 | Athani | 179 | 179 | 428:10 | 8407:57 | 4261:26 | 1256:00 | 5517:26 | 2736.1958 | 5945:36 | 33:13 | 95.857 | 95.5355 | 3086.5271 | 413:50 | 95.0046 | 94.365
17 | Chikkodi | 176 | 176 | 221:55 | 3159:08 | 953:23 | 484:52 | 1438:15 | 1545.5 | 1660:10 | 9:26 | 98.9016 | 98.7322 | 1677.1304 | 228:42 | 97.1303 | 96.8859
18 | Vijayapur | 149 | 149 | 223:33 | 7652:07 | 1078:59 | 876:00 | 1954:59 | 2913.2229 | 2178:32 | 14:37 | 98.2365 | 98.0348 | 3232.0611 | 520:36 | 93.6105 | 92.9112
19 | Indi | 231 | 231 | 431:01 | 9790:38 | 1708:39 | 1536:21 | 3245:00 | 3349.9771 | 3676:01 | 15:55 | 98.1119 | 97.8611 | 3757.9204 | 390:26 | 95.2608 | 94.6836
20 | B.Bagewadi | 120 | 120 | 413:35 | 7134:33 | 1434:27 | 833:47 | 2268:14 | 2377.2569 | 2681:49 | 22:21 | 97.4594 | 96.9962 | 2674.5299 | 534:54 | 93.526 | 92.7164
21 | Bagalkot | 169 | 169 | 424:01 | 8286:25 | 3138:50 | 1181:15 | 4320:05 | 3791.3667 | 4744:06 | 28:04 | 96.5642 | 96.2269 | 4136.634 | 587:27 | 92.6686 | 92.0009
22 | Jamkhandi | 214 | 214 | 441:04 | 8512:22 | 1590:31 | 703:16 | 2293:47 | 2145.2215 | 2734:51 | 12:47 | 98.5593 | 98.2823 | 2499.9035 | 280:22 | 96.7241 | 96.1824
23 | Mudhol | 160 | 160 | 216:12 | 3149:23 | 1021:38 | 425:37 | 1447:15 | 1822.1299 | 1663:27 | 10:24 | 98.7842 | 98.6026 | 1953.3542 | 293:00 | 96.2783 | 96.0103
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of February-2020 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of February-2020 |  |  |  | Reliability for cumulative period from Apr-19
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 48:45 | 1789:40 | 773:31 | 396:26 | 1169:57 | 1161.1139 | 1218:42 | 27:42 | 96.1796 | 96.0204 | 1235.6833 | 674:01 | 92.1227 | 91.6168
2 | Dharwad Rural | 64 | 64 | 220:22 | 2239:51 | 1261:24 | 682:24 | 1943:48 | 2154.6583 | 2164:10 | 33:49 | 95.6362 | 95.1415 | 2247.9854 | 843:00 | 89.9503 | 89.515
3 | Gadag | 85 | 85 | 70:40 | 1618:40 | 1102:24 | 827:27 | 1929:51 | 2154.1979 | 2000:31 | 23:32 | 96.7379 | 96.6185 | 2221.6424 | 627:17 | 92.4348 | 92.1979
4 | Ron | 52 | 52 | 259:30 | 1972:51 | 447:35 | 359:15 | 806:50 | 1100.5014 | 1066:20 | 20:30 | 97.7707 | 97.0537 | 1182.7035 | 545:52 | 93.6825 | 93.2107
5 | Haveri | 192 | 192 | 1622:30 | 17138:57 | 3165:03 | 1978:10 | 5143:13 | 5905.9757 | 6765:43 | 35:14 | 96.1512 | 94.9371 | 6620.0986 | 827:31 | 90.8178 | 89.7076
6 | Ranebennur | 176 | 176 | 699:27 | 7926:05 | 3868:50 | 1534:19 | 5403:09 | 4676.4612 | 6102:36 | 34:40 | 95.5891 | 95.0181 | 5006.7147 | 682:44 | 92.0684 | 91.5083
7 | Sirsi | 51 | 51 | 394:04 | 4252:45 | 712:34 | 677:22 | 1389:56 | 1174.191 | 1784:00 | 34:59 | 96.0843 | 94.9741 | 1351.3889 | 635:57 | 93.1274 | 92.0902
8 | Dandeli | 19 | 19 | 0:08 | 395:24 | 324:32 | 320:24 | 644:56 | 9042:03 | 645:04 | 33:57 | 95.123 | 95.122 | 9437:27 | 496:42 | 94.0809 | 93.822
9 | Karwar | 33 | 33 | 450:19 | 5987:25 | 319:22 | 175:30 | 494:52 | 12506:02 | 945:11 | 28:39 | 97.8454 | 95.8848 | 18493:27 | 560:24 | 95.2864 | 93.0298
10 | Honnavar | 37 | 37 | 277:14 | 7245:12 | 387:19 | 147:09 | 534:28 | 13801:16 | 811:42 | 21:56 | 97.9246 | 96.848 | 21046:28 | 568:49 | 95.3606 | 92.9251
11 | Belagavi | 132 | 132 | 278:27 | 5018:35 | 2967:17 | 1170:27 | 4137:44 | 2935.0528 | 4416:11 | 33:27 | 95.4962 | 95.1931 | 3144.1604 | 571:40 | 93.3626 | 92.8897
12 | Bailhongal | 188 | 188 | 1161:53 | 13811:51 | 3058:22 | 1400:50 | 4459:12 | 3899.1632 | 5621:05 | 29:54 | 96.5921 | 95.7041 | 4474.6569 | 571:14 | 93.8089 | 92.8951
13 | Ramdurg | 69 | 69 | 288:00 | 3464:05 | 853:30 | 500:45 | 1354:15 | 1670.6028 | 1642:15 | 23:48 | 97.1801 | 96.5804 | 1814.9396 | 631:17 | 92.7726 | 92.1482
14 | Ghataprabha | 157 | 157 | 128:15 | 4664:09 | 1061:31 | 727:35 | 1789:06 | 1935.7167 | 1917:21 | 12:13 | 98.3627 | 98.2453 | 2130.0563 | 325:37 | 96.3196 | 95.9501
15 | Raibag | 164 | 164 | 659:33 | 4477:44 | 3754:25 | 425:53 | 4180:18 | 3245.3451 | 4839:51 | 29:31 | 96.3377 | 95.7599 | 3431.9174 | 502:14 | 94.0929 | 93.7533
16 | Athani | 180 | 180 | 537:55 | 8945:52 | 3587:13 | 455:24 | 4042:37 | 2904.6382 | 4580:32 | 25:27 | 96.7731 | 96.3438 | 3277.3826 | 436:59 | 95.183 | 94.5649
17 | Chikkodi | 179 | 179 | 227:52 | 1284:43 | 1284:43 | 665:40 | 1950:23 | 1626.766 | 2178:15 | 12:10 | 98.4345 | 98.2516 | 1767.8909 | 237:02 | 97.2871 | 97.0518
18 | Vijayapur | 149 | 149 | 181:06 | 7833:13 | 938:25 | 714:52 | 1653:17 | 2982.1097 | 1834:23 | 12:19 | 98.4058 | 98.2311 | 3308.4938 | 532:55 | 94.0256 | 93.3717
19 | Indi | 231 | 231 | 469:45 | 10260:23 | 1817:09 | 880:33 | 2697:42 | 3462.3813 | 3167:27 | 13:43 | 98.3221 | 98.0299 | 3889.8975 | 404:09 | 95.5258 | 94.9733
20 | B.Bagewadi | 121 | 121 | 339:41 | 7474:14 | 1060:07 | 596:25 | 1656:32 | 2446.2792 | 1996:13 | 16:30 | 98.033 | 97.6296 | 2757.7056 | 546:59 | 93.965 | 93.1967
21 | Bagalkot | 172 | 172 | 461:41 | 8748:06 | 2650:54 | 1009:54 | 3660:48 | 3943.9 | 4122:29 | 23:58 | 96.942 | 96.5563 | 4308.4042 | 601:10 | 93.1553 | 92.5227
22 | Jamkhandi | 217 | 217 | 287:11 | 8799:33 | 1821:21 | 570:42 | 2392:03 | 2244.8903 | 2679:14 | 12:21 | 98.4162 | 98.226 | 2611.5382 | 288:50 | 96.9119 | 96.4075
23 | Mudhol | 160 | 160 | 168:54 | 3318:17 | 1150:41 | 574:48 | 1725:29 | 1894.025 | 1894:23 | 11:50 | 98.4505 | 98.2989 | 2032.2868 | 304:51 | 96.4664 | 96.2084
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of March-2020 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 19-20 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of March-2020 |  |  |  | Reliability for cumulative period from Apr-19 to Mar-20
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 19-20 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 44 | 44 | 54:15 | 1843:55 | 559:24 | 564:47 | 1124:11 | 1207.9549 | 1178:26 | 26:47 | 96.5659 | 96.4002 | 1284.7847 | 700:48 | 92.499 | 92.022
2 | Dharwad Rural | 64 | 64 | 126:42 | 2366:33 | 1436:27 | 1135:22 | 2571:49 | 2261.8174 | 2698:31 | 42:10 | 94.5988 | 94.3328 | 2360.4236 | 885:10 | 90.344 | 89.9231
3 | Gadag | 85 | 85 | 266:05 | 1884:45 | 1124:35 | 922:04 | 2046:39 | 2239.475 | 2312:44 | 27:13 | 96.7637 | 96.3429 | 2318.0063 | 654:30 | 92.8014 | 92.549
4 | Ron | 53 | 53 | 217:10 | 2190:01 | 400:45 | 617:55 | 1018:40 | 1142.9458 | 1235:50 | 23:19 | 97.4166 | 96.8659 | 1234.1965 | 558:53 | 94.1079 | 93.6375
5 | Haveri | 192 | 192 | 894:52 | 18033:49 | 2569:29 | 1534:45 | 4104:14 | 6076.9854 | 4999:06 | 26:02 | 97.1269 | 96.5004 | 6828.3944 | 853:33 | 91.3522 | 90.2829
6 | Ranebennur | 177 | 177 | 816:45 | 8742:50 | 3342:13 | 1741:37 | 5083:50 | 4888.2876 | 5900:35 | 33:20 | 96.1395 | 95.5193 | 5252.5723 | 712:13 | 92.4543 | 91.8919
7 | Sirsi | 51 | 51 | 150:14 | 4402:59 | 647:09 | 862:22 | 1509:31 | 1237.0875 | 1659:45 | 32:33 | 96.0217 | 95.6258 | 1420.5451 | 668:30 | 93.3725 | 92.3897
8 | Dandeli | 19 | 19 | 44:34 | 439:58 | 398:54 | 425:54 | 824:48 | 9866:51 | 869:22 | 45:45 | 94.1653 | 93.85 | 10306:49 | 542:28 | 94.088 | 93.8244
9 | Karwar | 33 | 33 | 166:41 | 6154:06 | 395:42 | 307:26 | 703:08 | 13209:10 | 869:49 | 26:21 | 97.1361 | 96.4572 | 19363:16 | 586:46 | 95.4431 | 93.3201
10 | Honnavar | 37 | 37 | 116:01 | 7361:13 | 363:16 | 219:32 | 582:48 | 14384:04 | 698:49 | 18:53 | 97.8829 | 97.4614 | 21745:17 | 587:43 | 95.5742 | 93.3093
11 | Belagavi | 131 | 131 | 302:20 | 5320:55 | 3063:34 | 1588:06 | 4651:40 | 3128.8722 | 4954:00 | 37:49 | 95.2273 | 94.9171 | 3350.5771 | 613:51 | 93.4742 | 93.0118
12 | Bailhongal | 189 | 189 | 644:55 | 14456:46 | 3298:08 | 2599:00 | 5897:08 | 4144.8771 | 6542:03 | 34:37 | 95.8062 | 95.3476 | 4747.2424 | 602:49 | 94.008 | 93.1372
13 | Ramdurg | 69 | 69 | 266:10 | 3730:15 | 1201:05 | 961:15 | 2162:20 | 1760.7 | 2428:30 | 35:12 | 95.7879 | 95.2694 | 1916.1271 | 666:29 | 93.028 | 92.4126
14 | Ghataprabha | 157 | 157 | 126:41 | 4790:50 | 1440:32 | 1001:12 | 2441:44 | 2037.4556 | 2568:25 | 16:22 | 97.9096 | 97.8012 | 2237.0736 | 341:58 | 96.4543 | 96.1069
15 | Raibag | 164 | 164 | 473:39 | 4951:23 | 3896:24 | 762:12 | 4658:36 | 3439.4535 | 5132:15 | 31:18 | 96.182 | 95.7938 | 3645.7611 | 533:32 | 94.2699 | 93.9262
16 | Athani | 180 | 180 | 1066:44 | 10012:36 | 2435:52 | 760:35 | 3196:27 | 3037.8236 | 4263:11 | 23:41 | 97.6132 | 96.8166 | 3455.0153 | 460:40 | 95.3889 | 94.7556
17 | Chikkodi | 179 | 179 | 249:31 | 1534:14 | 1344:13 | 845:15 | 2189:28 | 1717.9938 | 2438:59 | 13:38 | 98.356 | 98.1686 | 1869.5152 | 250:40 | 97.3777 | 97.1464
18 | Vijayapur | 149 | 149 | 205:13 | 8038:26 | 1028:39 | 1439:02 | 2467:41 | 3084.9299 | 2672:54 | 17:56 | 97.774 | 97.5889 | 3419.8646 | 550:51 | 94.3431 | 93.7289
19 | Indi | 231 | 231 | 999:04 | 11259:27 | 2554:44 | 2321:57 | 4876:41 | 3665.5764 | 5875:45 | 25:26 | 97.1625 | 96.5812 | 4134.7204 | 429:35 | 95.6644 | 95.1095
20 | B.Bagewadi | 123 | 123 | 496:56 | 7971:10 | 1434:30 | 1127:15 | 2561:45 | 2553.0187 | 3058:41 | 24:52 | 97.2006 | 96.6576 | 2885.1507 | 562:57 | 94.3289 | 93.5911
21 | Bagalkot | 181 | 181 | 346:05 | 9094:11 | 2898:13 | 1973:12 | 4871:25 | 4146.8757 | 5217:30 | 28:50 | 96.3825 | 96.1255 | 4525.8 | 600:06 | 93.7402 | 93.1682
22 | Jamkhandi | 219 | 219 | 495:54 | 9295:27 | 2448:47 | 806:05 | 3254:52 | 2380.5097 | 3750:46 | 17:08 | 98.0024 | 97.698 | 2767.8201 | 303:19 | 97.0301 | 96.5469
23 | Mudhol | 161 | 161 | 851:21 | 4169:38 | 1077:06 | 837:14 | 1914:20 | 1973.7889 | 2765:41 | 17:11 | 98.4018 | 97.6911 | 2147.5236 | 320:08 | 96.6504 | 96.3556
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]