## DHQ
Annex-1 | [13 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of April-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Apr-22
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 38 | 38 | 34:38 | 34:38 | 542:46 | 410:41 | 953:27 | 953:27 | 988:05 | 26:00 | 96.5152 | 96.3886 | 988:05 | 26:00 | 96.5152 | 96.3886
2 | Gadag | 13 | 13 | 2:55 | 2:55 | 79:29 | 65:21 | 144:50 | 144:50 | 147:45 | 11:22 | 98.4526 | 98.4215 | 147:45 | 11:22 | 98.4526 | 98.4215
3 | Haveri | 8 | 8 | 0:00 | 0:00 | 34:33 | 38:42 | 73:15 | 73:15 | 73:15 | 9:09 | 98.7283 | 98.7283 | 73:15 | 9:09 | 98.7283 | 98.7283
4 | Karwar | 10 | 10 | 46:58 | 46:58 | 78:37 | 100:05 | 178:42 | 178:42 | 225:40 | 22:34 | 97.5181 | 96.8657 | 225:40 | 22:34 | 97.5181 | 96.8657
5 | Belagavi | 80 | 80 | 251:17 | 251:17 | 187:21 | 285:33 | 472:54 | 472:54 | 724:11 | 9:03 | 99.179 | 98.7427 | 724:11 | 9:03 | 99.179 | 98.7427
6 | Vijayapur | 39 | 39 | 142:23 | 142:23 | 254:15 | 444:22 | 698:37 | 698:37 | 841:00 | 21:34 | 97.512 | 97.005 | 841:00 | 21:34 | 97.512 | 97.005
7 | Bagalkot | 12 | 12 | 2:40 | 2:40 | 42:39 | 41:37 | 84:16 | 84:16 | 86:56 | 7:15 | 99.0247 | 98.9938 | 86:56 | 7:15 | 99.0247 | 98.9938
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of May-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2022 |  |  |  | Reliability for cumulative period from Apr-22 to May-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 40 | 40 | 58:33 | 93:11 | 621:15 | 332:28 | 953:43 | 1907:10 | 1012:16 | 25:18 | 96.7953 | 96.5986 | 2000:21 | 50:01 | 96.7432 | 96.5841
2 | Gadag | 13 | 13 | 17:15 | 20:10 | 68:12 | 69:04 | 137:16 | 282:06 | 154:31 | 11:53 | 98.5808 | 98.4024 | 302:16 | 23:15 | 98.5178 | 98.4118
3 | Haveri | 8 | 8 | 8:50 | 8:50 | 105:05 | 46:00 | 151:05 | 224:20 | 159:55 | 19:59 | 97.4616 | 97.3132 | 233:10 | 29:09 | 98.0846 | 98.0092
4 | Karwar | 10 | 10 | 7:52 | 54:50 | 81:58 | 92:36 | 174:34 | 353:16 | 182:26 | 18:15 | 97.6537 | 97.5479 | 408:06 | 40:49 | 97.587 | 97.2124
5 | Belagavi | 80 | 80 | 274:38 | 525:55 | 238:23 | 329:56 | 568:19 | 1041:13 | 842:57 | 10:32 | 99.0452 | 98.5838 | 1567:08 | 19:35 | 99.111 | 98.6619
6 | Vijayapur | 38 | 38 | 222:58 | 365:21 | 174:31 | 508:39 | 683:10 | 1381:47 | 906:08 | 23:51 | 97.5836 | 96.7949 | 1747:08 | 45:59 | 97.5162 | 96.8595
7 | Bagalkot | 12 | 12 | 51:16 | 53:56 | 72:11 | 118:13 | 190:24 | 274:40 | 241:40 | 20:08 | 97.8674 | 97.2932 | 328:36 | 27:23 | 98.4366 | 98.1296
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of June-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2022 |  |  |  | Reliability for cumulative period from Apr-22 to June-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 41 | 41 | 14:40 | 107:51 | 638:51 | 163:23 | 802:14 | 2709:24 | 816:54 | 19:55 | 97.2824 | 97.2327 | 2817:15 | 68:43 | 96.9742 | 96.8538
2 | Gadag | 13 | 13 | 10:00 | 30:10 | 106:34 | 38:46 | 145:20 | 427:26 | 155:20 | 11:57 | 98.4473 | 98.3405 | 457:36 | 35:12 | 98.4945 | 98.3883
3 | Haveri | 8 | 8 | 3:20 | 12:10 | 45:45 | 18:45 | 64:30 | 288:50 | 67:50 | 8:29 | 98.8802 | 98.8223 | 301:00 | 37:38 | 98.3469 | 98.2772
4 | Karwar | 10 | 10 | 8:50 | 63:40 | 82:07 | 118:58 | 201:05 | 554:21 | 209:55 | 21:00 | 97.2072 | 97.0845 | 618:01 | 61:48 | 97.4618 | 97.1703
5 | Belagavi | 80 | 80 | 229:55 | 755:50 | 221:06 | 182:56 | 404:02 | 1445:15 | 633:57 | 7:55 | 99.2986 | 98.8994 | 2201:05 | 27:31 | 99.1728 | 98.7402
6 | Vijayapur | 40 | 40 | 122:02 | 487:23 | 359:27 | 195:55 | 555:22 | 1937:09 | 677:24 | 16:56 | 98.0716 | 97.6479 | 2424:32 | 60:37 | 97.7826 | 97.2247
7 | Bagalkot | 12 | 12 | 96:00 | 149:56 | 79:24 | 85:31 | 164:55 | 439:35 | 260:55 | 21:45 | 98.0912 | 96.9801 | 589:31 | 49:08 | 98.3227 | 97.7506
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of July-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2022 |  |  |  | Reliability for cumulative period from Apr-22 to July-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 41 | 41 | 40:59 | 148:50 | 575:19 | 223:50 | 799:09 | 3508:33 | 840:08 | 20:29 | 97.3802 | 97.2458 | 3657:23 | 89:12 | 97.0774 | 96.9534
2 | Gadag | 13 | 13 | 15:00 | 45:10 | 68:33 | 59:37 | 128:10 | 555:36 | 143:10 | 11:01 | 98.6749 | 98.5198 | 600:46 | 46:13 | 98.5404 | 98.4217
3 | Haveri | 8 | 8 | 0:00 | 12:10 | 32:35 | 26:10 | 58:45 | 347:35 | 58:45 | 7:21 | 99.0129 | 99.0129 | 359:45 | 44:58 | 98.5161 | 98.4642
4 | Karwar | 10 | 10 | 63:36 | 127:16 | 172:37 | 139:18 | 311:55 | 866:16 | 375:31 | 37:33 | 95.8076 | 94.9527 | 993:32 | 99:21 | 97.0414 | 96.6068
5 | Belagavi | 79 | 79 | 186:15 | 942:05 | 195:02 | 185:42 | 380:44 | 1825:59 | 566:59 | 7:11 | 99.3522 | 99.0353 | 2768:04 | 35:02 | 99.2106 | 98.8033
6 | Vijayapur | 41 | 41 | 83:39 | 571:02 | 252:03 | 388:30 | 640:33 | 2577:42 | 724:12 | 17:40 | 97.9001 | 97.6259 | 3148:44 | 76:48 | 97.8528 | 97.3771
7 | Bagalkot | 13 | 13 | 19:04 | 169:00 | 63:31 | 61:19 | 124:50 | 564:25 | 143:54 | 11:04 | 98.7093 | 98.5122 | 733:25 | 56:25 | 98.5172 | 98.0732
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of Aug-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Aug-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Aug-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 41 | 41 | 91:19 | 240:09 | 634:09 | 257:25 | 891:34 | 4400:07 | 982:53 | 23:58 | 97.0772 | 96.7779 | 4640:16 | 113:11 | 97.0773 | 96.9178
2 | Gadag | 13 | 13 | 0:20 | 45:30 | 41:04 | 55:08 | 96:12 | 651:48 | 96:32 | 7:26 | 99.0054 | 99.0019 | 697:18 | 53:38 | 98.6346 | 98.5393
3 | Haveri | 8 | 8 | 66:40 | 78:50 | 18:47 | 43:41 | 62:28 | 410:03 | 129:08 | 16:09 | 98.9505 | 97.8304 | 488:53 | 61:07 | 98.6041 | 98.3358
4 | Karwar | 10 | 10 | 2:22 | 129:38 | 73:13 | 96:24 | 169:37 | 1035:53 | 171:59 | 17:12 | 97.7202 | 97.6884 | 1165:31 | 116:33 | 97.179 | 96.8259
5 | Belagavi | 79 | 79 | 340:38 | 1282:43 | 289:01 | 207:38 | 496:39 | 2322:38 | 837:17 | 10:36 | 99.155 | 98.5755 | 3605:21 | 45:38 | 99.1993 | 98.7572
6 | Vijayapur | 42 | 42 | 142:55 | 713:57 | 194:59 | 414:48 | 609:47 | 3187:29 | 752:42 | 17:55 | 98.0486 | 97.5912 | 3901:26 | 92:53 | 97.9332 | 97.4703
7 | Bagalkot | 13 | 13 | 17:00 | 186:00 | 69:49 | 61:25 | 131:14 | 695:39 | 148:14 | 11:24 | 98.6432 | 98.4674 | 881:39 | 67:49 | 98.5427 | 98.1531
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of Sept-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Sept-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Sept-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 41 | 41 | 24:12 | 264:21 | 733:54 | 154:50 | 888:44 | 5288:51 | 912:56 | 22:16 | 96.9894 | 96.9074 | 5553:12 | 135:27 | 97.0629 | 96.9161
2 | Gadag | 13 | 13 | 52:50 | 98:20 | 150:41 | 44:21 | 195:02 | 846:50 | 247:52 | 19:04 | 97.9163 | 97.3519 | 945:10 | 72:42 | 98.5168 | 98.3446
3 | Haveri | 8 | 8 | 2:40 | 81:30 | 14:19 | 27:25 | 41:44 | 451:47 | 44:24 | 5:33 | 99.2755 | 99.2292 | 533:17 | 66:40 | 98.7142 | 98.4822
4 | Karwar | 10 | 10 | 18:56 | 148:34 | 46:30 | 67:25 | 113:55 | 1149:48 | 132:51 | 13:17 | 98.4178 | 98.1549 | 1298:22 | 129:50 | 97.3821 | 97.0438
5 | Belagavi | 79 | 79 | 129:48 | 1412:31 | 295:18 | 196:52 | 492:10 | 2814:48 | 621:58 | 7:52 | 99.1347 | 98.9065 | 4227:19 | 53:31 | 99.1887 | 98.7816
6 | Vijayapur | 42 | 42 | 329:32 | 1043:29 | 234:35 | 384:38 | 619:13 | 3806:42 | 948:45 | 22:35 | 97.9523 | 96.8626 | 4850:11 | 115:29 | 97.9363 | 97.3707
7 | Bagalkot | 13 | 13 | 98:00 | 284:00 | 89:01 | 35:59 | 125:00 | 820:39 | 223:00 | 17:09 | 98.6645 | 97.6175 | 1104:39 | 84:58 | 98.5627 | 98.0653
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of Oct-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Oct-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Oct-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 41 | 41 | 18:07 | 282:28 | 593:19 | 143:04 | 736:23 | 6025:14 | 754:30 | 18:24 | 97.5859 | 97.5266 | 6307:42 | 153:51 | 97.1387 | 97.0045
2 | Gadag | 13 | 13 | 4:20 | 102:40 | 68:31 | 29:13 | 97:44 | 944:34 | 102:04 | 7:51 | 98.9895 | 98.9447 | 1047:14 | 80:33 | 98.5853 | 98.4315
3 | Haveri | 8 | 8 | 0:00 | 81:30 | 42:39 | 40:11 | 82:50 | 534:37 | 82:50 | 10:21 | 98.6083 | 98.6083 | 616:07 | 77:01 | 98.6988 | 98.5005
4 | Karwar | 10 | 10 | 10:04 | 158:38 | 45:31 | 37:21 | 82:52 | 1232:40 | 92:56 | 9:18 | 98.8862 | 98.7509 | 1391:18 | 139:08 | 97.5999 | 97.2911
5 | Belagavi | 79 | 79 | 150:25 | 1562:56 | 197:29 | 206:46 | 404:15 | 3219:03 | 554:40 | 7:01 | 99.3122 | 99.0563 | 4781:59 | 60:32 | 99.2066 | 98.8214
6 | Vijayapur | 42 | 42 | 247:08 | 1290:37 | 216:24 | 293:31 | 509:55 | 4316:37 | 757:03 | 18:02 | 98.3682 | 97.5773 | 5607:14 | 133:30 | 97.9989 | 97.4006
7 | Bagalkot | 13 | 13 | 2:35 | 286:35 | 56:26 | 54:48 | 111:14 | 931:53 | 113:49 | 8:45 | 98.8499 | 98.8232 | 1218:28 | 93:44 | 98.6043 | 98.1751
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of Nov-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Nov-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Nov-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 42 | 42 | 106:58 | 389:26 | 632:50 | 86:59 | 719:49 | 6745:03 | 826:47 | 19:41 | 97.6197 | 97.2659 | 7134:29 | 169:52 | 97.2576 | 97.0992
2 | Gadag | 13 | 13 | 4:20 | 107:00 | 60:58 | 14:23 | 75:21 | 1019:55 | 79:41 | 6:08 | 99.195 | 99.1487 | 1126:55 | 86:41 | 98.6603 | 98.5197
3 | Haveri | 8 | 8 | 0:00 | 81:30 | 84:27 | 50:10 | 134:37 | 669:14 | 134:37 | 16:50 | 97.6629 | 97.6629 | 750:44 | 93:51 | 98.5715 | 98.3975
4 | Karwar | 10 | 10 | 14:40 | 173:18 | 48:54 | 43:41 | 92:35 | 1325:15 | 107:15 | 10:44 | 98.7141 | 98.5104 | 1498:33 | 149:51 | 97.7369 | 97.441
5 | Belagavi | 79 | 79 | 277:38 | 1840:34 | 383:19 | 133:27 | 516:46 | 3735:49 | 794:24 | 10:03 | 99.0915 | 98.6034 | 5576:23 | 70:35 | 99.1925 | 98.7946
6 | Vijayapur | 41 | 41 | 276:51 | 1567:28 | 195:50 | 223:13 | 419:03 | 4735:40 | 695:54 | 16:58 | 98.5805 | 97.6426 | 6303:08 | 153:44 | 98.0276 | 97.3747
7 | Bagalkot | 13 | 13 | 1:08 | 287:43 | 61:30 | 14:30 | 76:00 | 1007:53 | 77:08 | 5:56 | 99.188 | 99.1759 | 1295:36 | 99:40 | 98.6761 | 98.2981
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of DEC-2022
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Dec-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Dec-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 43 | 43 | 140:53 | 530:19 | 930:05 | 105:54 | 1035:59 | 7781:02 | 1176:52 | 27:22 | 96.7617 | 96.3214 | 8311:21 | 193:17 | 97.2583 | 97.0714
2 | Gadag | 12 | 12 | 57:32 | 164:32 | 51:08 | 15:55 | 67:03 | 1086:58 | 124:35 | 10:23 | 99.249 | 98.6046 | 1251:30 | 104:18 | 98.6276 | 98.4198
3 | Haveri | 8 | 8 | 0:00 | 81:30 | 117:01 | 15:05 | 132:06 | 801:20 | 132:06 | 16:31 | 97.7806 | 97.7806 | 882:50 | 110:21 | 98.4823 | 98.328
4 | Karwar | 10 | 10 | 132:50 | 306:08 | 27:49 | 46:37 | 74:26 | 1399:41 | 207:16 | 20:44 | 98.9996 | 97.2142 | 1705:49 | 170:35 | 97.8793 | 97.4154
5 | Belagavi | 79 | 79 | 157:41 | 1998:15 | 639:32 | 73:35 | 713:07 | 4448:56 | 870:48 | 11:01 | 98.7867 | 98.5184 | 6447:11 | 81:37 | 99.1467 | 98.7635
6 | Vijayapur | 41 | 41 | 190:19 | 1757:47 | 226:21 | 332:03 | 558:24 | 5294:04 | 748:43 | 18:16 | 98.1694 | 97.5455 | 7051:51 | 172:00 | 98.0436 | 97.394
7 | Bagalkot | 13 | 13 | 90:26 | 378:09 | 51:36 | 35:02 | 86:38 | 1094:31 | 177:04 | 13:37 | 99.1043 | 98.1693 | 1472:40 | 113:17 | 98.7243 | 98.2836
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of JAN-2023
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Jan-2023 |  |  |  | Reliability for cumulative period from Apr-22 to Jan-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Dharwad | 43 | 43 | 5:51 | 536:10 | 515:04 | 44:51 | 559:55 | 8340:57 | 565:46 | 13:09 | 98.2498 | 98.2315 | 8877:07 | 206:27 | 97.3587 | 97.1889
2 | Gadag | 12 | 12 | 1:00 | 165:32 | 27:04 | 8:53 | 35:57 | 1122:55 | 36:57 | 3:05 | 99.5973 | 99.5861 | 1288:27 | 107:22 | 98.7258 | 98.538
3 | Haveri | 8 | 8 | 0:00 | 81:30 | 43:43 | 11:00 | 54:43 | 856:03 | 54:43 | 6:50 | 99.0807 | 99.0807 | 937:33 | 117:12 | 98.5429 | 98.4042
4 | Karwar | 10 | 10 | 267:58 | 574:06 | 16:29 | 38:26 | 54:55 | 1454:36 | 322:53 | 32:17 | 99.2619 | 95.6602 | 2028:42 | 202:52 | 98.0193 | 97.2376
5 | Belagavi | 79 | 79 | 91:31 | 2089:46 | 383:45 | 67:29 | 451:14 | 4900:10 | 542:45 | 6:52 | 99.2323 | 99.0766 | 6989:56 | 88:29 | 99.1554 | 98.7952
6 | Vijayapur | 41 | 41 | 101:02 | 1858:49 | 170:47 | 167:26 | 338:13 | 5632:17 | 439:15 | 10:43 | 98.8912 | 98.56 | 7491:06 | 182:43 | 98.1295 | 97.5121
7 | Bagalkot | 13 | 13 | 0:15 | 378:24 | 49:08 | 11:50 | 60:58 | 1155:29 | 61:13 | 4:43 | 99.3697 | 99.3671 | 1533:53 | 117:59 | 98.7897 | 98.3934
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]

## URBAN
Annex-II | [13 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of April-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Apr-22
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 80 | 80 | 61:25 | 61:25 | 540:15 | 407:09 | 947:24 | 947:24 | 1008:49 | 12:37 | 98.3552 | 98.2486 | 1008:49 | 12:37 | 98.3552 | 98.2486
2 | Dharwad(R) | 14 | 14 | 1:40 | 1:40 | 151:26 | 242:33 | 393:59 | 393:59 | 395:39 | 28:16 | 96.0914 | 96.0749 | 395:39 | 28:16 | 96.0914 | 96.0749
3 | Kundagol | 1 | 1 | 37:05 | 37:05 | 6:30 | 5:05 | 11:35 | 11:35 | 48:40 | 48:40 | 98.3912 | 93.2407 | 48:40 | 48:40 | 98.3912 | 93.2407
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 8:23 | 22:13 | 30:36 | 30:36 | 30:36 | 30:36 | 95.75 | 95.75 | 30:36 | 30:36 | 95.75 | 95.75
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 12:37 | 43:23 | 56:00 | 56:00 | 56:00 | 56:00 | 92.2222 | 92.2222 | 56:00 | 56:00 | 92.2222 | 92.2222
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 17:50 | 44:20 | 62:10 | 62:10 | 62:10 | 31:05 | 95.6829 | 95.6829 | 62:10 | 31:05 | 95.6829 | 95.6829
7 | Alnavar | 2 | 2 | 0:00 | 0:00 | 14:45 | 9:15 | 24:00 | 24:00 | 24:00 | 12:00 | 98.3333 | 98.3333 | 24:00 | 12:00 | 98.3333 | 98.3333
8 | Naragund | 2 | 2 | 19:10 | 19:10 | 22:15 | 29:20 | 51:35 | 51:35 | 70:45 | 35:22 | 96.4178 | 95.0868 | 70:45 | 35:22 | 96.4178 | 95.0868
9 | Shirahatti | 1 | 1 | 0:00 | 0:00 | 6:15 | 16:40 | 22:55 | 22:55 | 22:55 | 22:55 | 96.8171 | 96.8171 | 22:55 | 22:55 | 96.8171 | 96.8171
10 | Laxmeshwar | 3 | 3 | 0:00 | 0:00 | 44:35 | 66:15 | 110:50 | 110:50 | 110:50 | 36:57 | 94.8688 | 94.8688 | 110:50 | 36:57 | 94.8688 | 94.8688
11 | Naregal | 1 | 1 | 1:10 | 1:10 | 4:55 | 6:35 | 11:30 | 11:30 | 12:40 | 12:40 | 98.4028 | 98.2407 | 12:40 | 12:40 | 98.4028 | 98.2407
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 27:30 | 22:40 | 50:10 | 50:10 | 50:10 | 25:05 | 96.5162 | 96.5162 | 50:10 | 25:05 | 96.5162 | 96.5162
13 | Ron | 3 | 3 | 0:00 | 0:00 | 54:40 | 44:42 | 99:22 | 99:22 | 99:22 | 33:07 | 95.3997 | 95.3997 | 99:22 | 33:07 | 95.3997 | 95.3997
14 | Mundaragi | 1 | 1 | 0:00 | 0:00 | 4:25 | 10:05 | 14:30 | 14:30 | 14:30 | 14:30 | 97.9861 | 97.9861 | 14:30 | 14:30 | 97.9861 | 97.9861
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 15:43 | 83:24 | 99:07 | 99:07 | 99:07 | 99:07 | 86.2338 | 86.2338 | 99:07 | 99:07 | 86.2338 | 86.2338
16 | Savanur | 2 | 2 | 0:00 | 0:00 | 22:15 | 8:00 | 30:15 | 30:15 | 30:15 | 15:08 | 97.8993 | 97.8993 | 30:15 | 15:08 | 97.8993 | 97.8993
17 | Shiggaon | 3 | 3 | 49:55 | 49:55 | 18:25 | 37:20 | 55:45 | 55:45 | 105:40 | 35:13 | 97.419 | 95.108 | 105:40 | 35:13 | 97.419 | 95.108
18 | Bankapur | 1 | 1 | 10:05 | 10:05 | 18:00 | 12:10 | 30:10 | 30:10 | 40:15 | 40:15 | 95.8102 | 94.4097 | 40:15 | 40:15 | 95.8102 | 94.4097
19 | Hangal | 2 | 2 | 2:26 | 2:26 | 4:30 | 19:00 | 23:30 | 23:30 | 25:56 | 12:58 | 98.3681 | 98.1991 | 25:56 | 12:58 | 98.3681 | 98.1991
20 | Ranebennur | 10 | 10 | 34:01 | 34:01 | 46:25 | 71:01 | 117:26 | 117:26 | 151:27 | 15:09 | 98.369 | 97.8965 | 151:27 | 15:09 | 98.369 | 97.8965
21 | Tuminakatti | 1 | 1 | 3:05 | 3:05 | 21:00 | 3:25 | 24:25 | 24:25 | 27:30 | 27:30 | 96.6088 | 96.1806 | 27:30 | 27:30 | 96.6088 | 96.1806
22 | Rattihalli | 1 | 1 | 6:25 | 6:25 | 4:25 | 12:55 | 17:20 | 17:20 | 23:45 | 23:45 | 97.5926 | 96.7014 | 23:45 | 23:45 | 97.5926 | 96.7014
23 | Hirekerur | 1 | 1 | 4:15 | 4:15 | 8:05 | 18:40 | 26:45 | 26:45 | 31:00 | 31:00 | 96.2847 | 95.6944 | 31:00 | 31:00 | 96.2847 | 95.6944
24 | Byadagi | 5 | 5 | 46:55 | 46:55 | 57:25 | 31:25 | 88:50 | 88:50 | 135:45 | 27:09 | 97.5324 | 96.2292 | 135:45 | 27:09 | 97.5324 | 96.2292
25 | Sirsi | 6 | 6 | 49:11 | 49:11 | 49:10 | 34:20 | 83:30 | 83:30 | 132:41 | 22:07 | 98.0671 | 96.9286 | 132:41 | 22:07 | 98.0671 | 96.9286
26 | Yellapur | 1 | 1 | 16:00 | 16:00 | 3:55 | 4:55 | 8:50 | 8:50 | 24:50 | 24:50 | 98.7731 | 96.5509 | 24:50 | 24:50 | 98.7731 | 96.5509
27 | Mundagod | 1 | 1 | 0:00 | 0:00 | 2:40 | 10:10 | 12:50 | 12:50 | 12:50 | 12:50 | 98.2176 | 98.2176 | 12:50 | 12:50 | 98.2176 | 98.2176
28 | Siddapur | 1 | 1 | 10:40 | 10:40 | 8:35 | 7:15 | 15:50 | 15:50 | 26:30 | 26:30 | 97.8009 | 96.3194 | 26:30 | 26:30 | 97.8009 | 96.3194
29 | Dandeli | 7 | 7 | 1:20 | 1:20 | 77:16 | 35:51 | 113:07 | 113:07 | 114:27 | 16:21 | 97.7556 | 97.7292 | 114:27 | 16:21 | 97.7556 | 97.7292
30 | Haliyal | 2 | 2 | 0:52 | 0:52 | 20:55 | 23:55 | 44:50 | 44:50 | 45:42 | 22:51 | 96.8866 | 96.8264 | 45:42 | 22:51 | 96.8866 | 96.8264
31 | Ankola | 3 | 3 | 26:42 | 26:42 | 11:28 | 24:45 | 36:13 | 36:13 | 62:55 | 20:58 | 98.3233 | 97.0872 | 62:55 | 20:58 | 98.3233 | 97.0872
32 | Kumta | 3 | 3 | 15:12 | 15:12 | 11:21 | 17:02 | 28:23 | 28:23 | 43:35 | 14:32 | 98.686 | 97.9823 | 43:35 | 14:32 | 98.686 | 97.9823
33 | Gokarna | 1 | 1 | 24:05 | 24:05 | 1:10 | 0:15 | 1:25 | 1:25 | 25:30 | 25:30 | 99.8032 | 96.4583 | 25:30 | 25:30 | 99.8032 | 96.4583
34 | Kasarkod | 1 | 1 | 11:21 | 11:21 | 2:35 | 4:55 | 7:30 | 7:30 | 18:51 | 18:51 | 98.9583 | 97.3819 | 18:51 | 18:51 | 98.9583 | 97.3819
35 | Honnavar | 3 | 3 | 16:06 | 16:06 | 20:00 | 16:36 | 36:36 | 36:36 | 52:42 | 17:34 | 98.3056 | 97.5602 | 52:42 | 17:34 | 98.3056 | 97.5602
36 | Murdeshwar | 4 | 4 | 24:32 | 24:32 | 28:04 | 13:59 | 42:03 | 42:03 | 66:35 | 16:39 | 98.5399 | 97.6881 | 66:35 | 16:39 | 98.5399 | 97.6881
37 | Bhatkal | 3 | 3 | 20:18 | 20:18 | 9:14 | 11:16 | 20:30 | 20:30 | 40:48 | 13:36 | 99.0509 | 98.1111 | 40:48 | 13:36 | 99.0509 | 98.1111
38 | Khanapur | 2 | 2 | 20:30 | 20:30 | 43:10 | 30:00 | 73:10 | 73:10 | 93:40 | 46:50 | 94.919 | 93.4954 | 93:40 | 46:50 | 94.919 | 93.4954
39 | Bailhongal | 3 | 3 | 0:00 | 0:00 | 103:10 | 43:15 | 146:25 | 146:25 | 146:25 | 48:48 | 93.2215 | 93.2215 | 146:25 | 48:48 | 93.2215 | 93.2215
40 | Kittur | 1 | 1 | 0:45 | 0:45 | 7:05 | 14:10 | 21:15 | 21:15 | 22:00 | 22:00 | 97.0486 | 96.9444 | 22:00 | 22:00 | 97.0486 | 96.9444
41 | M K Hubli | 1 | 1 | 0:25 | 0:25 | 18:25 | 10:50 | 29:15 | 29:15 | 29:40 | 29:40 | 95.9375 | 95.8796 | 29:40 | 29:40 | 95.9375 | 95.8796
42 | Soundatti | 3 | 3 | 11:50 | 11:50 | 40:05 | 23:03 | 63:08 | 63:08 | 74:58 | 24:59 | 97.0772 | 96.5293 | 74:58 | 24:59 | 97.0772 | 96.5293
43 | Munavalli | 1 | 1 | 10:10 | 10:10 | 28:50 | 4:25 | 33:15 | 33:15 | 43:25 | 43:25 | 95.3819 | 93.9699 | 43:25 | 43:25 | 95.3819 | 93.9699
44 | Yaragatti | 1 | 1 | 14:11 | 14:11 | 29:22 | 9:43 | 39:05 | 39:05 | 53:16 | 53:16 | 94.5718 | 92.6019 | 53:16 | 53:16 | 94.5718 | 92.6019
45 | Ramdurg | 2 | 2 | 11:46 | 11:46 | 38:25 | 18:07 | 56:32 | 56:32 | 68:18 | 34:09 | 96.0741 | 95.2569 | 68:18 | 34:09 | 96.0741 | 95.2569
46 | Gokak | 10 | 10 | 64:26 | 64:26 | 11:06 | 45:10 | 56:16 | 56:16 | 120:42 | 12:04 | 99.2185 | 98.3236 | 120:42 | 12:04 | 99.2185 | 98.3236
47 | Mudalagi | 2 | 2 | 0:15 | 0:15 | 23:05 | 31:35 | 54:40 | 54:40 | 54:55 | 27:27 | 96.2037 | 96.1863 | 54:55 | 27:27 | 96.2037 | 96.1863
48 | Konnur | 1 | 1 | 1:05 | 1:05 | 17:45 | 17:30 | 35:15 | 35:15 | 36:20 | 36:20 | 95.1042 | 94.9537 | 36:20 | 36:20 | 95.1042 | 94.9537
49 | Raibag | 1 | 1 | 0:00 | 0:00 | 31:35 | 20:00 | 51:35 | 51:35 | 51:35 | 51:35 | 92.8356 | 92.8356 | 51:35 | 51:35 | 92.8356 | 92.8356
50 | Kudachi | 1 | 1 | 0:40 | 0:40 | 48:00 | 20:05 | 68:05 | 68:05 | 68:45 | 68:45 | 90.544 | 90.4514 | 68:45 | 68:45 | 90.544 | 90.4514
51 | Athani | 7 | 7 | 51:12 | 51:12 | 80:28 | 176:33 | 257:01 | 257:01 | 308:13 | 44:02 | 94.9005 | 93.8846 | 308:13 | 44:02 | 94.9005 | 93.8846
52 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 8:50 | 35:15 | 44:05 | 44:05 | 44:05 | 22:02 | 96.9387 | 96.9387 | 44:05 | 22:02 | 96.9387 | 96.9387
53 | Nippani | 5 | 5 | 0:00 | 0:00 | 60:30 | 35:50 | 96:20 | 96:20 | 96:20 | 19:16 | 97.3241 | 97.3241 | 96:20 | 19:16 | 97.3241 | 97.3241
54 | Sadalaga | 1 | 1 | 1:25 | 1:25 | 15:40 | 11:10 | 26:50 | 26:50 | 28:15 | 28:15 | 96.2731 | 96.0764 | 28:15 | 28:15 | 96.2731 | 96.0764
55 | Muddebihal | 2 | 2 | 11:35 | 11:35 | 38:40 | 12:05 | 50:45 | 50:45 | 62:20 | 31:10 | 96.4757 | 95.6713 | 62:20 | 31:10 | 96.4757 | 95.6713
56 | Talikoti | 1 | 1 | 2:30 | 2:30 | 17:15 | 6:40 | 23:55 | 23:55 | 26:25 | 26:25 | 96.6782 | 96.331 | 26:25 | 26:25 | 96.6782 | 96.331
57 | B.Bagewadi | 1 | 1 | 6:52 | 6:52 | 12:41 | 9:40 | 22:21 | 22:21 | 29:13 | 29:13 | 96.8958 | 95.9421 | 29:13 | 29:13 | 96.8958 | 95.9421
58 | Indi | 3 | 3 | 6:58 | 6:58 | 25:07 | 6:24 | 31:31 | 31:31 | 38:29 | 12:50 | 98.5409 | 98.2184 | 38:29 | 12:50 | 98.5409 | 98.2184
59 | Sindagi | 2 | 2 | 16:50 | 16:50 | 22:40 | 11:55 | 34:35 | 34:35 | 51:25 | 25:42 | 97.5984 | 96.4294 | 51:25 | 25:42 | 97.5984 | 96.4294
60 | Guledgudda | 1 | 1 | 0:51 | 0:51 | 6:27 | 7:28 | 13:55 | 13:55 | 14:46 | 14:46 | 98.0671 | 97.9491 | 14:46 | 14:46 | 98.0671 | 97.9491
61 | Ilkal | 7 | 7 | 22:42 | 22:42 | 45:12 | 107:23 | 152:35 | 152:35 | 175:17 | 25:02 | 96.9726 | 96.5222 | 175:17 | 25:02 | 96.9726 | 96.5222
62 | Kerur | 1 | 1 | 2:45 | 2:45 | 24:27 | 15:20 | 39:47 | 39:47 | 42:32 | 42:32 | 94.4745 | 94.0926 | 42:32 | 42:32 | 94.4745 | 94.0926
63 | Hungund | 4 | 4 | 9:58 | 9:58 | 60:45 | 66:01 | 126:46 | 126:46 | 136:44 | 34:11 | 95.5984 | 95.2523 | 136:44 | 34:11 | 95.5984 | 95.2523
64 | Badami | 1 | 1 | 2:34 | 2:34 | 5:10 | 19:05 | 24:15 | 24:15 | 26:49 | 26:49 | 96.6319 | 96.2755 | 26:49 | 26:49 | 96.6319 | 96.2755
65 | Jamkhandi | 6 | 6 | 9:10 | 9:10 | 77:35 | 30:15 | 107:50 | 107:50 | 117:00 | 19:30 | 97.5039 | 97.2917 | 117:00 | 19:30 | 97.5039 | 97.2917
66 | Mahalingapur | 2 | 2 | 2:46 | 2:46 | 30:01 | 7:34 | 37:35 | 37:35 | 40:21 | 20:10 | 97.39 | 97.1979 | 40:21 | 20:10 | 97.39 | 97.1979
67 | Rannabelagali | 1 | 1 | 2:52 | 2:52 | 13:40 | 2:50 | 16:30 | 16:30 | 19:22 | 19:22 | 97.7083 | 97.3102 | 19:22 | 19:22 | 97.7083 | 97.3102
68 | Rabakavi | 2 | 2 | 6:05 | 6:05 | 24:40 | 12:25 | 37:05 | 37:05 | 43:10 | 21:35 | 97.4248 | 97.0023 | 43:10 | 21:35 | 97.4248 | 97.0023
69 | Banahatti | 2 | 2 | 4:10 | 4:10 | 25:10 | 4:50 | 30:00 | 30:00 | 34:10 | 17:05 | 97.9167 | 97.6273 | 34:10 | 17:05 | 97.9167 | 97.6273
70 | Terdal | 2 | 2 | 18:30 | 18:30 | 58:52 | 9:05 | 67:57 | 67:57 | 86:27 | 43:14 | 95.2812 | 93.9965 | 86:27 | 43:14 | 95.2812 | 93.9965
71 | Mudhol | 4 | 4 | 11:58 | 11:58 | 121:13 | 6:02 | 127:15 | 127:15 | 139:13 | 34:48 | 95.5816 | 95.1661 | 139:13 | 34:48 | 95.5816 | 95.1661
72 | Bilagi | 1 | 1 | 2:25 | 2:25 | 18:45 | 5:00 | 23:45 | 23:45 | 26:10 | 26:10 | 96.7014 | 96.3657 | 26:10 | 26:10 | 96.7014 | 96.3657
73 | Lokapur | 2 | 2 | 0:25 | 0:25 | 36:20 | 7:10 | 43:30 | 43:30 | 43:55 | 21:58 | 96.9792 | 96.9502 | 43:55 | 21:58 | 96.9792 | 96.9502
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of May-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2022 |  |  |  | Reliability for cumulative period from Apr-22 to May-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 80 | 80 | 32:59 | 94:24 | 377:16 | 458:56 | 836:12 | 1783:36 | 869:11 | 10:52 | 98.5951 | 98.5397 | 1878:00 | 23:29 | 98.4771 | 98.3965
2 | Dharwad(R) | 14 | 14 | 1:40 | 3:20 | 90:53 | 163:45 | 254:38 | 648:37 | 256:18 | 18:18 | 97.5554 | 97.5394 | 651:57 | 46:34 | 96.8354 | 96.8191
3 | Kundagol | 1 | 1 | 9:55 | 47:00 | 5:20 | 4:00 | 9:20 | 20:55 | 19:15 | 19:15 | 98.7455 | 97.4126 | 67:55 | 67:55 | 98.5713 | 95.3609
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 3:51 | 18:29 | 22:20 | 52:56 | 22:20 | 22:20 | 96.9982 | 96.9982 | 52:56 | 52:56 | 96.3843 | 96.3843
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 2:40 | 15:22 | 18:02 | 74:02 | 18:02 | 18:02 | 97.5762 | 97.5762 | 74:02 | 74:02 | 94.9431 | 94.9431
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 70:00 | 23:00 | 93:00 | 155:10 | 93:00 | 46:30 | 93.75 | 93.75 | 155:10 | 77:35 | 94.7006 | 94.7006
7 | Alnavar | 2 | 2 | 0:00 | 0:00 | 4:50 | 51:55 | 56:45 | 80:45 | 56:45 | 28:22 | 96.1862 | 96.1862 | 80:45 | 40:22 | 97.2421 | 97.2421
8 | Naragund | 2 | 2 | 17:20 | 36:30 | 34:35 | 15:30 | 50:05 | 101:40 | 67:25 | 33:43 | 96.6342 | 95.4693 | 138:10 | 69:05 | 96.5278 | 95.2812
9 | Shirahatti | 1 | 1 | 0:00 | 0:00 | 6:15 | 16:40 | 22:55 | 45:50 | 22:55 | 22:55 | 96.9198 | 96.9198 | 45:50 | 45:50 | 96.8693 | 96.8693
10 | Laxmeshwar | 3 | 3 | 0:00 | 0:00 | 53:42 | 38:37 | 92:19 | 203:09 | 92:19 | 30:46 | 95.8639 | 95.8639 | 203:09 | 67:43 | 95.3745 | 95.3745
11 | Naregal | 1 | 1 | 1:40 | 2:50 | 9:15 | 6:05 | 15:20 | 26:50 | 17:00 | 17:00 | 97.9391 | 97.7151 | 29:40 | 29:40 | 98.1671 | 97.9736
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 33:35 | 21:25 | 55:00 | 105:10 | 55:00 | 27:30 | 96.3038 | 96.3038 | 105:10 | 52:35 | 96.4082 | 96.4082
13 | Ron | 3 | 3 | 0:00 | 0:00 | 42:00 | 40:07 | 82:07 | 181:29 | 82:07 | 27:22 | 96.3209 | 96.3209 | 181:29 | 60:30 | 95.8679 | 95.8679
14 | Mundaragi | 1 | 1 | 0:00 | 0:00 | 19:45 | 40:15 | 60:00 | 74:30 | 60:00 | 60:00 | 91.9355 | 91.9355 | 74:30 | 74:30 | 94.9112 | 94.9112
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 22:06 | 67:59 | 90:05 | 189:12 | 90:05 | 90:05 | 87.892 | 87.892 | 189:12 | 189:12 | 87.0765 | 87.0765
16 | Savanur | 2 | 2 | 3:05 | 3:05 | 35:40 | 25:20 | 61:00 | 91:15 | 64:05 | 32:02 | 95.9005 | 95.6933 | 94:20 | 47:10 | 96.8835 | 96.7782
17 | Shiggaon | 3 | 3 | 27:35 | 77:30 | 31:05 | 81:20 | 112:25 | 168:10 | 140:00 | 46:40 | 94.9634 | 93.7276 | 245:40 | 81:53 | 96.1711 | 94.4065
18 | Bankapur | 1 | 1 | 18:55 | 29:00 | 23:45 | 42:10 | 65:55 | 96:05 | 84:50 | 84:50 | 91.1402 | 88.5977 | 125:05 | 125:05 | 93.4369 | 91.4561
19 | Hangal | 2 | 2 | 1:34 | 4:00 | 24:05 | 47:45 | 71:50 | 95:20 | 73:24 | 36:42 | 95.1725 | 95.0672 | 99:20 | 49:40 | 96.7441 | 96.6075
20 | Ranebennur | 10 | 10 | 4:32 | 38:33 | 89:26 | 143:25 | 232:51 | 350:17 | 237:23 | 23:44 | 96.8703 | 96.8094 | 388:50 | 38:53 | 97.6074 | 97.344
21 | Tuminakatti | 1 | 1 | 0:25 | 3:30 | 15:10 | 3:55 | 19:05 | 43:30 | 19:30 | 19:30 | 97.435 | 97.379 | 47:00 | 47:00 | 97.0287 | 96.7896
22 | Rattihalli | 1 | 1 | 0:45 | 7:10 | 28:15 | 8:40 | 36:55 | 54:15 | 37:40 | 37:40 | 95.0381 | 94.9373 | 61:25 | 61:25 | 96.2944 | 95.8049
23 | Hirekerur | 1 | 1 | 1:20 | 5:35 | 24:25 | 10:25 | 34:50 | 61:35 | 36:10 | 36:10 | 95.3181 | 95.1389 | 67:10 | 67:10 | 95.7935 | 95.4121
24 | Byadagi | 5 | 5 | 49:55 | 96:50 | 67:20 | 69:00 | 136:20 | 225:10 | 186:15 | 37:15 | 96.3351 | 94.9933 | 322:00 | 64:24 | 96.924 | 95.6011
25 | Sirsi | 6 | 6 | 10:18 | 59:29 | 21:15 | 25:58 | 47:13 | 130:43 | 57:31 | 9:35 | 98.9423 | 98.7115 | 190:12 | 31:42 | 98.5119 | 97.8347
26 | Yellapur | 1 | 1 | 3:25 | 19:25 | 5:25 | 3:40 | 9:05 | 17:55 | 12:30 | 12:30 | 98.7791 | 98.3199 | 37:20 | 37:20 | 98.7762 | 97.4499
27 | Mundagod | 1 | 1 | 0:00 | 0:00 | 7:10 | 9:35 | 16:45 | 29:35 | 16:45 | 16:45 | 97.7487 | 97.7487 | 29:35 | 29:35 | 97.9793 | 97.9793
28 | Siddapur | 1 | 1 | 10:40 | 21:20 | 8:35 | 7:15 | 15:50 | 31:40 | 26:30 | 26:30 | 97.8719 | 96.4382 | 53:00 | 53:00 | 97.837 | 96.3798
29 | Dandeli | 7 | 7 | 7:06 | 8:26 | 43:05 | 17:38 | 60:43 | 173:50 | 67:49 | 9:41 | 98.8342 | 98.6978 | 182:16 | 26:02 | 98.3037 | 98.2214
30 | Haliyal | 2 | 2 | 4:44 | 5:36 | 23:55 | 10:20 | 34:15 | 79:05 | 38:59 | 19:30 | 97.6983 | 97.3802 | 84:41 | 42:21 | 97.2991 | 97.1078
31 | Ankola | 3 | 3 | 32:48 | 59:30 | 13:13 | 0:37 | 13:50 | 50:03 | 46:38 | 15:33 | 99.3802 | 97.9107 | 109:33 | 36:31 | 98.8604 | 97.5057
32 | Kumta | 3 | 3 | 8:18 | 23:30 | 12:38 | 25:42 | 38:20 | 66:43 | 46:38 | 15:33 | 98.2826 | 97.9107 | 90:13 | 30:04 | 98.481 | 97.9459
33 | Gokarna | 1 | 1 | 9:42 | 33:47 | 6:35 | 2:25 | 9:00 | 10:25 | 18:42 | 18:42 | 98.7903 | 97.4866 | 44:12 | 44:12 | 99.2885 | 96.9809
34 | Kasarkod | 1 | 1 | 5:51 | 17:12 | 3:48 | 11:01 | 14:49 | 22:19 | 20:40 | 20:40 | 98.0085 | 97.2222 | 39:31 | 39:31 | 98.4756 | 97.3008
35 | Honnavar | 3 | 3 | 26:33 | 42:39 | 23:31 | 30:13 | 53:44 | 90:20 | 80:17 | 26:46 | 97.5926 | 96.4031 | 132:59 | 44:20 | 97.9432 | 96.9721
36 | Murdeshwar | 4 | 4 | 35:56 | 60:28 | 31:08 | 36:28 | 67:36 | 109:39 | 103:32 | 25:53 | 97.7285 | 96.5211 | 170:07 | 42:32 | 98.1276 | 97.095
37 | Bhatkal | 3 | 3 | 46:36 | 66:54 | 36:00 | 7:12 | 43:12 | 63:42 | 89:48 | 29:56 | 98.0645 | 95.9767 | 130:36 | 43:32 | 98.5496 | 97.0264
38 | Khanapur | 2 | 2 | 3:00 | 23:30 | 45:45 | 18:30 | 64:15 | 137:25 | 67:15 | 33:37 | 95.6821 | 95.4805 | 160:55 | 80:28 | 95.3068 | 94.5042
39 | Bailhongal | 3 | 3 | 0:00 | 0:00 | 58:20 | 25:20 | 83:40 | 230:05 | 83:40 | 27:53 | 96.2515 | 96.2515 | 230:05 | 76:42 | 94.7613 | 94.7613
40 | Kittur | 1 | 1 | 0:00 | 0:45 | 17:20 | 8:00 | 25:20 | 46:35 | 25:20 | 25:20 | 96.595 | 96.595 | 47:20 | 47:20 | 96.8181 | 96.7668
41 | M K Hubli | 1 | 1 | 0:20 | 0:45 | 12:45 | 5:55 | 18:40 | 47:55 | 19:00 | 19:00 | 97.491 | 97.4462 | 48:40 | 48:40 | 96.727 | 96.6758
42 | Soundatti | 3 | 3 | 3:42 | 15:32 | 33:16 | 10:53 | 44:09 | 107:17 | 47:51 | 15:57 | 98.022 | 97.8562 | 122:49 | 40:56 | 97.5573 | 97.2036
43 | Munavalli | 1 | 1 | 10:10 | 20:20 | 28:50 | 4:25 | 33:15 | 66:30 | 43:25 | 43:25 | 95.5309 | 94.1644 | 86:50 | 86:50 | 95.4577 | 94.0688
44 | Yaragatti | 1 | 1 | 1:58 | 16:09 | 44:47 | 11:14 | 56:01 | 95:06 | 57:59 | 57:59 | 92.4709 | 92.2065 | 111:15 | 111:15 | 93.5041 | 92.401
45 | Ramdurg | 2 | 2 | 0:00 | 11:46 | 31:03 | 16:50 | 47:53 | 104:25 | 47:53 | 23:56 | 96.782 | 96.782 | 116:11 | 58:05 | 96.4339 | 96.032
46 | Gokak | 10 | 10 | 75:42 | 140:08 | 37:44 | 22:08 | 59:52 | 116:08 | 135:34 | 13:33 | 99.1953 | 98.1779 | 256:16 | 25:38 | 99.2067 | 98.2495
47 | Mudalagi | 2 | 2 | 1:20 | 1:35 | 54:45 | 24:10 | 78:55 | 133:35 | 80:15 | 40:08 | 94.6965 | 94.6069 | 135:10 | 67:35 | 95.4377 | 95.3837
48 | Konnur | 1 | 1 | 0:25 | 1:30 | 19:30 | 6:05 | 25:35 | 60:50 | 26:00 | 26:00 | 96.5614 | 96.5054 | 62:20 | 62:20 | 95.8447 | 95.7423
49 | Raibag | 1 | 1 | 0:00 | 0:00 | 41:20 | 15:20 | 56:40 | 108:15 | 56:40 | 56:40 | 92.3835 | 92.3835 | 108:15 | 108:15 | 92.6059 | 92.6059
50 | Kudachi | 1 | 1 | 0:00 | 0:40 | 59:45 | 14:25 | 74:10 | 142:15 | 74:10 | 74:10 | 90.0314 | 90.0314 | 142:55 | 142:55 | 90.2835 | 90.2379
51 | Athani | 7 | 7 | 46:12 | 97:24 | 90:06 | 196:37 | 286:43 | 543:44 | 332:55 | 47:34 | 94.4947 | 93.6076 | 641:08 | 91:35 | 94.6942 | 93.7438
52 | Chikkodi | 2 | 2 | 0:00 | 0:00 | 21:10 | 9:25 | 30:35 | 74:40 | 30:35 | 15:18 | 97.9447 | 97.9447 | 74:40 | 37:20 | 97.4499 | 97.4499
53 | Nippani | 5 | 5 | 0:00 | 0:00 | 158:55 | 47:22 | 206:17 | 302:37 | 206:17 | 41:15 | 94.4547 | 94.4547 | 302:37 | 60:31 | 95.8659 | 95.8659
54 | Sadalaga | 1 | 1 | 13:40 | 15:05 | 20:25 | 7:05 | 27:30 | 54:20 | 41:10 | 41:10 | 96.3038 | 94.4668 | 69:25 | 69:25 | 96.2887 | 95.2584
55 | Muddebihal | 2 | 2 | 3:40 | 15:15 | 70:00 | 50:40 | 120:40 | 171:25 | 124:20 | 62:10 | 91.8907 | 91.6443 | 186:40 | 93:20 | 94.1456 | 93.6248
56 | Talikoti | 1 | 1 | 9:45 | 12:15 | 26:45 | 12:55 | 39:40 | 63:35 | 49:25 | 49:25 | 94.6685 | 93.358 | 75:50 | 75:50 | 95.6569 | 94.8201
57 | B.Bagewadi | 1 | 1 | 2:30 | 9:22 | 14:22 | 2:33 | 16:55 | 39:16 | 19:25 | 19:25 | 97.7263 | 97.3902 | 48:38 | 48:38 | 97.3179 | 96.6781
58 | Indi | 3 | 3 | 38:24 | 45:22 | 33:30 | 12:01 | 45:31 | 77:02 | 83:55 | 27:58 | 97.9607 | 96.2403 | 122:24 | 40:48 | 98.2461 | 97.2131
59 | Sindagi | 2 | 2 | 7:10 | 24:00 | 39:45 | 24:55 | 64:40 | 99:15 | 71:50 | 35:55 | 95.6541 | 95.1725 | 123:15 | 61:38 | 96.6103 | 95.7906
60 | Guledgudda | 1 | 1 | 0:00 | 0:51 | 11:35 | 8:21 | 19:56 | 33:51 | 19:56 | 19:56 | 97.3208 | 97.3208 | 34:42 | 34:42 | 97.6878 | 97.6298
61 | Ilkal | 7 | 7 | 17:00 | 39:42 | 107:25 | 139:06 | 246:31 | 399:06 | 263:31 | 37:39 | 95.2666 | 94.9402 | 438:48 | 62:41 | 96.1056 | 95.7182
62 | Kerur | 1 | 1 | 0:00 | 2:45 | 26:51 | 33:14 | 60:05 | 99:52 | 60:05 | 60:05 | 91.9243 | 91.9243 | 102:37 | 102:37 | 93.1785 | 92.9907
63 | Hungund | 4 | 4 | 9:49 | 19:47 | 82:52 | 82:30 | 165:22 | 292:08 | 175:11 | 43:48 | 94.4433 | 94.1135 | 311:55 | 77:59 | 95.0114 | 94.6736
64 | Badami | 1 | 1 | 0:20 | 2:54 | 12:10 | 14:57 | 27:07 | 51:22 | 27:27 | 27:27 | 96.3553 | 96.3105 | 54:16 | 54:16 | 96.4913 | 96.2933
65 | Jamkhandi | 6 | 6 | 0:00 | 9:10 | 183:35 | 64:55 | 248:30 | 356:20 | 248:30 | 41:25 | 94.4332 | 94.4332 | 365:30 | 60:55 | 95.9434 | 95.839
66 | Mahalingapur | 2 | 2 | 0:30 | 3:16 | 54:01 | 4:40 | 58:41 | 96:16 | 59:11 | 29:36 | 96.0562 | 96.0226 | 99:32 | 49:46 | 96.7122 | 96.6006
67 | Rannabelagali | 1 | 1 | 3:22 | 6:14 | 15:48 | 11:20 | 27:08 | 43:38 | 30:30 | 30:30 | 96.353 | 95.9005 | 49:52 | 49:52 | 97.0196 | 96.5938
68 | Rabakavi | 2 | 2 | 0:40 | 6:45 | 21:00 | 9:30 | 30:30 | 67:35 | 31:10 | 15:35 | 97.9503 | 97.9055 | 74:20 | 37:10 | 97.6918 | 97.4613
69 | Banahatti | 2 | 2 | 0:00 | 4:10 | 28:10 | 8:35 | 36:45 | 66:45 | 36:45 | 18:22 | 97.5302 | 97.5302 | 70:55 | 35:28 | 97.7203 | 97.578
70 | Terdal | 2 | 2 | 0:00 | 18:30 | 28:10 | 19:35 | 47:45 | 115:42 | 47:45 | 23:52 | 96.791 | 96.791 | 134:12 | 67:06 | 96.0485 | 95.4167
71 | Mudhol | 4 | 4 | 32:22 | 44:20 | 43:49 | 24:36 | 68:25 | 195:40 | 100:47 | 25:12 | 97.7011 | 96.6135 | 240:00 | 60:00 | 96.6587 | 95.9016
72 | Bilagi | 1 | 1 | 0:50 | 3:15 | 22:50 | 7:20 | 30:10 | 53:55 | 31:00 | 31:00 | 95.9453 | 95.8333 | 57:10 | 57:10 | 96.3172 | 96.0952
73 | Lokapur | 2 | 2 | 0:00 | 0:25 | 80:05 | 29:50 | 109:55 | 153:25 | 109:55 | 54:57 | 92.6131 | 92.6131 | 153:50 | 76:55 | 94.7604 | 94.7461
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of June-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2022 |  |  |  | Reliability for cumulative period from Apr-22 to June-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 80 | 80 | 157:27 | 251:51 | 379:20 | 253:07 | 632:27 | 2416:03 | 789:54 | 9:52 | 98.902 | 98.6286 | 2667:54 | 33:21 | 98.6172 | 98.473
2 | Dharwad(R) | 14 | 14 | 11:40 | 15:00 | 127:46 | 50:07 | 177:53 | 826:30 | 189:33 | 13:32 | 98.2353 | 98.1195 | 841:30 | 60:06 | 97.2969 | 97.2478
3 | Kundagol | 1 | 1 | 27:10 | 74:10 | 4:55 | 9:05 | 14:00 | 34:55 | 41:10 | 41:10 | 98.0556 | 94.2824 | 109:05 | 109:05 | 98.4013 | 95.0053
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 10:13 | 11:10 | 21:23 | 74:19 | 21:23 | 21:23 | 97.0301 | 97.0301 | 74:19 | 74:19 | 96.5972 | 96.5972
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 8:00 | 6:55 | 14:55 | 88:57 | 14:55 | 14:55 | 97.9282 | 97.9282 | 88:57 | 88:57 | 95.9272 | 95.9272
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 7:50 | 8:10 | 16:00 | 171:10 | 16:00 | 8:00 | 98.8889 | 98.8889 | 171:10 | 85:35 | 96.0813 | 96.0813
7 | Alnavar | 2 | 2 | 0:00 | 0:00 | 4:30 | 28:20 | 32:50 | 113:35 | 32:50 | 16:25 | 97.7199 | 97.7199 | 113:35 | 56:47 | 97.3996 | 97.3996
8 | Naragund | 2 | 2 | 1:10 | 37:40 | 17:30 | 32:30 | 50:00 | 151:40 | 51:10 | 25:35 | 96.5278 | 96.4468 | 189:20 | 94:40 | 96.5278 | 95.6654
9 | Shirahatti | 1 | 1 | 0:00 | 0:00 | 5:50 | 11:50 | 17:40 | 63:30 | 17:40 | 17:40 | 97.5463 | 97.5463 | 63:30 | 63:30 | 97.0925 | 97.0925
10 | Laxmeshwar | 3 | 3 | 0:00 | 0:00 | 20:36 | 15:50 | 36:26 | 239:35 | 36:26 | 12:09 | 98.3133 | 98.3133 | 239:35 | 79:52 | 96.3434 | 96.3434
11 | Naregal | 1 | 1 | 0:00 | 2:50 | 6:35 | 12:00 | 18:35 | 45:25 | 18:35 | 18:35 | 97.419 | 97.419 | 48:15 | 48:15 | 97.9205 | 97.7908
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 9:10 | 9:50 | 19:00 | 124:10 | 19:00 | 9:30 | 98.6806 | 98.6806 | 124:10 | 62:05 | 97.1574 | 97.1574
13 | Ron | 3 | 3 | 0:00 | 0:00 | 19:05 | 10:40 | 29:45 | 211:14 | 29:45 | 9:55 | 98.6227 | 98.6227 | 211:14 | 70:25 | 96.776 | 96.776
14 | Mundaragi | 1 | 1 | 0:00 | 0:00 | 16:55 | 18:50 | 35:45 | 110:15 | 35:45 | 35:45 | 95.0347 | 95.0347 | 110:15 | 110:15 | 94.9519 | 94.9519
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 18:18 | 57:46 | 76:04 | 265:16 | 76:04 | 76:04 | 89.4352 | 89.4352 | 265:16 | 265:16 | 87.8541 | 87.8541
16 | Savanur | 2 | 2 | 1:10 | 4:15 | 14:10 | 5:00 | 19:10 | 110:25 | 20:20 | 10:10 | 98.669 | 98.588 | 114:40 | 57:20 | 97.4721 | 97.3748
17 | Shiggaon | 3 | 3 | 13:40 | 91:10 | 37:10 | 19:10 | 56:20 | 224:30 | 70:00 | 23:20 | 97.392 | 96.7593 | 315:40 | 105:13 | 96.5736 | 95.1821
18 | Bankapur | 1 | 1 | 18:25 | 47:25 | 21:15 | 13:40 | 34:55 | 131:00 | 53:20 | 53:20 | 95.1505 | 92.5926 | 178:25 | 178:25 | 94.0018 | 91.8307
19 | Hangal | 2 | 2 | 6:04 | 10:04 | 26:15 | 44:50 | 71:05 | 166:25 | 77:09 | 38:34 | 95.0637 | 94.6424 | 176:29 | 88:14 | 96.1901 | 95.9596
20 | Ranebennur | 10 | 10 | 4:00 | 42:33 | 120:34 | 46:59 | 167:33 | 517:50 | 171:33 | 17:09 | 97.6729 | 97.6174 | 560:23 | 56:02 | 97.629 | 97.4341
21 | Tuminakatti | 1 | 1 | 0:35 | 4:05 | 35:20 | 10:05 | 45:25 | 88:55 | 46:00 | 46:00 | 93.6921 | 93.6111 | 93:00 | 93:00 | 95.9287 | 95.7418
22 | Rattihalli | 1 | 1 | 0:35 | 7:45 | 21:35 | 7:20 | 28:55 | 83:10 | 29:30 | 29:30 | 95.9838 | 95.9028 | 90:55 | 90:55 | 96.192 | 95.8371
23 | Hirekerur | 1 | 1 | 1:00 | 6:35 | 17:00 | 14:30 | 31:30 | 93:05 | 32:30 | 32:30 | 95.625 | 95.4861 | 99:40 | 99:40 | 95.7379 | 95.4365
24 | Byadagi | 5 | 5 | 27:21 | 124:11 | 38:18 | 27:35 | 65:53 | 291:03 | 93:14 | 18:39 | 98.1699 | 97.4102 | 415:14 | 83:03 | 97.3347 | 96.1975
25 | Sirsi | 6 | 6 | 41:13 | 100:42 | 74:32 | 18:09 | 92:41 | 223:24 | 133:54 | 22:19 | 97.8546 | 96.9005 | 324:06 | 54:01 | 98.2952 | 97.5267
26 | Yellapur | 1 | 1 | 14:25 | 33:50 | 11:45 | 3:40 | 15:25 | 33:20 | 29:50 | 29:50 | 97.8588 | 95.8565 | 67:10 | 67:10 | 98.4737 | 96.9246
27 | Mundagod | 1 | 1 | 1:40 | 1:40 | 7:10 | 9:35 | 16:45 | 46:20 | 18:25 | 18:25 | 97.6736 | 97.4421 | 48:00 | 48:00 | 97.8785 | 97.8022
28 | Siddapur | 1 | 1 | 7:20 | 28:40 | 5:25 | 5:30 | 10:55 | 42:35 | 18:15 | 18:15 | 98.4838 | 97.4653 | 71:15 | 71:15 | 98.0502 | 96.7376
29 | Dandeli | 7 | 7 | 17:18 | 25:44 | 65:44 | 11:53 | 77:37 | 251:27 | 94:55 | 13:34 | 98.46 | 98.1167 | 277:11 | 39:36 | 98.3552 | 98.1869
30 | Haliyal | 2 | 2 | 0:00 | 5:36 | 4:10 | 5:40 | 9:50 | 88:55 | 9:50 | 4:55 | 99.3171 | 99.3171 | 94:31 | 47:16 | 97.9644 | 97.8362
31 | Ankola | 3 | 3 | 22:17 | 81:47 | 36:45 | 39:58 | 76:43 | 126:46 | 99:00 | 33:00 | 96.4483 | 95.4167 | 208:33 | 69:31 | 98.0652 | 96.817
32 | Kumta | 3 | 3 | 0:48 | 24:18 | 23:50 | 28:04 | 51:54 | 118:37 | 52:42 | 17:34 | 97.5972 | 97.5602 | 142:55 | 47:38 | 98.1896 | 97.8187
33 | Gokarna | 1 | 1 | 12:10 | 45:57 | 4:05 | 3:50 | 7:55 | 18:20 | 20:05 | 20:05 | 98.9005 | 97.2106 | 64:17 | 64:17 | 99.1606 | 97.0566
34 | Kasarkod | 1 | 1 | 36:17 | 53:29 | 10:51 | 8:35 | 19:26 | 41:45 | 55:43 | 55:43 | 97.3009 | 92.2616 | 95:14 | 95:14 | 98.0884 | 95.6395
35 | Honnavar | 3 | 3 | 4:21 | 47:00 | 30:38 | 32:09 | 62:47 | 153:07 | 67:08 | 22:23 | 97.0934 | 96.892 | 200:07 | 66:42 | 97.6631 | 96.9457
36 | Murdeshwar | 4 | 4 | 6:52 | 67:20 | 55:59 | 29:45 | 85:44 | 195:23 | 92:36 | 23:09 | 97.0231 | 96.7847 | 262:43 | 65:41 | 97.7635 | 96.9927
37 | Bhatkal | 3 | 3 | 17:15 | 84:09 | 23:20 | 10:48 | 34:08 | 97:50 | 51:23 | 17:08 | 98.4198 | 97.6211 | 181:59 | 60:40 | 98.5068 | 97.2225
38 | Khanapur | 2 | 2 | 12:55 | 36:25 | 21:40 | 13:30 | 35:10 | 172:35 | 48:05 | 24:02 | 97.5579 | 96.6609 | 209:00 | 104:30 | 96.0489 | 95.2152
39 | Bailhongal | 3 | 3 | 0:00 | 0:00 | 21:10 | 15:35 | 36:45 | 266:50 | 36:45 | 12:15 | 98.2986 | 98.2986 | 266:50 | 88:57 | 95.9275 | 95.9275
40 | Kittur | 1 | 1 | 0:00 | 0:45 | 17:20 | 8:00 | 25:20 | 71:55 | 25:20 | 25:20 | 96.4815 | 96.4815 | 72:40 | 72:40 | 96.7071 | 96.6728
41 | M K Hubli | 1 | 1 | 0:00 | 0:45 | 20:10 | 1:45 | 21:55 | 69:50 | 21:55 | 21:55 | 96.956 | 96.956 | 70:35 | 70:35 | 96.8025 | 96.7682
42 | Soundatti | 3 | 3 | 6:55 | 22:27 | 24:18 | 4:28 | 28:46 | 136:03 | 35:41 | 11:54 | 98.6682 | 98.348 | 158:30 | 52:50 | 97.9235 | 97.5809
43 | Munavalli | 1 | 1 | 14:05 | 34:25 | 35:20 | 3:50 | 39:10 | 105:40 | 53:15 | 53:15 | 94.5602 | 92.6042 | 140:05 | 140:05 | 95.1618 | 93.5859
44 | Yaragatti | 1 | 1 | 8:50 | 24:59 | 34:20 | 9:47 | 44:07 | 139:13 | 52:57 | 52:57 | 93.8727 | 92.6458 | 164:12 | 164:12 | 93.6256 | 92.4817
45 | Ramdurg | 2 | 2 | 2:00 | 13:46 | 34:45 | 11:05 | 45:50 | 150:15 | 47:50 | 23:55 | 96.8171 | 96.6782 | 164:01 | 82:00 | 96.5602 | 96.245
46 | Gokak | 10 | 10 | 30:04 | 170:12 | 13:47 | 14:39 | 28:26 | 144:34 | 58:30 | 5:51 | 99.6051 | 99.1875 | 314:46 | 31:29 | 99.3381 | 98.5588
47 | Mudalagi | 2 | 2 | 1:10 | 2:45 | 31:50 | 5:00 | 36:50 | 170:25 | 38:00 | 19:00 | 97.4421 | 97.3611 | 173:10 | 86:35 | 96.0985 | 96.0356
48 | Konnur | 1 | 1 | 0:40 | 2:10 | 19:15 | 1:50 | 21:05 | 81:55 | 21:45 | 21:45 | 97.0718 | 96.9792 | 84:05 | 84:05 | 96.2492 | 96.15
49 | Raibag | 1 | 1 | 0:00 | 0:00 | 15:05 | 13:00 | 28:05 | 136:20 | 28:05 | 28:05 | 96.0995 | 96.0995 | 136:20 | 136:20 | 93.7576 | 93.7576
50 | Kudachi | 1 | 1 | 0:00 | 0:40 | 43:55 | 1:25 | 45:20 | 187:35 | 45:20 | 45:20 | 93.7037 | 93.7037 | 188:15 | 188:15 | 91.411 | 91.3805
51 | Athani | 7 | 7 | 26:21 | 123:45 | 41:04 | 83:43 | 124:47 | 668:31 | 151:08 | 21:35 | 97.5241 | 97.0013 | 792:16 | 113:11 | 95.6272 | 94.8177
52 | Chikkodi | 4 | 4 | 0:00 | 0:00 | 19:17 | 9:38 | 28:55 | 103:35 | 28:55 | 7:14 | 98.9959 | 98.9959 | 103:35 | 25:54 | 98.8143 | 98.8143
53 | Nippani | 5 | 5 | 0:00 | 0:00 | 94:00 | 37:35 | 131:35 | 434:12 | 131:35 | 26:19 | 96.3449 | 96.3449 | 434:12 | 86:50 | 96.0238 | 96.0238
54 | Sadalaga | 1 | 1 | 1:50 | 16:55 | 22:25 | 3:30 | 25:55 | 80:15 | 27:45 | 27:45 | 96.4005 | 96.1458 | 97:10 | 97:10 | 96.3255 | 95.551
55 | Muddebihal | 2 | 2 | 0:55 | 16:10 | 52:55 | 21:50 | 74:45 | 246:10 | 75:40 | 37:50 | 94.809 | 94.7454 | 262:20 | 131:10 | 94.3643 | 93.9942
56 | Talikoti | 1 | 1 | 4:30 | 16:45 | 40:25 | 19:40 | 60:05 | 123:40 | 64:35 | 64:35 | 91.6551 | 91.0301 | 140:25 | 140:25 | 94.3376 | 93.5707
57 | B.Bagewadi | 1 | 1 | 0:31 | 9:53 | 12:54 | 4:38 | 17:32 | 56:48 | 18:03 | 18:03 | 97.5648 | 97.4931 | 66:41 | 66:41 | 97.3993 | 96.9467
58 | Indi | 3 | 3 | 0:13 | 45:35 | 33:28 | 8:07 | 41:35 | 118:37 | 41:48 | 13:56 | 98.0748 | 98.0648 | 164:12 | 54:44 | 98.1896 | 97.4939
59 | Sindagi | 2 | 2 | 33:00 | 57:00 | 23:10 | 12:10 | 35:20 | 134:35 | 68:20 | 34:10 | 97.5463 | 95.2546 | 191:35 | 95:48 | 96.9189 | 95.6139
60 | Guledgudda | 1 | 1 | 0:10 | 1:01 | 21:21 | 10:10 | 31:31 | 65:22 | 31:41 | 31:41 | 95.6227 | 95.5995 | 66:23 | 66:23 | 97.007 | 96.9605
61 | Ilkal | 7 | 7 | 5:20 | 45:02 | 62:20 | 177:23 | 239:43 | 638:49 | 245:03 | 35:00 | 95.2437 | 95.1379 | 683:51 | 97:42 | 95.8215 | 95.5269
62 | Kerur | 1 | 1 | 8:47 | 11:32 | 24:59 | 17:56 | 42:55 | 142:47 | 51:42 | 51:42 | 94.0394 | 92.8194 | 154:19 | 154:19 | 93.4623 | 92.9342
63 | Hungund | 4 | 4 | 8:00 | 27:47 | 56:17 | 51:08 | 107:25 | 399:33 | 115:25 | 28:51 | 96.2703 | 95.9925 | 427:20 | 106:50 | 95.4264 | 95.1084
64 | Badami | 1 | 1 | 8:08 | 11:02 | 11:42 | 17:15 | 28:57 | 80:19 | 37:05 | 37:05 | 95.9792 | 94.8495 | 91:21 | 91:21 | 96.3225 | 95.8173
65 | Jamkhandi | 6 | 6 | 12:35 | 21:45 | 70:20 | 20:45 | 91:05 | 447:25 | 103:40 | 17:17 | 97.8916 | 97.6003 | 469:10 | 78:12 | 96.5856 | 96.4197
66 | Mahalingapur | 2 | 2 | 3:25 | 6:41 | 24:43 | 5:31 | 30:14 | 126:30 | 33:39 | 16:50 | 97.9005 | 97.6632 | 133:11 | 66:36 | 97.1039 | 96.9509
67 | Rannabelagali | 1 | 1 | 1:05 | 7:19 | 19:25 | 8:45 | 28:10 | 71:48 | 29:15 | 29:15 | 96.088 | 95.9375 | 79:07 | 79:07 | 96.7125 | 96.3774
68 | Rabakavi | 2 | 2 | 19:00 | 25:45 | 12:30 | 7:05 | 19:35 | 87:10 | 38:35 | 19:18 | 98.64 | 97.3206 | 112:55 | 56:27 | 98.0044 | 97.4149
69 | Banahatti | 2 | 2 | 2:20 | 6:30 | 57:40 | 10:25 | 68:05 | 134:50 | 70:25 | 35:12 | 95.272 | 95.11 | 141:20 | 70:40 | 96.9132 | 96.7643
70 | Terdal | 2 | 2 | 0:00 | 18:30 | 23:40 | 4:00 | 27:40 | 143:22 | 27:40 | 13:50 | 98.0787 | 98.0787 | 161:52 | 80:56 | 96.7178 | 96.2943
71 | Mudhol | 4 | 4 | 13:25 | 57:45 | 49:27 | 32:42 | 82:09 | 277:49 | 95:34 | 23:54 | 97.1476 | 96.6817 | 335:34 | 83:54 | 96.8199 | 96.1588
72 | Bilagi | 1 | 1 | 1:17 | 4:32 | 22:30 | 3:45 | 26:15 | 80:10 | 27:32 | 27:32 | 96.3542 | 96.1759 | 84:42 | 84:42 | 96.3294 | 96.1218
73 | Lokapur | 2 | 2 | 2:50 | 3:15 | 66:10 | 51:30 | 117:40 | 271:05 | 120:30 | 60:15 | 91.8287 | 91.6319 | 274:20 | 137:10 | 93.7939 | 93.7195
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of July-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2022 |  |  |  | Reliability for cumulative period from Apr-22 to July-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 80 | 80 | 35:26 | 287:17 | 226:54 | 271:28 | 498:22 | 2914:25 | 533:48 | 6:40 | 99.1627 | 99.1032 | 3201:42 | 40:01 | 98.7558 | 98.6332
2 | Dharwad(R) | 14 | 14 | 21:32 | 36:32 | 159:38 | 121:28 | 281:06 | 1107:36 | 302:38 | 21:37 | 97.3013 | 97.0945 | 1144:08 | 81:43 | 97.298 | 97.2089
3 | Kundagol | 1 | 1 | 1:25 | 75:35 | 5:20 | 2:25 | 7:45 | 42:40 | 9:10 | 9:10 | 98.9583 | 98.7679 | 118:15 | 118:15 | 98.5428 | 95.9614
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 13:22 | 18:50 | 32:12 | 106:31 | 32:12 | 32:12 | 95.672 | 95.672 | 106:31 | 106:31 | 96.3621 | 96.3621
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 10:40 | 5:25 | 16:05 | 105:02 | 16:05 | 16:05 | 97.8383 | 97.8383 | 105:02 | 105:02 | 96.4128 | 96.4128
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 7:35 | 32:15 | 39:50 | 211:00 | 39:50 | 19:55 | 97.323 | 97.323 | 211:00 | 105:30 | 96.3969 | 96.3969
7 | Alnavar | 2 | 2 | 0:00 | 0:00 | 10:50 | 9:00 | 19:50 | 133:25 | 19:50 | 9:55 | 98.6671 | 98.6671 | 133:25 | 66:42 | 97.7217 | 97.7217
8 | Naragund | 2 | 2 | 3:20 | 41:00 | 27:45 | 24:00 | 51:45 | 203:25 | 55:05 | 27:32 | 96.5222 | 96.2982 | 244:25 | 122:13 | 96.5264 | 95.8262
9 | Shirahatti | 1 | 1 | 0:00 | 0:00 | 3:40 | 7:30 | 11:10 | 74:40 | 11:10 | 11:10 | 98.4991 | 98.4991 | 74:40 | 74:40 | 97.4499 | 97.4499
10 | Laxmeshwar | 3 | 3 | 0:00 | 0:00 | 44:20 | 18:25 | 62:45 | 302:20 | 62:45 | 20:55 | 97.1886 | 97.1886 | 302:20 | 100:47 | 96.5581 | 96.5581
11 | Naregal | 1 | 1 | 2:30 | 5:20 | 2:25 | 5:25 | 7:50 | 53:15 | 10:20 | 10:20 | 98.9471 | 98.6111 | 58:35 | 58:35 | 98.1814 | 97.9992
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 15:05 | 13:55 | 29:00 | 153:10 | 29:00 | 14:30 | 98.0511 | 98.0511 | 153:10 | 76:35 | 97.3844 | 97.3844
13 | Ron | 3 | 3 | 0:00 | 0:00 | 52:42 | 15:05 | 67:47 | 279:01 | 67:47 | 22:36 | 96.9631 | 96.9631 | 279:01 | 93:00 | 96.8236 | 96.8236
14 | Mundaragi | 1 | 1 | 0:00 | 0:00 | 7:25 | 11:35 | 19:00 | 129:15 | 19:00 | 19:00 | 97.4462 | 97.4462 | 129:15 | 129:15 | 95.5857 | 95.5857
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 13:06 | 21:03 | 34:09 | 299:25 | 34:09 | 34:09 | 95.4099 | 95.4099 | 299:25 | 299:25 | 89.774 | 89.774
16 | Savanur | 2 | 2 | 0:20 | 4:35 | 7:25 | 17:05 | 24:30 | 134:55 | 24:50 | 12:25 | 98.3535 | 98.3311 | 139:30 | 69:45 | 97.6961 | 97.6178
17 | Shiggaon | 3 | 3 | 29:25 | 120:35 | 12:15 | 20:20 | 32:35 | 257:05 | 62:00 | 20:40 | 98.5402 | 97.2222 | 377:40 | 125:53 | 97.0733 | 95.7005
18 | Bankapur | 1 | 1 | 6:35 | 54:00 | 26:20 | 19:15 | 45:35 | 176:35 | 52:10 | 52:10 | 93.8732 | 92.9884 | 230:35 | 230:35 | 93.9691 | 92.1249
19 | Hangal | 2 | 2 | 0:10 | 10:14 | 31:30 | 42:55 | 74:25 | 240:50 | 74:35 | 37:18 | 94.9989 | 94.9877 | 251:04 | 125:32 | 95.8874 | 95.7127
20 | Ranebennur | 10 | 10 | 0:00 | 42:33 | 34:29 | 67:45 | 102:14 | 620:04 | 102:14 | 10:13 | 98.6259 | 98.6259 | 662:37 | 66:16 | 97.8823 | 97.737
21 | Tuminakatti | 1 | 1 | 0:15 | 4:20 | 13:05 | 6:55 | 20:00 | 108:55 | 20:15 | 20:15 | 97.3118 | 97.2782 | 113:15 | 113:15 | 96.2802 | 96.1322
22 | Rattihalli | 1 | 1 | 0:20 | 8:05 | 21:20 | 6:55 | 28:15 | 111:25 | 28:35 | 28:35 | 96.203 | 96.1582 | 119:30 | 119:30 | 96.1948 | 95.9187
23 | Hirekerur | 1 | 1 | 0:05 | 6:40 | 11:40 | 7:45 | 19:25 | 112:30 | 19:30 | 19:30 | 97.3902 | 97.379 | 119:10 | 119:10 | 96.1578 | 95.9301
24 | Byadagi | 5 | 5 | 24:35 | 148:46 | 83:15 | 31:25 | 114:40 | 405:43 | 139:15 | 27:51 | 96.9176 | 96.2567 | 554:29 | 110:54 | 97.2287 | 96.2125
25 | Sirsi | 6 | 6 | 30:02 | 130:44 | 28:31 | 29:06 | 57:37 | 281:01 | 87:39 | 14:36 | 98.7093 | 98.0365 | 411:45 | 68:38 | 98.4004 | 97.6562
26 | Yellapur | 1 | 1 | 8:30 | 42:20 | 6:20 | 9:20 | 15:40 | 49:00 | 24:10 | 24:10 | 97.8943 | 96.7518 | 91:20 | 91:20 | 98.3265 | 96.8807
27 | Mundagod | 1 | 1 | 0:35 | 2:15 | 3:40 | 2:30 | 6:10 | 52:30 | 6:45 | 6:45 | 99.1711 | 99.0927 | 54:45 | 54:45 | 98.207 | 98.1301
28 | Siddapur | 1 | 1 | 7:20 | 36:00 | 5:25 | 5:30 | 10:55 | 53:30 | 18:15 | 18:15 | 98.5327 | 97.547 | 89:30 | 89:30 | 98.1728 | 96.9433
29 | Dandeli | 7 | 7 | 22:22 | 48:06 | 58:46 | 56:38 | 115:24 | 366:51 | 137:46 | 19:41 | 97.7842 | 97.3547 | 414:57 | 59:17 | 98.2101 | 97.9755
30 | Haliyal | 2 | 2 | 0:32 | 6:08 | 8:25 | 11:35 | 20:00 | 108:55 | 20:32 | 10:16 | 98.6559 | 98.6201 | 115:03 | 57:32 | 98.1401 | 98.0353
31 | Ankola | 3 | 3 | 15:42 | 97:29 | 13:43 | 31:13 | 44:56 | 171:42 | 60:38 | 20:13 | 97.9869 | 97.2835 | 269:11 | 89:44 | 98.0453 | 96.9355
32 | Kumta | 3 | 3 | 0:00 | 24:18 | 37:09 | 36:27 | 73:36 | 192:13 | 73:36 | 24:32 | 96.7025 | 96.7025 | 216:31 | 72:10 | 97.8117 | 97.5351
33 | Gokarna | 1 | 1 | 7:05 | 53:02 | 5:00 | 6:55 | 11:55 | 30:15 | 19:00 | 19:00 | 98.3983 | 97.4462 | 83:17 | 83:17 | 98.9669 | 97.1556
34 | Kasarkod | 1 | 1 | 24:37 | 78:06 | 17:38 | 28:00 | 45:38 | 87:23 | 70:15 | 70:15 | 93.8665 | 90.5578 | 165:29 | 165:29 | 97.0156 | 94.3482
35 | Honnavar | 3 | 3 | 1:24 | 48:24 | 68:32 | 39:31 | 108:03 | 261:10 | 109:27 | 36:29 | 95.1591 | 95.0963 | 309:34 | 103:11 | 97.0268 | 96.4758
36 | Murdeshwar | 4 | 4 | 1:52 | 69:12 | 48:27 | 28:34 | 77:01 | 272:24 | 78:53 | 19:43 | 97.4121 | 97.3494 | 341:36 | 85:24 | 97.6742 | 97.0833
37 | Bhatkal | 3 | 3 | 7:57 | 92:06 | 27:03 | 20:46 | 47:49 | 145:39 | 55:46 | 18:35 | 97.8577 | 97.5015 | 237:45 | 79:15 | 98.3419 | 97.2934
38 | Khanapur | 2 | 2 | 3:45 | 40:10 | 57:20 | 34:40 | 92:00 | 264:35 | 95:45 | 47:52 | 93.8172 | 93.5652 | 304:45 | 152:22 | 95.4818 | 94.7959
39 | Bailhongal | 3 | 3 | 0:00 | 0:00 | 33:00 | 10:15 | 43:15 | 310:05 | 43:15 | 14:25 | 98.0623 | 98.0623 | 310:05 | 103:22 | 96.4699 | 96.4699
40 | Kittur | 1 | 1 | 1:45 | 2:30 | 11:35 | 1:20 | 12:55 | 84:50 | 14:40 | 14:40 | 98.2639 | 98.0287 | 87:20 | 87:20 | 97.1027 | 97.0173
41 | M K Hubli | 1 | 1 | 0:00 | 0:45 | 10:20 | 11:55 | 22:15 | 92:05 | 22:15 | 22:15 | 97.0094 | 97.0094 | 92:50 | 92:50 | 96.8551 | 96.8295
42 | Soundatti | 3 | 3 | 0:13 | 22:40 | 21:03 | 10:04 | 31:07 | 167:10 | 31:20 | 10:27 | 98.6059 | 98.5962 | 189:50 | 63:17 | 98.0969 | 97.8389
43 | Munavalli | 1 | 1 | 2:10 | 36:35 | 31:45 | 13:25 | 45:10 | 150:50 | 47:20 | 47:20 | 93.9292 | 93.638 | 187:25 | 187:25 | 94.8486 | 93.5992
44 | Yaragatti | 1 | 1 | 9:22 | 34:21 | 36:48 | 6:42 | 43:30 | 182:43 | 52:52 | 52:52 | 94.1532 | 92.8943 | 217:04 | 217:04 | 93.7597 | 92.5865
45 | Ramdurg | 2 | 2 | 1:00 | 14:46 | 15:15 | 6:15 | 21:30 | 171:45 | 22:30 | 11:15 | 98.5551 | 98.4879 | 186:31 | 93:16 | 97.0671 | 96.8149
46 | Gokak | 10 | 10 | 27:24 | 197:36 | 10:20 | 23:09 | 33:29 | 178:03 | 60:53 | 6:05 | 99.55 | 99.1817 | 375:39 | 37:34 | 99.3919 | 98.717
47 | Mudalagi | 2 | 2 | 0:50 | 3:35 | 23:35 | 9:20 | 32:55 | 203:20 | 33:45 | 16:52 | 97.7879 | 97.7319 | 206:55 | 103:28 | 96.5278 | 96.4666
48 | Konnur | 1 | 1 | 0:00 | 2:10 | 21:30 | 8:50 | 30:20 | 112:15 | 30:20 | 30:20 | 95.9229 | 95.9229 | 114:25 | 114:25 | 96.1663 | 96.0923
49 | Raibag | 1 | 1 | 0:00 | 0:00 | 21:35 | 13:15 | 34:50 | 171:10 | 34:50 | 34:50 | 95.3181 | 95.3181 | 171:10 | 171:10 | 94.1541 | 94.1541
50 | Kudachi | 1 | 1 | 0:00 | 0:40 | 41:00 | 1:35 | 42:35 | 230:10 | 42:35 | 42:35 | 94.2764 | 94.2764 | 230:50 | 230:50 | 92.1391 | 92.1163
51 | Athani | 7 | 7 | 17:33 | 141:18 | 50:23 | 92:03 | 142:26 | 810:57 | 159:59 | 22:51 | 97.2651 | 96.9281 | 952:15 | 136:02 | 96.0434 | 95.354
52 | Chikkodi | 4 | 4 | 0:00 | 0:00 | 20:24 | 11:07 | 31:31 | 135:06 | 31:31 | 7:53 | 98.941 | 98.941 | 135:06 | 33:46 | 98.8465 | 98.8465
53 | Nippani | 5 | 5 | 0:00 | 0:00 | 50:20 | 49:40 | 100:00 | 534:12 | 100:00 | 20:00 | 97.3118 | 97.3118 | 534:12 | 106:50 | 96.3511 | 96.3511
54 | Sadalaga | 1 | 1 | 5:28 | 22:23 | 22:35 | 12:35 | 35:10 | 115:25 | 40:38 | 40:38 | 95.2733 | 94.5385 | 137:48 | 137:48 | 96.0582 | 95.2937
55 | Muddebihal | 2 | 2 | 13:45 | 29:55 | 42:45 | 25:00 | 67:45 | 313:55 | 81:30 | 40:45 | 95.4469 | 94.5228 | 343:50 | 171:55 | 94.6394 | 94.1285
56 | Talikoti | 1 | 1 | 7:15 | 24:00 | 41:40 | 13:50 | 55:30 | 179:10 | 62:45 | 62:45 | 92.5403 | 91.5659 | 203:10 | 203:10 | 93.8809 | 93.0612
57 | B.Bagewadi | 1 | 1 | 4:21 | 14:14 | 3:45 | 3:37 | 7:22 | 64:10 | 11:43 | 11:43 | 99.0099 | 98.4252 | 78:24 | 78:24 | 97.8085 | 97.3224
58 | Indi | 3 | 3 | 2:27 | 48:02 | 10:15 | 5:52 | 16:07 | 134:44 | 18:34 | 6:11 | 99.2779 | 99.1682 | 182:46 | 60:55 | 98.4662 | 97.9193
59 | Sindagi | 2 | 2 | 11:50 | 68:50 | 39:30 | 23:10 | 62:40 | 197:15 | 74:30 | 37:15 | 95.7885 | 94.9933 | 266:05 | 133:03 | 96.6317 | 95.4562
60 | Guledgudda | 1 | 1 | 4:49 | 5:50 | 12:03 | 5:27 | 17:30 | 82:52 | 22:19 | 22:19 | 97.6478 | 97.0004 | 88:42 | 88:42 | 97.1699 | 96.9706
61 | Ilkal | 7 | 7 | 17:10 | 62:12 | 52:38 | 125:43 | 178:21 | 817:10 | 195:31 | 27:56 | 96.5755 | 96.2458 | 879:22 | 125:37 | 96.013 | 95.7096
62 | Kerur | 1 | 1 | 0:30 | 12:02 | 13:56 | 4:49 | 18:45 | 161:32 | 19:15 | 19:15 | 97.4798 | 97.4126 | 173:34 | 173:34 | 94.4832 | 94.0722
63 | Hungund | 4 | 4 | 11:16 | 39:03 | 53:24 | 48:32 | 101:56 | 501:29 | 113:12 | 28:18 | 96.5748 | 96.1962 | 540:32 | 135:08 | 95.7182 | 95.3848
64 | Badami | 1 | 1 | 0:15 | 11:17 | 11:54 | 11:37 | 23:31 | 103:50 | 23:46 | 23:46 | 96.8392 | 96.8056 | 115:07 | 115:07 | 96.4538 | 96.0684
65 | Jamkhandi | 6 | 6 | 1:00 | 22:45 | 123:55 | 20:40 | 144:35 | 592:00 | 145:35 | 24:16 | 96.7611 | 96.7387 | 614:45 | 102:28 | 96.6302 | 96.5007
66 | Mahalingapur | 2 | 2 | 1:56 | 8:37 | 16:46 | 8:09 | 24:55 | 151:25 | 26:51 | 13:25 | 98.3255 | 98.1956 | 160:02 | 80:01 | 97.4143 | 97.2672
67 | Rannabelagali | 1 | 1 | 0:15 | 7:34 | 11:05 | 12:15 | 23:20 | 95:08 | 23:35 | 23:35 | 96.8638 | 96.8302 | 102:42 | 102:42 | 96.7509 | 96.4925
68 | Rabakavi | 2 | 2 | 6:55 | 32:40 | 10:15 | 1:30 | 11:45 | 98:55 | 18:40 | 9:20 | 99.2103 | 98.7455 | 131:35 | 65:47 | 98.3108 | 97.753
69 | Banahatti | 2 | 2 | 0:00 | 6:30 | 26:40 | 11:10 | 37:50 | 172:40 | 37:50 | 18:55 | 97.4574 | 97.4574 | 179:10 | 89:35 | 97.0515 | 96.9405
70 | Terdal | 2 | 2 | 0:00 | 18:30 | 24:35 | 3:25 | 28:00 | 171:22 | 28:00 | 14:00 | 98.1183 | 98.1183 | 189:52 | 94:56 | 97.0737 | 96.7577
71 | Mudhol | 4 | 4 | 6:37 | 64:22 | 45:13 | 12:15 | 57:28 | 335:17 | 64:05 | 16:01 | 98.069 | 97.8467 | 399:39 | 99:55 | 97.1373 | 96.5877
72 | Bilagi | 1 | 1 | 1:50 | 6:22 | 28:08 | 5:20 | 33:28 | 113:38 | 35:18 | 35:18 | 95.5018 | 95.2554 | 120:00 | 120:00 | 96.1191 | 95.9016
73 | Lokapur | 2 | 2 | 1:00 | 4:15 | 57:05 | 25:30 | 82:35 | 353:40 | 83:35 | 41:48 | 94.45 | 94.3828 | 357:55 | 178:58 | 93.9606 | 93.888
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of Aug-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Aug-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Aug-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 81 | 81 | 162:17 | 449:34 | 456:42 | 309:26 | 766:08 | 3680:33 | 928:25 | 11:28 | 98.7287 | 98.4594 | 4130:07 | 50:59 | 98.7626 | 98.6114
2 | Dharwad(R) | 14 | 14 | 11:20 | 47:52 | 115:14 | 127:26 | 242:40 | 1350:16 | 254:00 | 18:09 | 97.6703 | 97.5614 | 1398:08 | 99:52 | 97.3734 | 97.2803
3 | Kundagol | 1 | 1 | 1:30 | 77:05 | 7:15 | 4:25 | 11:40 | 54:20 | 13:10 | 13:10 | 98.4319 | 98.2303 | 131:25 | 131:25 | 98.5203 | 96.4211
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 9:40 | 6:02 | 15:42 | 122:13 | 15:42 | 15:42 | 97.8898 | 97.8898 | 122:13 | 122:13 | 96.6717 | 96.6717
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 18:22 | 22:25 | 40:47 | 145:49 | 40:47 | 40:47 | 94.5184 | 94.5184 | 145:49 | 145:49 | 96.029 | 96.029
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 57:05 | 14:55 | 72:00 | 283:00 | 72:00 | 36:00 | 95.1613 | 95.1613 | 283:00 | 141:30 | 96.1465 | 96.1465
7 | Alnavar | 2 | 2 | 0:00 | 0:00 | 33:10 | 12:40 | 45:50 | 179:15 | 45:50 | 22:55 | 96.9198 | 96.9198 | 179:15 | 89:37 | 97.5592 | 97.5592
8 | Naragund | 2 | 2 | 4:20 | 45:20 | 27:15 | 17:50 | 45:05 | 248:30 | 49:25 | 24:42 | 96.9702 | 96.679 | 293:50 | 146:55 | 96.6163 | 95.999
9 | Shirahatti | 1 | 1 | 0:00 | 0:00 | 5:15 | 9:50 | 15:05 | 89:45 | 15:05 | 15:05 | 97.9727 | 97.9727 | 89:45 | 89:45 | 97.5558 | 97.5558
10 | Laxmeshwar | 3 | 3 | 0:00 | 0:00 | 15:44 | 16:28 | 32:12 | 334:32 | 32:12 | 10:44 | 98.5573 | 98.5573 | 334:32 | 111:31 | 96.9632 | 96.9632
11 | Naregal | 1 | 1 | 0:15 | 5:35 | 5:30 | 6:20 | 11:50 | 65:05 | 12:05 | 12:05 | 98.4095 | 98.3759 | 70:40 | 70:40 | 98.2276 | 98.0755
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 20:10 | 6:50 | 27:00 | 180:10 | 27:00 | 13:30 | 98.1855 | 98.1855 | 180:10 | 90:05 | 97.5468 | 97.5468
13 | Ron | 3 | 3 | 0:00 | 0:00 | 31:35 | 10:40 | 42:15 | 321:16 | 42:15 | 14:05 | 98.1071 | 98.1071 | 321:16 | 107:05 | 97.0836 | 97.0836
14 | Mundaragi | 1 | 1 | 0:00 | 0:00 | 2:00 | 9:30 | 11:30 | 140:45 | 11:30 | 11:30 | 98.4543 | 98.4543 | 140:45 | 140:45 | 96.1669 | 96.1669
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 25:08 | 41:17 | 66:25 | 365:50 | 66:25 | 66:25 | 91.073 | 91.073 | 365:50 | 365:50 | 90.0372 | 90.0372
16 | Savanur | 2 | 2 | 4:50 | 9:25 | 29:55 | 8:40 | 38:35 | 173:30 | 43:25 | 21:42 | 97.407 | 97.0822 | 182:55 | 91:28 | 97.6375 | 97.5093
17 | Shiggaon | 3 | 3 | 19:35 | 140:10 | 15:30 | 13:25 | 28:55 | 286:00 | 48:30 | 16:10 | 98.7045 | 97.8271 | 426:10 | 142:03 | 97.4038 | 96.1314
18 | Bankapur | 1 | 1 | 25:45 | 79:45 | 20:45 | 8:40 | 29:25 | 206:00 | 55:10 | 55:10 | 96.0461 | 92.5851 | 285:45 | 285:45 | 94.39 | 92.2181
19 | Hangal | 2 | 2 | 6:50 | 17:04 | 7:25 | 21:10 | 28:35 | 269:25 | 35:25 | 17:43 | 98.0791 | 97.6198 | 286:29 | 143:14 | 96.3315 | 96.0991
20 | Ranebennur | 10 | 10 | 4:30 | 47:03 | 93:48 | 65:13 | 159:01 | 779:05 | 163:31 | 16:21 | 97.8627 | 97.8022 | 826:08 | 82:37 | 97.8783 | 97.7502
21 | Tuminakatti | 1 | 1 | 1:00 | 5:20 | 12:10 | 0:20 | 12:30 | 121:25 | 13:30 | 13:30 | 98.3199 | 98.1855 | 126:45 | 126:45 | 96.6934 | 96.5482
22 | Rattihalli | 1 | 1 | 0:55 | 9:00 | 7:05 | 11:35 | 18:40 | 130:05 | 19:35 | 19:35 | 97.491 | 97.3678 | 139:05 | 139:05 | 96.4574 | 96.2123
23 | Hirekerur | 1 | 1 | 0:25 | 7:05 | 9:50 | 11:40 | 21:30 | 134:00 | 21:55 | 21:55 | 97.1102 | 97.0542 | 141:05 | 141:05 | 96.3508 | 96.1579
24 | Byadagi | 5 | 5 | 23:45 | 172:31 | 41:19 | 24:00 | 65:19 | 471:02 | 89:04 | 17:49 | 98.2442 | 97.6057 | 643:33 | 128:43 | 97.4345 | 96.4948
25 | Sirsi | 6 | 6 | 17:30 | 148:14 | 59:49 | 25:19 | 85:08 | 366:09 | 102:38 | 17:06 | 98.0929 | 97.7009 | 514:23 | 85:44 | 98.3381 | 97.6653
26 | Yellapur | 1 | 1 | 21:55 | 64:15 | 4:35 | 9:35 | 14:10 | 63:10 | 36:05 | 36:05 | 98.0959 | 95.1501 | 127:25 | 127:25 | 98.2798 | 96.53
27 | Mundagod | 1 | 1 | 0:52 | 3:07 | 12:00 | 4:25 | 16:25 | 68:55 | 17:17 | 17:17 | 97.7935 | 97.677 | 72:02 | 72:02 | 98.1232 | 98.0383
28 | Siddapur | 1 | 1 | 5:25 | 41:25 | 5:40 | 11:00 | 16:40 | 70:10 | 22:05 | 22:05 | 97.7599 | 97.0318 | 111:35 | 111:35 | 98.0891 | 96.9612
29 | Dandeli | 7 | 7 | 13:06 | 61:12 | 53:32 | 30:10 | 83:42 | 450:33 | 96:48 | 13:50 | 98.3929 | 98.1413 | 511:45 | 73:06 | 98.2472 | 98.0091
30 | Haliyal | 2 | 2 | 0:32 | 6:40 | 25:02 | 13:33 | 38:35 | 147:30 | 39:07 | 19:34 | 97.407 | 97.3712 | 154:10 | 77:05 | 97.9916 | 97.9008
31 | Ankola | 3 | 3 | 40:38 | 138:07 | 9:03 | 10:18 | 19:21 | 191:03 | 59:59 | 20:00 | 99.1331 | 97.3126 | 329:10 | 109:43 | 98.2657 | 97.0119
32 | Kumta | 3 | 3 | 1:27 | 25:45 | 14:18 | 9:37 | 23:55 | 216:08 | 25:22 | 8:27 | 98.9285 | 98.8635 | 241:53 | 80:38 | 98.038 | 97.8043
33 | Gokarna | 1 | 1 | 2:45 | 55:47 | 1:55 | 3:15 | 5:10 | 35:25 | 7:55 | 7:55 | 99.3056 | 98.9359 | 91:12 | 91:12 | 99.0355 | 97.5163
34 | Kasarkod | 1 | 1 | 9:31 | 87:37 | 10:10 | 5:40 | 15:50 | 103:13 | 25:21 | 25:21 | 97.8719 | 96.5927 | 190:50 | 190:50 | 97.1891 | 94.803
35 | Honnavar | 3 | 3 | 1:27 | 49:51 | 45:46 | 22:21 | 68:07 | 329:17 | 69:34 | 23:11 | 96.9482 | 96.8832 | 379:08 | 126:23 | 97.0109 | 96.5583
36 | Murdeshwar | 4 | 4 | 2:20 | 71:32 | 33:46 | 35:24 | 69:10 | 341:34 | 71:30 | 17:52 | 97.6759 | 97.5974 | 413:06 | 103:17 | 97.6745 | 97.1875
37 | Bhatkal | 3 | 3 | 16:15 | 108:21 | 23:04 | 22:24 | 45:28 | 191:07 | 61:43 | 20:34 | 97.963 | 97.2349 | 299:28 | 99:49 | 98.2651 | 97.2815
38 | Khanapur | 2 | 2 | 13:45 | 53:55 | 41:05 | 47:15 | 88:20 | 352:55 | 102:05 | 51:02 | 94.0636 | 93.1396 | 406:50 | 203:25 | 95.1945 | 94.4603
39 | Bailhongal | 3 | 3 | 1:45 | 1:45 | 43:40 | 26:20 | 70:00 | 380:05 | 71:45 | 23:55 | 96.8638 | 96.7854 | 381:50 | 127:17 | 96.5497 | 96.5338
40 | Kittur | 1 | 1 | 0:25 | 2:55 | 3:00 | 6:25 | 9:25 | 94:15 | 9:50 | 9:50 | 98.7343 | 98.6783 | 97:10 | 97:10 | 97.4333 | 97.3538
41 | M K Hubli | 1 | 1 | 0:00 | 0:45 | 22:10 | 8:40 | 30:50 | 122:55 | 30:50 | 30:50 | 95.8557 | 95.8557 | 123:40 | 123:40 | 96.6526 | 96.6322
42 | Soundatti | 3 | 3 | 3:09 | 25:49 | 26:03 | 12:59 | 39:02 | 206:12 | 42:11 | 14:04 | 98.2512 | 98.1101 | 232:01 | 77:20 | 98.1282 | 97.8938
43 | Munavalli | 1 | 1 | 2:40 | 39:15 | 45:55 | 5:20 | 51:15 | 202:05 | 53:55 | 53:55 | 93.1116 | 92.7531 | 241:20 | 241:20 | 94.4966 | 93.4277
44 | Yaragatti | 1 | 1 | 2:09 | 36:30 | 37:19 | 14:06 | 51:25 | 234:08 | 53:34 | 53:34 | 93.0892 | 92.8002 | 270:38 | 270:38 | 93.6238 | 92.6298
45 | Ramdurg | 2 | 2 | 0:50 | 15:36 | 15:20 | 3:40 | 19:00 | 190:45 | 19:50 | 9:55 | 98.7231 | 98.6671 | 206:21 | 103:10 | 97.4026 | 97.1902
46 | Gokak | 10 | 10 | 20:34 | 218:10 | 42:51 | 64:12 | 107:03 | 285:06 | 127:37 | 12:46 | 98.5612 | 98.2847 | 503:16 | 50:20 | 99.2236 | 98.6294
47 | Mudalagi | 2 | 2 | 1:00 | 4:35 | 38:25 | 9:55 | 48:20 | 251:40 | 49:20 | 24:40 | 96.7518 | 96.6846 | 256:15 | 128:08 | 96.5732 | 96.5108
48 | Konnur | 1 | 1 | 0:00 | 2:10 | 19:35 | 11:50 | 31:25 | 143:40 | 31:25 | 31:25 | 95.7773 | 95.7773 | 145:50 | 145:50 | 96.0875 | 96.0285
49 | Raibag | 1 | 1 | 0:00 | 0:00 | 25:27 | 33:10 | 58:37 | 229:47 | 58:37 | 58:37 | 92.1214 | 92.1214 | 229:47 | 229:47 | 93.7423 | 93.7423
50 | Kudachi | 1 | 1 | 0:20 | 1:00 | 49:40 | 19:15 | 68:55 | 299:05 | 69:15 | 69:15 | 90.737 | 90.6922 | 300:05 | 300:05 | 91.855 | 91.8278
51 | Athani | 7 | 7 | 39:33 | 180:51 | 59:20 | 133:11 | 192:31 | 1003:28 | 232:04 | 33:09 | 96.3034 | 95.544 | 1184:19 | 169:11 | 96.0961 | 95.3925
52 | Chikkodi | 4 | 4 | 16:20 | 16:20 | 33:07 | 15:47 | 48:54 | 184:00 | 65:14 | 16:18 | 98.3569 | 97.808 | 200:20 | 50:05 | 98.7473 | 98.6361
53 | Nippani | 5 | 5 | 0:00 | 0:00 | 99:50 | 21:10 | 121:00 | 655:12 | 121:00 | 24:12 | 96.7473 | 96.7473 | 655:12 | 131:02 | 96.4314 | 96.4314
54 | Sadalaga | 1 | 1 | 0:00 | 22:23 | 25:25 | 2:40 | 28:05 | 143:30 | 28:05 | 28:05 | 96.2254 | 96.2254 | 165:53 | 165:53 | 96.092 | 95.4825
55 | Muddebihal | 2 | 2 | 4:05 | 34:00 | 64:10 | 16:15 | 80:25 | 394:20 | 84:30 | 42:15 | 94.5957 | 94.3212 | 428:20 | 214:10 | 94.6305 | 94.1676
56 | Talikoti | 1 | 1 | 20:30 | 44:30 | 11:35 | 7:05 | 18:40 | 197:50 | 39:10 | 39:10 | 97.491 | 94.7357 | 242:20 | 242:20 | 94.6124 | 93.4005
57 | B.Bagewadi | 1 | 1 | 1:00 | 15:14 | 5:28 | 7:09 | 12:37 | 76:47 | 13:37 | 13:37 | 98.3042 | 98.1698 | 92:01 | 92:01 | 97.909 | 97.4941
58 | Indi | 3 | 3 | 36:36 | 84:38 | 12:39 | 6:31 | 19:10 | 153:54 | 55:46 | 18:35 | 99.1413 | 97.5015 | 238:32 | 79:31 | 98.6029 | 97.8347
59 | Sindagi | 2 | 2 | 39:40 | 108:30 | 36:50 | 26:05 | 62:55 | 260:10 | 102:35 | 51:18 | 95.7717 | 93.106 | 368:40 | 184:20 | 96.4574 | 94.98
60 | Guledgudda | 1 | 1 | 0:52 | 6:42 | 12:21 | 4:26 | 16:47 | 99:39 | 17:39 | 17:39 | 97.7442 | 97.6277 | 106:21 | 106:21 | 97.2862 | 97.1038
61 | Ilkal | 7 | 7 | 28:50 | 91:02 | 80:27 | 162:57 | 243:24 | 1060:34 | 272:14 | 38:53 | 95.3264 | 94.7728 | 1151:36 | 164:31 | 95.8739 | 95.5198
62 | Kerur | 1 | 1 | 4:07 | 16:09 | 20:41 | 4:23 | 25:04 | 186:36 | 29:11 | 29:11 | 96.6308 | 96.0775 | 202:45 | 202:45 | 94.9183 | 94.4785
63 | Hungund | 4 | 4 | 17:12 | 56:15 | 56:07 | 81:01 | 137:08 | 638:37 | 154:20 | 38:35 | 95.392 | 94.8141 | 694:52 | 173:43 | 95.6521 | 95.2692
64 | Badami | 1 | 1 | 2:03 | 13:20 | 8:40 | 9:59 | 18:39 | 122:29 | 20:42 | 20:42 | 97.4933 | 97.2177 | 135:49 | 135:49 | 96.6644 | 96.3013
65 | Jamkhandi | 6 | 6 | 11:00 | 33:45 | 52:40 | 25:05 | 77:45 | 669:45 | 88:45 | 14:48 | 98.2583 | 98.0119 | 703:30 | 117:15 | 96.9601 | 96.8069
66 | Mahalingapur | 2 | 2 | 5:19 | 13:56 | 47:34 | 4:28 | 52:02 | 203:27 | 57:21 | 28:40 | 96.5031 | 96.1458 | 217:23 | 108:42 | 97.2297 | 97.04
67 | Rannabelagali | 1 | 1 | 6:00 | 13:34 | 8:20 | 9:10 | 17:30 | 112:38 | 23:30 | 23:30 | 97.6478 | 96.8414 | 126:12 | 126:12 | 96.9326 | 96.5632
68 | Rabakavi | 2 | 2 | 5:40 | 38:20 | 13:15 | 8:55 | 22:10 | 121:05 | 27:50 | 13:55 | 98.5103 | 98.1295 | 159:25 | 79:42 | 98.3513 | 97.8293
69 | Banahatti | 2 | 2 | 1:30 | 8:00 | 24:30 | 5:25 | 29:55 | 202:35 | 31:25 | 15:42 | 97.9895 | 97.8887 | 210:35 | 105:18 | 97.2415 | 97.1326
70 | Terdal | 2 | 2 | 1:40 | 20:10 | 27:30 | 6:30 | 34:00 | 205:22 | 35:40 | 17:50 | 97.7151 | 97.603 | 225:32 | 112:46 | 97.2036 | 96.929
71 | Mudhol | 4 | 4 | 13:52 | 78:14 | 55:13 | 9:54 | 65:07 | 400:24 | 78:59 | 19:45 | 97.8119 | 97.346 | 478:38 | 119:40 | 97.274 | 96.7413
72 | Bilagi | 1 | 1 | 1:00 | 7:22 | 15:45 | 4:00 | 19:45 | 133:23 | 20:45 | 20:45 | 97.3454 | 97.211 | 140:45 | 140:45 | 96.3676 | 96.1669
73 | Lokapur | 2 | 2 | 0:00 | 4:15 | 56:45 | 18:20 | 75:05 | 428:45 | 75:05 | 37:32 | 94.9541 | 94.9541 | 433:00 | 216:30 | 94.1619 | 94.104
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of Sept-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Sept-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Sept-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 82 | 82 | 40:27 | 490:01 | 279:41 | 194:12 | 473:53 | 4154:26 | 514:20 | 6:16 | 99.1974 | 99.1288 | 4644:27 | 56:38 | 98.8465 | 98.7104
2 | Dharwad(R) | 14 | 14 | 23:25 | 71:17 | 117:24 | 65:18 | 182:42 | 1532:58 | 206:07 | 14:43 | 98.1875 | 97.9552 | 1604:15 | 114:35 | 97.5069 | 97.391
3 | Kundagol | 1 | 1 | 7:20 | 84:25 | 6:20 | 7:15 | 13:35 | 67:55 | 20:55 | 20:55 | 98.1134 | 97.0949 | 152:20 | 152:20 | 98.4536 | 96.5316
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 12:06 | 6:57 | 19:03 | 141:16 | 19:03 | 19:03 | 97.3542 | 97.3542 | 141:16 | 141:16 | 96.7835 | 96.7835
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 4:55 | 18:20 | 23:15 | 169:04 | 23:15 | 23:15 | 96.7708 | 96.7708 | 169:04 | 169:04 | 96.1506 | 96.1506
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 11:40 | 21:25 | 33:05 | 316:05 | 33:05 | 16:33 | 97.7025 | 97.7025 | 316:05 | 158:02 | 96.4016 | 96.4016
7 | Alnavar | 2 | 2 | 0:00 | 0:00 | 10:50 | 18:40 | 29:30 | 208:45 | 29:30 | 14:45 | 97.9514 | 97.9514 | 208:45 | 104:22 | 97.6235 | 97.6235
8 | Naragund | 2 | 2 | 13:30 | 58:50 | 24:30 | 8:20 | 32:50 | 281:20 | 46:20 | 23:10 | 97.7199 | 96.7824 | 340:10 | 170:05 | 96.7972 | 96.1274
9 | Shirahatti | 1 | 1 | 0:00 | 0:00 | 6:30 | 17:10 | 23:40 | 113:25 | 23:40 | 23:40 | 96.713 | 96.713 | 113:25 | 113:25 | 97.4177 | 97.4177
10 | Laxmeshwar | 3 | 3 | 0:00 | 0:00 | 66:17 | 22:35 | 88:52 | 423:24 | 88:52 | 29:37 | 95.8858 | 95.8858 | 423:24 | 141:08 | 96.7866 | 96.7866
11 | Naregal | 1 | 1 | 0:25 | 6:00 | 9:50 | 3:10 | 13:00 | 78:05 | 13:25 | 13:25 | 98.1944 | 98.1366 | 84:05 | 84:05 | 98.2221 | 98.0855
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 29:10 | 15:00 | 44:10 | 224:20 | 44:10 | 22:05 | 96.9329 | 96.9329 | 224:20 | 112:10 | 97.4461 | 97.4461
13 | Ron | 3 | 3 | 0:00 | 0:00 | 23:35 | 18:40 | 42:15 | 363:31 | 42:15 | 14:05 | 98.044 | 98.044 | 363:31 | 121:10 | 97.2411 | 97.2411
14 | Mundaragi | 1 | 1 | 0:00 | 0:00 | 13:35 | 15:15 | 28:50 | 169:35 | 28:50 | 28:50 | 95.9954 | 95.9954 | 169:35 | 169:35 | 96.1388 | 96.1388
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 44:06 | 42:35 | 86:41 | 452:31 | 86:41 | 86:41 | 87.9606 | 87.9606 | 452:31 | 452:31 | 89.6968 | 89.6968
16 | Savanur | 2 | 2 | 2:25 | 11:50 | 13:35 | 3:10 | 16:45 | 190:15 | 19:10 | 9:35 | 98.8368 | 98.669 | 202:05 | 101:02 | 97.8341 | 97.6994
17 | Shiggaon | 3 | 3 | 30:20 | 170:30 | 27:45 | 25:40 | 53:25 | 339:25 | 83:45 | 27:55 | 97.527 | 96.1227 | 509:55 | 169:58 | 97.424 | 96.13
18 | Bankapur | 1 | 1 | 9:45 | 89:30 | 15:10 | 11:55 | 27:05 | 233:05 | 36:50 | 36:50 | 96.2384 | 94.8843 | 322:35 | 322:35 | 94.693 | 92.6552
19 | Hangal | 2 | 2 | 1:40 | 18:44 | 26:25 | 11:20 | 37:45 | 307:10 | 39:25 | 19:42 | 97.3785 | 97.2627 | 325:54 | 162:57 | 96.5031 | 96.2898
20 | Ranebennur | 10 | 10 | 7:10 | 54:13 | 105:57 | 71:21 | 177:18 | 956:23 | 184:28 | 18:27 | 97.5375 | 97.438 | 1010:36 | 101:04 | 97.8224 | 97.699
21 | Tuminakatti | 1 | 1 | 1:20 | 6:40 | 23:10 | 0:20 | 23:30 | 144:55 | 24:50 | 24:50 | 96.7361 | 96.5509 | 151:35 | 151:35 | 96.7004 | 96.5486
22 | Rattihalli | 1 | 1 | 1:50 | 10:50 | 11:35 | 5:20 | 16:55 | 147:00 | 18:45 | 18:45 | 97.6505 | 97.3958 | 157:50 | 157:50 | 96.653 | 96.4063
23 | Hirekerur | 1 | 1 | 1:00 | 8:05 | 17:55 | 6:20 | 24:15 | 158:15 | 25:15 | 25:15 | 96.6319 | 96.4931 | 166:20 | 166:20 | 96.3969 | 96.2128
24 | Byadagi | 5 | 5 | 10:23 | 182:54 | 27:20 | 29:36 | 56:56 | 527:58 | 67:19 | 13:28 | 98.4185 | 98.1301 | 710:52 | 142:10 | 97.5958 | 96.7629
25 | Sirsi | 6 | 6 | 25:22 | 173:36 | 45:16 | 15:49 | 61:05 | 427:14 | 86:27 | 14:24 | 98.586 | 97.9988 | 600:50 | 100:08 | 98.3787 | 97.72
26 | Yellapur | 1 | 1 | 2:55 | 67:10 | 13:00 | 4:15 | 17:15 | 80:25 | 20:10 | 20:10 | 97.6042 | 97.1991 | 147:35 | 147:35 | 98.169 | 96.6397
27 | Mundagod | 1 | 1 | 0:15 | 3:22 | 16:50 | 4:25 | 21:15 | 90:10 | 21:30 | 21:30 | 97.0486 | 97.0139 | 93:32 | 93:32 | 97.947 | 97.8704
28 | Siddapur | 1 | 1 | 0:45 | 42:10 | 2:50 | 3:10 | 6:00 | 76:10 | 6:45 | 6:45 | 99.1667 | 99.0625 | 118:20 | 118:20 | 98.2658 | 97.3057
29 | Dandeli | 7 | 7 | 5:38 | 66:50 | 11:18 | 41:37 | 52:55 | 503:28 | 58:33 | 8:22 | 98.9501 | 98.8383 | 570:18 | 81:28 | 98.3624 | 98.145
30 | Haliyal | 2 | 2 | 0:48 | 7:28 | 7:49 | 7:10 | 14:59 | 162:29 | 15:47 | 7:54 | 98.9595 | 98.9039 | 169:57 | 84:58 | 98.1502 | 98.0652
31 | Ankola | 3 | 3 | 10:50 | 148:57 | 5:39 | 15:50 | 21:29 | 212:32 | 32:19 | 10:46 | 99.0054 | 98.5039 | 361:29 | 120:30 | 98.387 | 97.2565
32 | Kumta | 3 | 3 | 0:24 | 26:09 | 16:08 | 10:02 | 26:10 | 242:18 | 26:34 | 8:51 | 98.7886 | 98.7701 | 268:27 | 89:29 | 98.1611 | 97.9626
33 | Gokarna | 1 | 1 | 13:25 | 69:12 | 2:50 | 2:50 | 5:40 | 41:05 | 19:05 | 19:05 | 99.213 | 97.3495 | 110:17 | 110:17 | 99.0646 | 97.489
34 | Kasarkod | 1 | 1 | 12:32 | 100:09 | 9:25 | 6:15 | 15:40 | 118:53 | 28:12 | 28:12 | 97.8241 | 96.0833 | 219:02 | 219:02 | 97.2932 | 95.0129
35 | Honnavar | 3 | 3 | 0:24 | 50:15 | 43:05 | 22:22 | 65:27 | 394:44 | 65:51 | 21:57 | 96.9699 | 96.9514 | 444:59 | 148:20 | 97.0041 | 96.6228
36 | Murdeshwar | 4 | 4 | 0:36 | 72:08 | 22:41 | 15:59 | 38:40 | 380:14 | 39:16 | 9:49 | 98.6574 | 98.6366 | 452:22 | 113:06 | 97.8356 | 97.4251
37 | Bhatkal | 3 | 3 | 23:00 | 131:21 | 9:32 | 6:49 | 16:21 | 207:28 | 39:21 | 13:07 | 99.2431 | 98.1782 | 338:49 | 112:56 | 98.4254 | 97.4285
38 | Khanapur | 2 | 2 | 5:55 | 59:50 | 18:20 | 14:50 | 33:10 | 386:05 | 39:05 | 19:32 | 97.6968 | 97.2859 | 445:55 | 222:57 | 95.6047 | 94.9235
39 | Bailhongal | 3 | 3 | 0:30 | 2:15 | 13:35 | 15:55 | 29:30 | 409:35 | 30:00 | 10:00 | 98.6343 | 98.6111 | 411:50 | 137:17 | 96.8914 | 96.8744
40 | Kittur | 1 | 1 | 0:41 | 3:36 | 12:30 | 11:25 | 23:55 | 118:10 | 24:36 | 24:36 | 96.6782 | 96.5833 | 121:46 | 121:46 | 97.3095 | 97.2275
41 | M K Hubli | 1 | 1 | 0:00 | 0:45 | 15:55 | 4:10 | 20:05 | 143:00 | 20:05 | 20:05 | 97.2106 | 97.2106 | 143:45 | 143:45 | 96.7441 | 96.727
42 | Soundatti | 3 | 3 | 32:50 | 58:39 | 32:09 | 13:56 | 46:05 | 252:17 | 78:55 | 26:18 | 97.8665 | 96.3465 | 310:56 | 103:39 | 98.0853 | 97.6402
43 | Munavalli | 1 | 1 | 14:35 | 53:50 | 45:05 | 3:40 | 48:45 | 250:50 | 63:20 | 63:20 | 93.2292 | 91.2037 | 304:40 | 304:40 | 94.2889 | 93.0631
44 | Yaragatti | 1 | 1 | 2:17 | 38:47 | 41:36 | 13:06 | 54:42 | 288:50 | 56:59 | 56:59 | 92.4028 | 92.0856 | 327:37 | 327:37 | 93.4236 | 92.5406
45 | Ramdurg | 2 | 2 | 15:20 | 30:56 | 18:30 | 6:15 | 24:45 | 215:30 | 40:05 | 20:02 | 98.2812 | 97.2164 | 246:26 | 123:13 | 97.5467 | 97.1945
46 | Gokak | 10 | 10 | 18:48 | 236:58 | 9:21 | 26:20 | 35:41 | 320:47 | 54:29 | 5:27 | 99.5044 | 99.2433 | 557:45 | 55:47 | 99.2696 | 98.7301
47 | Mudalagi | 2 | 2 | 7:00 | 11:35 | 20:45 | 2:00 | 22:45 | 274:25 | 29:45 | 14:53 | 98.4201 | 97.934 | 286:00 | 143:00 | 96.8759 | 96.7441
48 | Konnur | 1 | 1 | 0:00 | 2:10 | 29:15 | 7:30 | 36:45 | 180:25 | 36:45 | 36:45 | 94.8958 | 94.8958 | 182:35 | 182:35 | 95.8922 | 95.8428
49 | Raibag | 1 | 1 | 0:00 | 0:00 | 28:33 | 3:25 | 31:58 | 261:45 | 31:58 | 31:58 | 95.5602 | 95.5602 | 261:45 | 261:45 | 94.0403 | 94.0403
50 | Kudachi | 1 | 1 | 0:00 | 1:00 | 49:00 | 7:00 | 56:00 | 355:05 | 56:00 | 56:00 | 92.2222 | 92.2222 | 356:05 | 356:05 | 91.9152 | 91.8925
51 | Athani | 7 | 7 | 13:51 | 194:42 | 89:12 | 47:28 | 136:40 | 1140:08 | 150:31 | 21:30 | 97.2884 | 97.0136 | 1334:50 | 190:41 | 96.2915 | 95.6582
52 | Chikkodi | 4 | 4 | 0:00 | 16:20 | 25:21 | 12:32 | 37:53 | 221:53 | 37:53 | 9:28 | 98.6846 | 98.6846 | 238:13 | 59:33 | 98.737 | 98.644
53 | Nippani | 5 | 5 | 0:00 | 0:00 | 24:50 | 15:50 | 40:40 | 695:52 | 40:40 | 8:08 | 98.8704 | 98.8704 | 695:52 | 139:10 | 96.8312 | 96.8312
54 | Sadalaga | 1 | 1 | 0:30 | 22:53 | 15:40 | 1:05 | 16:45 | 160:15 | 17:15 | 17:15 | 97.6736 | 97.6042 | 183:08 | 183:08 | 96.3513 | 95.8303
55 | Muddebihal | 2 | 2 | 0:10 | 34:10 | 49:05 | 18:05 | 67:10 | 461:30 | 67:20 | 33:40 | 95.3356 | 95.3241 | 495:40 | 247:50 | 94.7461 | 94.3572
56 | Talikoti | 1 | 1 | 3:10 | 47:40 | 19:30 | 5:15 | 24:45 | 222:35 | 27:55 | 27:55 | 96.5625 | 96.1227 | 270:15 | 270:15 | 94.9321 | 93.8468
57 | B.Bagewadi | 1 | 1 | 0:20 | 15:34 | 11:09 | 9:41 | 20:50 | 97:37 | 21:10 | 21:10 | 97.1065 | 97.0602 | 113:11 | 113:11 | 97.7774 | 97.423
58 | Indi | 3 | 3 | 0:10 | 84:48 | 4:43 | 10:17 | 15:00 | 168:54 | 15:10 | 5:03 | 99.3056 | 99.2978 | 253:42 | 84:34 | 98.7181 | 98.0745
59 | Sindagi | 2 | 2 | 1:00 | 109:30 | 23:35 | 11:35 | 35:10 | 295:20 | 36:10 | 18:05 | 97.5579 | 97.4884 | 404:50 | 202:25 | 96.6378 | 95.3912
60 | Guledgudda | 1 | 1 | 10:05 | 16:47 | 15:06 | 6:59 | 22:05 | 121:44 | 32:10 | 32:10 | 96.9329 | 95.5324 | 138:31 | 138:31 | 97.2283 | 96.8462
61 | Ilkal | 7 | 7 | 3:58 | 95:00 | 119:34 | 132:06 | 251:40 | 1312:14 | 255:38 | 36:31 | 95.0066 | 94.9279 | 1407:14 | 201:02 | 95.7317 | 95.4227
62 | Kerur | 1 | 1 | 0:00 | 16:09 | 29:11 | 9:43 | 38:54 | 225:30 | 38:54 | 38:54 | 94.5972 | 94.5972 | 241:39 | 241:39 | 94.8657 | 94.498
63 | Hungund | 4 | 4 | 1:30 | 57:45 | 71:32 | 52:43 | 124:15 | 762:52 | 125:45 | 31:26 | 95.6858 | 95.6337 | 820:37 | 205:09 | 95.6576 | 95.3289
64 | Badami | 1 | 1 | 2:00 | 15:20 | 10:40 | 10:44 | 21:24 | 143:53 | 23:24 | 23:24 | 97.0278 | 96.75 | 159:13 | 159:13 | 96.724 | 96.3748
65 | Jamkhandi | 6 | 6 | 5:35 | 39:20 | 120:05 | 27:50 | 147:55 | 817:40 | 153:30 | 25:35 | 96.576 | 96.4468 | 857:00 | 142:50 | 96.8971 | 96.7479
66 | Mahalingapur | 2 | 2 | 0:20 | 14:16 | 53:23 | 3:00 | 56:23 | 259:50 | 56:43 | 28:22 | 96.0845 | 96.0613 | 274:06 | 137:03 | 97.042 | 96.8796
67 | Rannabelagali | 1 | 1 | 2:58 | 16:32 | 18:00 | 1:50 | 19:50 | 132:28 | 22:48 | 22:48 | 97.2454 | 96.8333 | 149:00 | 149:00 | 96.9839 | 96.6075
68 | Rabakavi | 2 | 2 | 6:20 | 44:40 | 27:00 | 7:00 | 34:00 | 155:05 | 40:20 | 20:10 | 97.6389 | 97.1991 | 199:45 | 99:52 | 98.2345 | 97.726
69 | Banahatti | 2 | 2 | 0:00 | 8:00 | 47:35 | 9:20 | 56:55 | 259:30 | 56:55 | 28:28 | 96.0475 | 96.0475 | 267:30 | 133:45 | 97.0458 | 96.9547
70 | Terdal | 2 | 2 | 6:00 | 26:10 | 142:35 | 21:40 | 164:15 | 369:37 | 170:15 | 85:08 | 88.5938 | 88.1771 | 395:47 | 197:54 | 95.7922 | 95.4943
71 | Mudhol | 4 | 4 | 18:56 | 97:10 | 121:26 | 23:21 | 144:47 | 545:11 | 163:43 | 40:56 | 94.9728 | 94.3154 | 642:21 | 160:35 | 96.8967 | 96.3436
72 | Bilagi | 1 | 1 | 0:52 | 8:14 | 23:50 | 4:00 | 27:50 | 161:13 | 28:42 | 28:42 | 96.1343 | 96.0139 | 169:27 | 169:27 | 96.3293 | 96.1418
73 | Lokapur | 2 | 2 | 3:34 | 7:49 | 52:55 | 40:50 | 93:45 | 522:30 | 97:19 | 48:40 | 93.4896 | 93.2419 | 530:19 | 265:10 | 94.0517 | 93.9627
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of Oct-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Oct-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Oct-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 85 | 85 | 24:17 | 514:18 | 368:01 | 312:32 | 680:33 | 4834:59 | 704:50 | 8:18 | 98.9239 | 98.8855 | 5349:17 | 62:56 | 98.8925 | 98.7747
2 | Dharwad(R) | 14 | 14 | 9:25 | 80:42 | 107:17 | 51:43 | 159:00 | 1691:58 | 168:25 | 12:02 | 98.4735 | 98.3831 | 1772:40 | 126:37 | 97.6469 | 97.5347
3 | Kundagol | 1 | 1 | 8:32 | 92:57 | 11:40 | 3:00 | 14:40 | 82:35 | 23:12 | 23:12 | 98.0287 | 96.8817 | 175:32 | 175:32 | 98.3921 | 96.5823
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 1:44 | 9:56 | 11:40 | 152:56 | 11:40 | 11:40 | 98.4319 | 98.4319 | 152:56 | 152:56 | 97.0223 | 97.0223
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 7:05 | 7:30 | 14:35 | 183:39 | 14:35 | 14:35 | 98.0399 | 98.0399 | 183:39 | 183:39 | 96.4243 | 96.4243
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 23:05 | 43:05 | 66:10 | 382:15 | 66:10 | 33:05 | 95.5533 | 95.5533 | 382:15 | 191:08 | 96.2787 | 96.2787
7 | Alnavar | 2 | 2 | 0:00 | 0:00 | 8:20 | 13:30 | 21:50 | 230:35 | 21:50 | 10:55 | 98.5327 | 98.5327 | 230:35 | 115:18 | 97.7552 | 97.7552
8 | Naragund | 2 | 2 | 3:00 | 61:50 | 17:05 | 35:50 | 52:55 | 334:15 | 55:55 | 27:58 | 96.4438 | 96.2422 | 396:05 | 198:03 | 96.746 | 96.144
9 | Shirahatti | 1 | 1 | 0:00 | 0:00 | 5:20 | 10:50 | 16:10 | 129:35 | 16:10 | 16:10 | 97.8271 | 97.8271 | 129:35 | 129:35 | 97.477 | 97.477
10 | Laxmeshwar | 3 | 3 | 0:00 | 0:00 | 22:53 | 12:55 | 35:48 | 459:12 | 35:48 | 11:56 | 98.3961 | 98.3961 | 459:12 | 153:04 | 97.0197 | 97.0197
11 | Naregal | 1 | 1 | 1:10 | 7:10 | 4:55 | 2:00 | 6:55 | 85:00 | 8:05 | 8:05 | 99.0703 | 98.9135 | 92:10 | 92:10 | 98.345 | 98.2055
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 20:15 | 11:25 | 31:40 | 256:00 | 31:40 | 15:50 | 97.8719 | 97.8719 | 256:00 | 128:00 | 97.5078 | 97.5078
13 | Ron | 3 | 3 | 0:00 | 0:00 | 26:10 | 4:55 | 31:05 | 394:36 | 31:05 | 10:22 | 98.6074 | 98.6074 | 394:36 | 131:32 | 97.439 | 97.439
14 | Mundaragi | 1 | 1 | 0:50 | 0:50 | 7:10 | 13:25 | 20:35 | 190:10 | 21:25 | 21:25 | 97.2334 | 97.1214 | 191:00 | 191:00 | 96.2974 | 96.2812
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 12:45 | 21:00 | 33:45 | 486:16 | 33:45 | 33:45 | 95.4637 | 95.4637 | 486:16 | 486:16 | 90.5322 | 90.5322
16 | Savanur | 2 | 2 | 3:15 | 15:05 | 15:00 | 14:55 | 29:55 | 220:10 | 33:10 | 16:35 | 97.9895 | 97.7711 | 235:15 | 117:38 | 97.8566 | 97.7098
17 | Shiggaon | 3 | 3 | 21:30 | 192:00 | 12:10 | 24:25 | 36:35 | 376:00 | 58:05 | 19:22 | 98.361 | 97.3977 | 568:00 | 189:20 | 97.5597 | 96.3136
18 | Bankapur | 1 | 1 | 12:00 | 101:30 | 18:55 | 9:30 | 28:25 | 261:30 | 40:25 | 40:25 | 96.1806 | 94.5677 | 363:00 | 363:00 | 94.9085 | 92.9322
19 | Hangal | 2 | 2 | 33:20 | 52:04 | 30:45 | 18:00 | 48:45 | 355:55 | 82:05 | 41:03 | 96.7238 | 94.4836 | 407:59 | 204:00 | 96.5351 | 96.0282
20 | Ranebennur | 10 | 10 | 1:20 | 55:33 | 40:50 | 19:18 | 60:08 | 1016:31 | 61:28 | 6:09 | 99.1918 | 99.1738 | 1072:04 | 107:12 | 98.0208 | 97.9126
21 | Tuminakatti | 1 | 1 | 0:40 | 7:20 | 10:50 | 1:05 | 11:55 | 156:50 | 12:35 | 12:35 | 98.3983 | 98.3087 | 164:10 | 164:10 | 96.9464 | 96.8036
22 | Rattihalli | 1 | 1 | 0:25 | 11:15 | 12:45 | 5:20 | 18:05 | 165:05 | 18:30 | 18:30 | 97.5694 | 97.5134 | 176:20 | 176:20 | 96.7858 | 96.5667
23 | Hirekerur | 1 | 1 | 0:25 | 8:30 | 14:05 | 7:25 | 21:30 | 179:45 | 21:55 | 21:55 | 97.1102 | 97.0542 | 188:15 | 188:15 | 96.5002 | 96.3347
24 | Byadagi | 5 | 5 | 6:00 | 188:54 | 59:35 | 124:00 | 183:35 | 711:33 | 189:35 | 37:55 | 95.065 | 94.9037 | 900:27 | 180:05 | 97.2292 | 96.4936
25 | Sirsi | 6 | 6 | 0:00 | 173:36 | 74:20 | 6:52 | 81:12 | 508:26 | 81:12 | 13:32 | 98.181 | 98.181 | 682:02 | 113:40 | 98.3501 | 97.7868
26 | Yellapur | 1 | 1 | 1:50 | 69:00 | 2:00 | 3:50 | 5:50 | 86:15 | 7:40 | 7:40 | 99.2159 | 98.9695 | 155:15 | 155:15 | 98.3207 | 96.9772
27 | Mundagod | 1 | 1 | 0:10 | 3:32 | 2:15 | 3:40 | 5:55 | 96:05 | 6:05 | 6:05 | 99.2047 | 99.1823 | 99:37 | 99:37 | 98.1292 | 98.0604
28 | Siddapur | 1 | 1 | 12:45 | 54:55 | 3:20 | 6:30 | 9:50 | 86:00 | 22:35 | 22:35 | 98.6783 | 96.9646 | 140:55 | 140:55 | 98.3255 | 97.2563
29 | Dandeli | 7 | 7 | 18:01 | 84:51 | 68:19 | 67:59 | 136:18 | 639:46 | 154:19 | 22:03 | 97.3829 | 97.0369 | 724:37 | 103:31 | 98.2205 | 97.9845
30 | Haliyal | 2 | 2 | 0:44 | 8:12 | 7:50 | 6:35 | 14:25 | 176:54 | 15:09 | 7:34 | 99.0311 | 98.9819 | 185:06 | 92:33 | 98.2778 | 98.198
31 | Ankola | 3 | 3 | 7:18 | 156:15 | 6:31 | 6:49 | 13:20 | 225:52 | 20:38 | 6:53 | 99.4026 | 99.0756 | 382:07 | 127:22 | 98.5341 | 97.52
32 | Kumta | 3 | 3 | 1:12 | 27:21 | 3:03 | 5:35 | 8:38 | 250:56 | 9:50 | 3:17 | 99.6132 | 99.5594 | 278:17 | 92:46 | 98.3714 | 98.1939
33 | Gokarna | 1 | 1 | 6:55 | 76:07 | 1:15 | 1:35 | 2:50 | 43:55 | 9:45 | 9:45 | 99.6192 | 98.6895 | 120:02 | 120:02 | 99.1449 | 97.6629
34 | Kasarkod | 1 | 1 | 0:00 | 100:09 | 0:50 | 1:35 | 2:25 | 121:18 | 2:25 | 2:25 | 99.6752 | 99.6752 | 221:27 | 221:27 | 97.6382 | 95.6883
35 | Honnavar | 3 | 3 | 1:30 | 51:45 | 19:28 | 4:44 | 24:12 | 418:56 | 25:42 | 8:34 | 98.9158 | 98.8486 | 470:41 | 156:54 | 97.2811 | 96.9452
36 | Murdeshwar | 4 | 4 | 2:00 | 74:08 | 16:00 | 12:08 | 28:08 | 408:22 | 30:08 | 7:32 | 99.0547 | 98.9875 | 482:30 | 120:38 | 98.0122 | 97.6514
37 | Bhatkal | 3 | 3 | 28:21 | 159:42 | 16:21 | 2:43 | 19:04 | 226:32 | 47:25 | 15:48 | 99.1458 | 97.8756 | 386:14 | 128:45 | 98.5298 | 97.4933
38 | Khanapur | 2 | 2 | 1:30 | 61:20 | 8:20 | 12:25 | 20:45 | 406:50 | 22:15 | 11:08 | 98.6055 | 98.5047 | 468:10 | 234:05 | 96.0394 | 95.4423
39 | Bailhongal | 3 | 3 | 0:00 | 2:15 | 22:55 | 10:50 | 33:45 | 443:20 | 33:45 | 11:15 | 98.4879 | 98.4879 | 445:35 | 148:32 | 97.1227 | 97.1081
40 | Kittur | 1 | 1 | 0:00 | 3:36 | 15:32 | 4:35 | 20:07 | 138:17 | 20:07 | 20:07 | 97.2961 | 97.2961 | 141:53 | 141:53 | 97.3076 | 97.2375
41 | M K Hubli | 1 | 1 | 0:00 | 0:45 | 29:05 | 25:30 | 54:35 | 197:35 | 54:35 | 54:35 | 92.6635 | 92.6635 | 198:20 | 198:20 | 96.153 | 96.1384
42 | Soundatti | 3 | 3 | 0:30 | 59:09 | 27:46 | 8:33 | 36:19 | 288:36 | 36:49 | 12:16 | 98.3729 | 98.3505 | 347:45 | 115:55 | 98.1269 | 97.7431
43 | Munavalli | 1 | 1 | 0:00 | 53:50 | 32:55 | 6:25 | 39:20 | 290:10 | 39:20 | 39:20 | 94.7133 | 94.7133 | 344:00 | 344:00 | 94.3503 | 93.3022
44 | Yaragatti | 1 | 1 | 1:05 | 39:52 | 23:58 | 4:44 | 28:42 | 317:32 | 29:47 | 29:47 | 96.1425 | 95.9969 | 357:24 | 357:24 | 93.8175 | 93.0413
45 | Ramdurg | 2 | 2 | 1:30 | 32:26 | 15:00 | 7:05 | 22:05 | 237:35 | 23:35 | 11:48 | 98.5159 | 98.4151 | 270:01 | 135:00 | 97.6871 | 97.3713
46 | Gokak | 10 | 10 | 13:56 | 250:54 | 1:14 | 11:01 | 12:15 | 333:02 | 26:11 | 2:37 | 99.8353 | 99.6481 | 583:56 | 58:24 | 99.3516 | 98.8631
47 | Mudalagi | 2 | 2 | 3:10 | 14:45 | 34:40 | 9:20 | 44:00 | 318:25 | 47:10 | 23:35 | 97.043 | 96.8302 | 333:10 | 166:35 | 96.9001 | 96.7566
48 | Konnur | 1 | 1 | 0:00 | 2:10 | 11:55 | 2:25 | 14:20 | 194:45 | 14:20 | 14:20 | 98.0735 | 98.0735 | 196:55 | 196:55 | 96.2081 | 96.166
49 | Raibag | 1 | 1 | 0:00 | 0:00 | 23:35 | 18:30 | 42:05 | 303:50 | 42:05 | 42:05 | 94.3436 | 94.3436 | 303:50 | 303:50 | 94.0842 | 94.0842
50 | Kudachi | 1 | 1 | 0:20 | 1:20 | 37:00 | 0:45 | 37:45 | 392:50 | 38:05 | 38:05 | 94.9261 | 94.8813 | 394:10 | 394:10 | 92.3514 | 92.3254
51 | Athani | 7 | 7 | 12:09 | 206:51 | 74:00 | 85:06 | 159:06 | 1299:14 | 171:15 | 24:28 | 96.9451 | 96.7118 | 1506:05 | 215:09 | 96.3862 | 95.8108
52 | Chikkodi | 4 | 4 | 0:00 | 16:20 | 29:54 | 9:33 | 39:27 | 261:20 | 39:27 | 9:52 | 98.6744 | 98.6744 | 277:40 | 69:25 | 98.7279 | 98.6484
53 | Nippani | 5 | 5 | 0:00 | 0:00 | 39:10 | 23:35 | 62:45 | 758:37 | 62:45 | 12:33 | 98.3132 | 98.3132 | 758:37 | 151:43 | 97.0459 | 97.0459
54 | Sadalaga | 1 | 1 | 0:00 | 22:53 | 12:05 | 10:30 | 22:35 | 182:50 | 22:35 | 22:35 | 96.9646 | 96.9646 | 205:43 | 205:43 | 96.4402 | 95.9946
55 | Muddebihal | 2 | 2 | 2:55 | 37:05 | 37:45 | 6:05 | 43:50 | 505:20 | 46:45 | 23:22 | 97.0542 | 96.8582 | 542:25 | 271:13 | 95.0805 | 94.7195
56 | Talikoti | 1 | 1 | 7:45 | 55:25 | 19:30 | 14:40 | 34:10 | 256:45 | 41:55 | 41:55 | 95.4077 | 94.366 | 312:10 | 312:10 | 95.001 | 93.922
57 | B.Bagewadi | 1 | 1 | 1:14 | 16:48 | 8:14 | 2:36 | 10:50 | 108:27 | 12:04 | 12:04 | 98.5439 | 98.3781 | 125:15 | 125:15 | 97.8884 | 97.5613
58 | Indi | 3 | 3 | 0:00 | 84:48 | 6:03 | 5:37 | 11:40 | 180:34 | 11:40 | 3:53 | 99.4773 | 99.4773 | 265:22 | 88:27 | 98.8281 | 98.2777
59 | Sindagi | 2 | 2 | 9:50 | 119:20 | 24:50 | 6:45 | 31:35 | 326:55 | 41:25 | 20:42 | 97.8775 | 97.2166 | 446:15 | 223:08 | 96.8174 | 95.6557
60 | Guledgudda | 1 | 1 | 0:56 | 17:43 | 15:23 | 9:09 | 24:32 | 146:16 | 25:28 | 25:28 | 96.7025 | 96.5771 | 163:59 | 163:59 | 97.1521 | 96.8072
61 | Ilkal | 7 | 7 | 11:26 | 106:26 | 74:10 | 122:48 | 196:58 | 1509:12 | 208:24 | 29:46 | 96.218 | 95.9985 | 1615:38 | 230:48 | 95.8022 | 95.5061
62 | Kerur | 1 | 1 | 4:07 | 20:16 | 20:41 | 4:23 | 25:04 | 250:34 | 29:11 | 29:11 | 96.6308 | 96.0775 | 270:50 | 270:50 | 95.1214 | 94.7268
63 | Hungund | 4 | 4 | 6:10 | 63:55 | 43:33 | 53:05 | 96:38 | 859:30 | 102:48 | 25:42 | 96.7529 | 96.5457 | 923:25 | 230:51 | 95.8163 | 95.5052
64 | Badami | 1 | 1 | 0:25 | 15:45 | 2:57 | 14:45 | 17:42 | 161:35 | 18:07 | 18:07 | 97.621 | 97.565 | 177:20 | 177:20 | 96.8539 | 96.5472
65 | Jamkhandi | 6 | 6 | 0:00 | 39:20 | 48:35 | 32:20 | 80:55 | 898:35 | 80:55 | 13:29 | 98.1874 | 98.1874 | 937:55 | 156:19 | 97.084 | 96.9564
66 | Mahalingapur | 2 | 2 | 0:10 | 14:26 | 17:14 | 4:51 | 22:05 | 281:55 | 22:15 | 11:08 | 98.5159 | 98.5047 | 296:21 | 148:10 | 97.2555 | 97.115
67 | Rannabelagali | 1 | 1 | 0:00 | 16:32 | 13:20 | 1:07 | 14:27 | 146:55 | 14:27 | 14:27 | 98.0578 | 98.0578 | 163:27 | 163:27 | 97.1395 | 96.8176
68 | Rabakavi | 2 | 2 | 0:40 | 45:20 | 11:00 | 3:00 | 14:00 | 169:05 | 14:40 | 7:20 | 99.0591 | 99.0143 | 214:25 | 107:12 | 98.3539 | 97.9126
69 | Banahatti | 2 | 2 | 0:00 | 8:00 | 20:05 | 2:20 | 22:25 | 281:55 | 22:25 | 11:12 | 98.4935 | 98.4935 | 289:55 | 144:58 | 97.2555 | 97.1776
70 | Terdal | 2 | 2 | 0:00 | 26:10 | 17:45 | 11:35 | 29:20 | 398:57 | 29:20 | 14:40 | 98.0287 | 98.0287 | 425:07 | 212:34 | 96.1161 | 95.8614
71 | Mudhol | 4 | 4 | 3:11 | 100:21 | 120:39 | 21:19 | 141:58 | 687:09 | 145:09 | 36:17 | 95.2296 | 95.1226 | 787:30 | 196:52 | 96.6552 | 96.1668
72 | Bilagi | 1 | 1 | 1:56 | 10:10 | 18:25 | 7:00 | 25:25 | 186:38 | 27:21 | 27:21 | 96.5838 | 96.3239 | 196:48 | 196:48 | 96.3662 | 96.1682
73 | Lokapur | 2 | 2 | 0:00 | 7:49 | 47:00 | 23:10 | 70:10 | 592:40 | 70:10 | 35:05 | 95.2845 | 95.2845 | 600:29 | 300:14 | 94.2303 | 94.1542
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of Nov-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Nov-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Nov-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 85 | 85 | 38:49 | 553:07 | 92:08 | 200:50 | 292:58 | 5127:57 | 331:47 | 3:54 | 99.5213 | 99.4579 | 5681:04 | 66:50 | 98.9698 | 98.8587
2 | Dharwad(R) | 14 | 14 | 13:35 | 94:17 | 102:43 | 26:25 | 129:08 | 1821:06 | 142:43 | 10:12 | 98.7189 | 98.5842 | 1915:23 | 136:49 | 97.7787 | 97.6637
3 | Kundagol | 1 | 1 | 2:39 | 95:36 | 16:30 | 1:00 | 17:30 | 100:05 | 20:09 | 20:09 | 97.5694 | 97.2014 | 195:41 | 195:41 | 98.2909 | 96.6584
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 9:28 | 6:04 | 15:32 | 168:28 | 15:32 | 15:32 | 97.8426 | 97.8426 | 168:28 | 168:28 | 97.1232 | 97.1232
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 12:15 | 6:39 | 18:54 | 202:33 | 18:54 | 18:54 | 97.375 | 97.375 | 202:33 | 202:33 | 96.5412 | 96.5412
6 | Kalghatagi | 2 | 2 | 0:00 | 0:00 | 31:25 | 3:40 | 35:05 | 417:20 | 35:05 | 17:32 | 97.5637 | 97.5637 | 417:20 | 208:40 | 96.4367 | 96.4367
7 | Alnavar | 2 | 2 | 0:00 | 0:00 | 22:30 | 7:00 | 29:30 | 260:05 | 29:30 | 14:45 | 97.9514 | 97.9514 | 260:05 | 130:02 | 97.7793 | 97.7793
8 | Naragund | 2 | 2 | 3:10 | 65:00 | 38:10 | 28:55 | 67:05 | 401:20 | 70:15 | 35:08 | 95.3414 | 95.1215 | 466:20 | 233:10 | 96.5733 | 96.0183
9 | Shirahatti | 1 | 1 | 0:00 | 0:00 | 5:55 | 0:45 | 6:40 | 136:15 | 6:40 | 6:40 | 99.0741 | 99.0741 | 136:15 | 136:15 | 97.6733 | 97.6733
10 | Laxmeshwar | 3 | 3 | 0:00 | 0:00 | 4:22 | 4:04 | 8:26 | 467:38 | 8:26 | 2:49 | 99.6096 | 99.6096 | 467:38 | 155:53 | 97.3382 | 97.3382
11 | Naregal | 1 | 1 | 0:00 | 7:10 | 2:45 | 1:05 | 3:50 | 88:50 | 3:50 | 3:50 | 99.4676 | 99.4676 | 96:00 | 96:00 | 98.483 | 98.3607
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 14:55 | 4:15 | 19:10 | 275:10 | 19:10 | 9:35 | 98.669 | 98.669 | 275:10 | 137:35 | 97.6506 | 97.6506
13 | Ron | 3 | 3 | 0:00 | 0:00 | 15:20 | 5:00 | 20:20 | 414:56 | 20:20 | 6:47 | 99.0586 | 99.0586 | 414:56 | 138:19 | 97.6381 | 97.6381
14 | Mundaragi | 1 | 1 | 0:50 | 1:40 | 9:55 | 10:35 | 20:30 | 210:40 | 21:20 | 21:20 | 97.1528 | 97.037 | 212:20 | 212:20 | 96.4026 | 96.3741
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 16:48 | 4:55 | 21:43 | 507:59 | 21:43 | 21:43 | 96.9838 | 96.9838 | 507:59 | 507:59 | 91.3254 | 91.3254
16 | Savanur | 2 | 2 | 7:40 | 22:45 | 80:30 | 4:40 | 85:10 | 305:20 | 92:50 | 46:25 | 94.0856 | 93.5532 | 328:05 | 164:02 | 97.393 | 97.1987
17 | Shiggaon | 3 | 3 | 30:55 | 222:55 | 25:35 | 10:15 | 35:50 | 411:50 | 66:45 | 22:15 | 98.341 | 96.9097 | 634:45 | 211:35 | 97.6558 | 96.3869
18 | Bankapur | 1 | 1 | 17:00 | 118:30 | 12:30 | 12:20 | 24:50 | 286:20 | 41:50 | 41:50 | 96.5509 | 94.1898 | 404:50 | 404:50 | 95.1104 | 93.0869
19 | Hangal | 2 | 2 | 7:05 | 59:09 | 3:45 | 3:25 | 7:10 | 363:05 | 14:15 | 7:08 | 99.5023 | 99.0104 | 422:14 | 211:07 | 96.8999 | 96.3949
20 | Ranebennur | 10 | 10 | 2:40 | 58:13 | 55:53 | 15:12 | 71:05 | 1087:36 | 73:45 | 7:22 | 99.0127 | 98.9757 | 1145:49 | 114:35 | 98.1428 | 98.0433
21 | Tuminakatti | 1 | 1 | 0:35 | 7:55 | 19:10 | 1:00 | 20:10 | 177:00 | 20:45 | 20:45 | 97.1991 | 97.1181 | 184:55 | 184:55 | 96.9775 | 96.8423
22 | Rattihalli | 1 | 1 | 1:10 | 12:25 | 9:05 | 4:25 | 13:30 | 178:35 | 14:40 | 14:40 | 98.125 | 97.963 | 191:00 | 191:00 | 96.9504 | 96.7384
23 | Hirekerur | 1 | 1 | 0:10 | 8:40 | 16:10 | 2:10 | 18:20 | 198:05 | 18:30 | 18:30 | 97.4537 | 97.4306 | 206:45 | 206:45 | 96.6174 | 96.4694
24 | Byadagi | 5 | 5 | 10:15 | 199:09 | 69:49 | 29:43 | 99:32 | 811:05 | 109:47 | 21:57 | 97.2352 | 96.9505 | 1010:14 | 202:03 | 97.2299 | 96.5497
25 | Sirsi | 6 | 6 | 27:05 | 200:41 | 78:03 | 9:58 | 88:01 | 596:27 | 115:06 | 19:11 | 97.9626 | 97.3356 | 797:08 | 132:51 | 98.3025 | 97.7313
26 | Yellapur | 1 | 1 | 8:20 | 77:20 | 9:50 | 2:15 | 12:05 | 98:20 | 20:25 | 20:25 | 98.3218 | 97.1644 | 175:40 | 175:40 | 98.3208 | 97.0002
27 | Mundagod | 1 | 1 | 0:10 | 3:42 | 4:25 | 2:55 | 7:20 | 103:25 | 7:30 | 7:30 | 98.9815 | 98.9583 | 107:07 | 107:07 | 98.234 | 98.1708
28 | Siddapur | 1 | 1 | 6:55 | 61:50 | 1:20 | 1:35 | 2:55 | 88:55 | 9:50 | 9:50 | 99.5949 | 98.6343 | 150:45 | 150:45 | 98.4816 | 97.4257
29 | Dandeli | 7 | 7 | 3:56 | 88:47 | 77:57 | 60:41 | 138:38 | 778:24 | 142:34 | 20:22 | 97.2493 | 97.1713 | 867:11 | 123:53 | 98.1011 | 97.8845
30 | Haliyal | 2 | 2 | 0:44 | 8:56 | 4:20 | 1:35 | 5:55 | 182:49 | 6:39 | 3:20 | 99.5891 | 99.5382 | 191:45 | 95:52 | 98.4391 | 98.3628
31 | Ankola | 3 | 3 | 7:10 | 163:25 | 12:53 | 6:19 | 19:12 | 245:04 | 26:22 | 8:47 | 99.1111 | 98.7793 | 408:29 | 136:10 | 98.605 | 97.6748
32 | Kumta | 3 | 3 | 1:00 | 28:21 | 14:08 | 6:51 | 20:59 | 271:55 | 21:59 | 7:20 | 99.0285 | 98.9823 | 300:16 | 100:05 | 98.4522 | 98.2908
33 | Gokarna | 1 | 1 | 2:54 | 79:01 | 4:20 | 1:10 | 5:30 | 49:25 | 8:24 | 8:24 | 99.2361 | 98.8333 | 128:26 | 128:26 | 99.1561 | 97.8068
34 | Kasarkod | 1 | 1 | 25:22 | 125:31 | 5:03 | 4:49 | 9:52 | 131:10 | 35:14 | 35:14 | 98.6296 | 95.1065 | 256:41 | 256:41 | 97.7601 | 95.6167
35 | Honnavar | 3 | 3 | 1:51 | 53:36 | 19:17 | 4:37 | 23:54 | 442:50 | 25:45 | 8:35 | 98.8935 | 98.8079 | 496:26 | 165:29 | 97.4793 | 97.1742
36 | Murdeshwar | 4 | 4 | 2:40 | 76:48 | 29:31 | 15:38 | 45:09 | 453:31 | 47:49 | 11:57 | 98.4323 | 98.3397 | 530:19 | 132:35 | 98.0639 | 97.736
37 | Bhatkal | 3 | 3 | 12:39 | 172:21 | 25:37 | 7:34 | 33:11 | 259:43 | 45:50 | 15:17 | 98.4637 | 97.8781 | 432:04 | 144:01 | 98.5216 | 97.5406
38 | Khanapur | 2 | 2 | 9:35 | 70:55 | 148:40 | 8:50 | 157:30 | 564:20 | 167:05 | 83:32 | 89.0625 | 88.397 | 635:15 | 317:37 | 95.1816 | 94.5761
39 | Bailhongal | 3 | 3 | 0:00 | 2:15 | 45:20 | 4:45 | 50:05 | 493:25 | 50:05 | 16:42 | 97.6813 | 97.6813 | 495:40 | 165:13 | 97.1914 | 97.1786
40 | Kittur | 1 | 1 | 0:35 | 4:11 | 10:20 | 4:45 | 15:05 | 153:22 | 15:40 | 15:40 | 97.9051 | 97.8241 | 157:33 | 157:33 | 97.381 | 97.3096
41 | M K Hubli | 1 | 1 | 0:00 | 0:45 | 10:45 | 9:00 | 19:45 | 217:20 | 19:45 | 19:45 | 97.2569 | 97.2569 | 218:05 | 218:05 | 96.2887 | 96.2759
42 | Soundatti | 3 | 3 | 6:43 | 65:52 | 16:43 | 4:08 | 20:51 | 309:27 | 27:34 | 9:11 | 99.0347 | 98.7238 | 375:19 | 125:06 | 98.2386 | 97.8636
43 | Munavalli | 1 | 1 | 17:30 | 71:20 | 19:30 | 1:50 | 21:20 | 311:30 | 38:50 | 38:50 | 97.037 | 94.6065 | 382:50 | 382:50 | 94.6807 | 93.4625
44 | Yaragatti | 1 | 1 | 5:18 | 45:10 | 30:29 | 3:52 | 34:21 | 351:53 | 39:39 | 39:39 | 95.2292 | 94.4931 | 397:03 | 397:03 | 93.9911 | 93.2198
45 | Ramdurg | 2 | 2 | 1:58 | 34:24 | 10:30 | 2:35 | 13:05 | 250:40 | 15:03 | 7:32 | 99.0914 | 98.9549 | 285:04 | 142:32 | 97.8597 | 97.566
46 | Gokak | 10 | 10 | 15:33 | 266:27 | 70:51 | 29:18 | 100:09 | 433:11 | 115:42 | 11:34 | 98.609 | 98.3931 | 699:38 | 69:58 | 99.2603 | 98.8053
47 | Mudalagi | 2 | 2 | 0:40 | 15:25 | 36:00 | 1:15 | 37:15 | 355:40 | 37:55 | 18:57 | 97.4132 | 97.3669 | 371:05 | 185:33 | 96.9632 | 96.8316
48 | Konnur | 1 | 1 | 0:00 | 2:10 | 24:30 | 1:05 | 25:35 | 220:20 | 25:35 | 25:35 | 96.4468 | 96.4468 | 222:30 | 222:30 | 96.2375 | 96.2005
49 | Raibag | 1 | 1 | 0:00 | 0:00 | 24:05 | 2:56 | 27:01 | 330:51 | 27:01 | 27:01 | 96.2477 | 96.2477 | 330:51 | 330:51 | 94.3502 | 94.3502
50 | Kudachi | 1 | 1 | 0:00 | 1:20 | 19:35 | 1:15 | 20:50 | 413:40 | 20:50 | 20:50 | 97.1065 | 97.1065 | 415:00 | 415:00 | 92.936 | 92.9133
51 | Athani | 7 | 7 | 32:35 | 239:26 | 82:31 | 40:23 | 122:54 | 1422:08 | 155:29 | 22:13 | 97.5615 | 96.915 | 1661:34 | 237:22 | 96.5307 | 95.9466
52 | Chikkodi | 4 | 4 | 0:00 | 16:20 | 28:09 | 4:39 | 32:48 | 294:08 | 32:48 | 8:12 | 98.8611 | 98.8611 | 310:28 | 77:37 | 98.7443 | 98.6746
53 | Nippani | 5 | 5 | 0:00 | 0:00 | 31:55 | 9:55 | 41:50 | 800:27 | 41:50 | 8:22 | 98.838 | 98.838 | 800:27 | 160:05 | 97.2662 | 97.2662
54 | Sadalaga | 1 | 1 | 0:10 | 23:03 | 14:35 | 1:45 | 16:20 | 199:10 | 16:30 | 16:30 | 97.7315 | 97.7083 | 222:13 | 222:13 | 96.5989 | 96.2053
55 | Muddebihal | 2 | 2 | 23:00 | 60:05 | 58:30 | 5:55 | 64:25 | 569:45 | 87:25 | 43:42 | 95.5266 | 93.9294 | 629:50 | 314:55 | 95.1353 | 94.6223
56 | Talikoti | 1 | 1 | 17:50 | 73:15 | 15:40 | 3:05 | 18:45 | 275:30 | 36:35 | 36:35 | 97.3958 | 94.919 | 348:45 | 348:45 | 95.2954 | 94.0446
57 | B.Bagewadi | 1 | 1 | 1:20 | 18:08 | 15:05 | 0:35 | 15:40 | 124:07 | 17:00 | 17:00 | 97.8241 | 97.6389 | 142:15 | 142:15 | 97.8805 | 97.5709
58 | Indi | 3 | 3 | 27:25 | 112:13 | 5:04 | 2:27 | 7:31 | 188:05 | 34:56 | 11:39 | 99.652 | 98.3827 | 300:18 | 100:06 | 98.9294 | 98.2906
59 | Sindagi | 2 | 2 | 16:50 | 136:10 | 30:20 | 2:50 | 33:10 | 360:05 | 50:00 | 25:00 | 97.6968 | 96.5278 | 496:15 | 248:08 | 96.9255 | 95.7629
60 | Guledgudda | 1 | 1 | 0:12 | 17:55 | 5:43 | 4:23 | 10:06 | 156:22 | 10:18 | 10:18 | 98.5972 | 98.5694 | 174:17 | 174:17 | 97.3298 | 97.0239
61 | Ilkal | 7 | 7 | 2:30 | 108:56 | 141:32 | 75:03 | 216:35 | 1725:47 | 219:05 | 31:18 | 95.7027 | 95.6531 | 1834:43 | 262:06 | 95.79 | 95.5242
62 | Kerur | 1 | 1 | 0:44 | 21:00 | 8:04 | 2:00 | 10:04 | 260:38 | 10:48 | 10:48 | 98.6019 | 98.5 | 281:38 | 281:38 | 95.5493 | 95.1907
63 | Hungund | 4 | 4 | 1:50 | 65:45 | 49:56 | 27:36 | 77:32 | 937:02 | 79:22 | 19:50 | 97.3079 | 97.2442 | 1002:47 | 250:42 | 95.9997 | 95.719
64 | Badami | 1 | 1 | 0:24 | 16:09 | 8:38 | 8:02 | 16:40 | 178:15 | 17:04 | 17:04 | 97.6852 | 97.6296 | 194:24 | 194:24 | 96.9561 | 96.6803
65 | Jamkhandi | 6 | 6 | 5:00 | 44:20 | 66:10 | 6:50 | 73:00 | 971:35 | 78:00 | 13:00 | 98.3102 | 98.1944 | 1015:55 | 169:19 | 97.2348 | 97.1086
66 | Mahalingapur | 2 | 2 | 0:30 | 14:56 | 17:07 | 3:40 | 20:47 | 302:42 | 21:17 | 10:38 | 98.5567 | 98.522 | 317:38 | 158:49 | 97.4155 | 97.288
67 | Rannabelagali | 1 | 1 | 0:00 | 16:32 | 24:24 | 0:40 | 25:04 | 171:59 | 25:04 | 25:04 | 96.5185 | 96.5185 | 188:31 | 188:31 | 97.0631 | 96.7808
68 | Rabakavi | 2 | 2 | 0:00 | 45:20 | 9:35 | 5:00 | 14:35 | 183:40 | 14:35 | 7:18 | 98.9873 | 98.9873 | 229:00 | 114:30 | 98.4318 | 98.0447
69 | Banahatti | 2 | 2 | 1:10 | 9:10 | 15:25 | 0:10 | 15:35 | 297:30 | 16:45 | 8:22 | 98.9178 | 98.8368 | 306:40 | 153:20 | 97.4599 | 97.3816
70 | Terdal | 2 | 2 | 0:20 | 26:30 | 28:35 | 2:05 | 30:40 | 429:37 | 31:00 | 15:30 | 97.8704 | 97.8472 | 456:07 | 228:04 | 96.3318 | 96.1056
71 | Mudhol | 4 | 4 | 0:56 | 101:17 | 53:23 | 3:44 | 57:07 | 744:16 | 58:03 | 14:31 | 98.0168 | 97.9844 | 845:33 | 211:23 | 96.8226 | 96.3902
72 | Bilagi | 1 | 1 | 8:35 | 18:45 | 10:55 | 1:20 | 12:15 | 198:53 | 20:50 | 20:50 | 98.2986 | 97.1065 | 217:38 | 217:38 | 96.6038 | 96.2836
73 | Lokapur | 2 | 2 | 0:00 | 7:49 | 50:50 | 3:35 | 54:25 | 647:05 | 54:25 | 27:12 | 96.2211 | 96.2211 | 654:54 | 327:27 | 94.475 | 94.4083
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of Dec-2022
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Dec-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Dec-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 86 | 86 | 140:15 | 693:22 | 441:43 | 299:05 | 740:48 | 5868:45 | 881:03 | 10:15 | 98.8422 | 98.623 | 6562:07 | 76:18 | 98.966 | 98.8439
2 | Dharwad(R) | 14 | 14 | 21:30 | 115:47 | 141:10 | 49:12 | 190:22 | 2011:28 | 211:52 | 15:08 | 98.1724 | 97.9659 | 2127:15 | 151:57 | 97.8231 | 97.6978
3 | Kundagol | 1 | 1 | 13:21 | 108:57 | 3:01 | 8:21 | 11:22 | 111:27 | 24:43 | 24:43 | 98.4722 | 96.6779 | 220:24 | 220:24 | 98.3114 | 96.6606
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 9:34 | 5:56 | 15:30 | 183:58 | 15:30 | 15:30 | 97.9167 | 97.9167 | 183:58 | 183:58 | 97.2126 | 97.2126
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 4:50 | 3:35 | 8:25 | 210:58 | 8:25 | 8:25 | 98.8687 | 98.8687 | 210:58 | 210:58 | 96.8035 | 96.8035
6 | Kalghatagi | 2 | 2 | 4:55 | 4:55 | 9:05 | 9:55 | 19:00 | 436:20 | 23:55 | 11:58 | 98.7231 | 98.3927 | 441:15 | 220:38 | 96.6944 | 96.6572
7 | Alnavar | 2 | 2 | 0:00 | 0:00 | 11:10 | 3:50 | 15:00 | 275:05 | 15:00 | 7:30 | 98.9919 | 98.9919 | 275:05 | 137:32 | 97.916 | 97.916
8 | Naragund | 2 | 2 | 14:10 | 79:10 | 11:00 | 1:00 | 12:00 | 413:20 | 26:10 | 13:05 | 99.1935 | 98.2415 | 492:30 | 246:15 | 96.8687 | 96.2689
9 | Shirahatti | 1 | 1 | 0:00 | 0:00 | 6:30 | 12:40 | 19:10 | 155:25 | 19:10 | 19:10 | 97.4238 | 97.4238 | 155:25 | 155:25 | 97.6452 | 97.6452
10 | Laxmeshwar | 3 | 3 | 0:00 | 0:00 | 38:23 | 9:02 | 47:25 | 515:03 | 47:25 | 15:48 | 97.8756 | 97.8756 | 515:03 | 171:41 | 97.3987 | 97.3987
11 | Naregal | 1 | 1 | 1:20 | 8:30 | 8:40 | 1:20 | 10:00 | 98:50 | 11:20 | 11:20 | 98.6559 | 98.4767 | 107:20 | 107:20 | 98.5025 | 98.3737
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 26:00 | 6:05 | 32:05 | 307:15 | 32:05 | 16:02 | 97.8439 | 97.8439 | 307:15 | 153:38 | 97.6723 | 97.6723
13 | Ron | 3 | 3 | 0:00 | 0:00 | 22:35 | 7:00 | 29:35 | 444:31 | 29:35 | 9:52 | 98.6746 | 98.6746 | 444:31 | 148:10 | 97.755 | 97.755
14 | Mundaragi | 1 | 1 | 18:10 | 19:50 | 16:15 | 21:40 | 37:55 | 248:35 | 56:05 | 56:05 | 94.9037 | 92.4619 | 268:25 | 268:25 | 96.2336 | 95.9331
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 21:00 | 6:15 | 27:15 | 535:14 | 27:15 | 27:15 | 96.3374 | 96.3374 | 535:14 | 535:14 | 91.8904 | 91.8904
16 | Savanur | 2 | 2 | 0:00 | 22:45 | 75:25 | 3:40 | 79:05 | 384:25 | 79:05 | 39:32 | 94.6853 | 94.6853 | 407:10 | 203:35 | 97.0878 | 96.9154
17 | Shiggaon | 3 | 3 | 6:10 | 229:05 | 36:25 | 3:50 | 40:15 | 452:05 | 46:25 | 15:28 | 98.1967 | 97.9204 | 681:10 | 227:03 | 97.7168 | 96.5598
18 | Bankapur | 1 | 1 | 10:05 | 128:35 | 9:10 | 7:30 | 16:40 | 303:00 | 26:45 | 26:45 | 97.7599 | 96.4046 | 431:35 | 431:35 | 95.4091 | 93.4609
19 | Hangal | 2 | 2 | 19:10 | 78:19 | 9:00 | 1:40 | 10:40 | 373:45 | 29:50 | 14:55 | 99.2832 | 97.9951 | 452:04 | 226:02 | 97.1686 | 96.5753
20 | Ranebennur | 10 | 10 | 7:00 | 65:13 | 40:50 | 30:30 | 71:20 | 1158:56 | 78:20 | 7:50 | 99.0412 | 98.9471 | 1224:09 | 122:25 | 98.244 | 98.1452
21 | Tuminakatti | 1 | 1 | 0:40 | 8:35 | 9:45 | 0:20 | 10:05 | 187:05 | 10:45 | 10:45 | 98.6447 | 98.5551 | 195:40 | 195:40 | 97.1654 | 97.0354
22 | Rattihalli | 1 | 1 | 1:00 | 13:25 | 10:15 | 4:30 | 14:45 | 193:20 | 15:45 | 15:45 | 98.0175 | 97.8831 | 206:45 | 206:45 | 97.0707 | 96.8674
23 | Hirekerur | 1 | 1 | 0:20 | 9:00 | 15:30 | 3:50 | 19:20 | 217:25 | 19:40 | 19:40 | 97.4014 | 97.3566 | 226:25 | 226:25 | 96.7058 | 96.5694
24 | Byadagi | 5 | 5 | 16:15 | 215:24 | 67:22 | 18:10 | 85:32 | 896:37 | 101:47 | 20:21 | 97.7007 | 97.2639 | 1112:01 | 222:24 | 97.283 | 96.6303
25 | Sirsi | 6 | 6 | 23:20 | 224:01 | 68:05 | 6:28 | 74:33 | 671:00 | 97:53 | 16:19 | 98.33 | 97.8073 | 895:01 | 149:10 | 98.3056 | 97.7399
26 | Yellapur | 1 | 1 | 9:10 | 86:30 | 9:10 | 4:35 | 13:45 | 112:05 | 22:55 | 22:55 | 98.1519 | 96.9198 | 198:35 | 198:35 | 98.3018 | 96.9912
27 | Mundagod | 1 | 1 | 24:40 | 28:22 | 10:20 | 2:00 | 12:20 | 115:45 | 37:00 | 37:00 | 98.3423 | 95.0269 | 144:07 | 144:07 | 98.2462 | 97.8164
28 | Siddapur | 1 | 1 | 0:25 | 62:15 | 0:25 | 2:40 | 3:05 | 92:00 | 3:30 | 3:30 | 99.5856 | 99.5296 | 154:15 | 154:15 | 98.6061 | 97.6629
29 | Dandeli | 7 | 7 | 8:00 | 96:47 | 52:18 | 11:03 | 63:21 | 841:45 | 71:21 | 10:12 | 98.7836 | 98.63 | 938:32 | 134:05 | 98.178 | 97.9685
30 | Haliyal | 2 | 2 | 0:00 | 8:56 | 6:45 | 1:50 | 8:35 | 191:24 | 8:35 | 4:18 | 99.4232 | 99.4232 | 200:20 | 100:10 | 98.55 | 98.4823
31 | Ankola | 3 | 3 | 30:37 | 194:02 | 3:46 | 3:40 | 7:26 | 252:30 | 38:03 | 12:41 | 99.667 | 98.2953 | 446:32 | 148:51 | 98.7247 | 97.7448
32 | Kumta | 3 | 3 | 1:21 | 29:42 | 10:01 | 5:03 | 15:04 | 286:59 | 16:25 | 5:28 | 99.325 | 99.2645 | 316:41 | 105:34 | 98.5506 | 98.4006
33 | Gokarna | 1 | 1 | 2:54 | 81:55 | 2:35 | 1:05 | 3:40 | 53:05 | 6:34 | 6:34 | 99.5072 | 99.1174 | 135:00 | 135:00 | 99.1957 | 97.9545
34 | Kasarkod | 1 | 1 | 39:24 | 164:55 | 3:05 | 5:33 | 8:38 | 139:48 | 48:02 | 48:02 | 98.8396 | 93.5439 | 304:43 | 304:43 | 97.8818 | 95.3831
35 | Honnavar | 3 | 3 | 1:21 | 54:57 | 15:14 | 8:27 | 23:41 | 466:31 | 25:02 | 8:21 | 98.9389 | 98.8784 | 521:28 | 173:49 | 97.6439 | 97.3663
36 | Murdeshwar | 4 | 4 | 1:52 | 78:40 | 23:19 | 14:52 | 38:11 | 491:42 | 40:03 | 10:01 | 98.717 | 98.6542 | 570:22 | 142:36 | 98.1375 | 97.8395
37 | Bhatkal | 3 | 3 | 6:48 | 179:09 | 11:36 | 0:40 | 12:16 | 271:59 | 19:04 | 6:21 | 99.4504 | 99.1458 | 451:08 | 150:23 | 98.6263 | 97.7215
38 | Khanapur | 2 | 2 | 8:20 | 79:15 | 31:05 | 16:55 | 48:00 | 612:20 | 56:20 | 28:10 | 96.7742 | 96.2142 | 691:35 | 345:47 | 95.3611 | 94.7607
39 | Bailhongal | 3 | 3 | 0:00 | 2:15 | 17:30 | 4:55 | 22:25 | 515:50 | 22:25 | 7:28 | 98.9957 | 98.9957 | 518:05 | 172:42 | 97.3948 | 97.3834
40 | Kittur | 1 | 1 | 0:20 | 4:31 | 11:10 | 16:40 | 27:50 | 181:12 | 28:10 | 28:10 | 96.259 | 96.2142 | 185:43 | 185:43 | 97.2545 | 97.1861
41 | M K Hubli | 1 | 1 | 0:00 | 0:45 | 13:50 | 6:10 | 20:00 | 237:20 | 20:00 | 20:00 | 97.3118 | 97.3118 | 238:05 | 238:05 | 96.404 | 96.3927
42 | Soundatti | 3 | 3 | 16:27 | 82:19 | 29:36 | 3:30 | 33:06 | 342:33 | 49:33 | 16:31 | 98.517 | 97.78 | 424:52 | 141:37 | 98.2699 | 97.8542
43 | Munavalli | 1 | 1 | 3:40 | 75:00 | 30:00 | 0:50 | 30:50 | 342:20 | 34:30 | 34:30 | 95.8557 | 95.3629 | 417:20 | 417:20 | 94.8131 | 93.6768
44 | Yaragatti | 1 | 1 | 1:58 | 47:08 | 30:24 | 3:04 | 33:28 | 385:21 | 35:26 | 35:26 | 95.5018 | 95.2375 | 432:29 | 432:29 | 94.1614 | 93.4472
45 | Ramdurg | 2 | 2 | 2:00 | 36:24 | 35:52 | 1:32 | 37:24 | 288:04 | 39:24 | 19:42 | 97.4866 | 97.3522 | 324:28 | 162:14 | 97.8177 | 97.5419
46 | Gokak | 10 | 10 | 3:16 | 269:43 | 2:34 | 9:36 | 12:10 | 445:21 | 15:26 | 1:33 | 99.8365 | 99.7926 | 715:04 | 71:30 | 99.3252 | 98.9166
47 | Mudalagi | 2 | 2 | 0:00 | 15:25 | 36:50 | 1:10 | 38:00 | 393:40 | 38:00 | 19:00 | 97.4462 | 97.4462 | 409:05 | 204:32 | 97.0177 | 96.9009
48 | Konnur | 1 | 1 | 0:50 | 3:00 | 16:15 | 0:15 | 16:30 | 236:50 | 17:20 | 17:20 | 97.7823 | 97.6703 | 239:50 | 239:50 | 96.4116 | 96.3662
49 | Raibag | 1 | 1 | 0:00 | 0:00 | 26:35 | 2:35 | 29:10 | 360:01 | 29:10 | 29:10 | 96.0797 | 96.0797 | 360:01 | 360:01 | 94.5452 | 94.5452
50 | Kudachi | 1 | 1 | 0:00 | 1:20 | 23:20 | 5:10 | 28:30 | 442:10 | 28:30 | 28:30 | 96.1694 | 96.1694 | 443:30 | 443:30 | 93.3005 | 93.2803
51 | Athani | 7 | 7 | 6:30 | 245:56 | 134:54 | 37:11 | 172:05 | 1594:13 | 178:35 | 25:31 | 96.6958 | 96.571 | 1840:09 | 262:53 | 96.5493 | 96.017
52 | Chikkodi | 4 | 4 | 0:00 | 16:20 | 45:30 | 8:30 | 54:00 | 348:08 | 54:00 | 13:30 | 98.1855 | 98.1855 | 364:28 | 91:07 | 98.6813 | 98.6194
53 | Nippani | 5 | 5 | 0:00 | 0:00 | 75:25 | 13:15 | 88:40 | 889:07 | 88:40 | 17:44 | 97.6165 | 97.6165 | 889:07 | 177:49 | 97.3057 | 97.3057
54 | Sadalaga | 1 | 1 | 0:00 | 23:03 | 21:15 | 0:40 | 21:55 | 221:05 | 21:55 | 21:55 | 97.0542 | 97.0542 | 244:08 | 244:08 | 96.6503 | 96.301
55 | Muddebihal | 2 | 2 | 22:40 | 82:45 | 25:10 | 5:50 | 31:00 | 600:45 | 53:40 | 26:50 | 97.9167 | 96.3934 | 683:30 | 341:45 | 95.4489 | 94.822
56 | Talikoti | 1 | 1 | 7:10 | 80:25 | 10:35 | 3:00 | 13:35 | 289:05 | 20:45 | 20:45 | 98.1743 | 97.211 | 369:30 | 369:30 | 95.6199 | 94.4015
57 | B.Bagewadi | 1 | 1 | 7:55 | 26:03 | 14:12 | 1:55 | 16:07 | 140:14 | 24:02 | 24:02 | 97.8338 | 96.7697 | 166:17 | 166:17 | 97.8753 | 97.4806
58 | Indi | 3 | 3 | 10:58 | 123:11 | 6:29 | 6:18 | 12:47 | 200:52 | 23:45 | 7:55 | 99.4273 | 98.9359 | 324:03 | 108:01 | 98.9855 | 98.3634
59 | Sindagi | 2 | 2 | 10:40 | 146:50 | 19:25 | 2:45 | 22:10 | 382:15 | 32:50 | 16:25 | 98.5103 | 97.7935 | 529:05 | 264:32 | 97.1042 | 95.9918
60 | Guledgudda | 2 | 2 | 3:07 | 21:02 | 25:56 | 3:22 | 29:18 | 185:40 | 32:25 | 16:12 | 98.0309 | 97.8215 | 206:42 | 103:21 | 98.5934 | 98.4341
61 | Ilkal | 7 | 7 | 17:00 | 125:56 | 102:54 | 85:41 | 188:35 | 1914:22 | 205:35 | 29:22 | 96.379 | 96.0525 | 2040:18 | 291:28 | 95.8563 | 95.5838
62 | Kerur | 1 | 1 | 6:58 | 27:58 | 11:50 | 2:53 | 14:43 | 275:21 | 21:41 | 21:41 | 98.022 | 97.0856 | 303:19 | 303:19 | 95.828 | 95.4043
63 | Hungund | 4 | 4 | 14:54 | 80:39 | 58:17 | 31:55 | 90:12 | 1027:14 | 105:06 | 26:16 | 96.9691 | 96.4684 | 1107:53 | 276:58 | 96.109 | 95.8035
64 | Badami | 2 | 2 | 0:52 | 17:01 | 2:33 | 13:08 | 15:41 | 193:56 | 16:33 | 8:16 | 98.946 | 98.8878 | 210:57 | 105:28 | 98.5308 | 98.4019
65 | Jamkhandi | 6 | 6 | 2:30 | 46:50 | 103:55 | 6:10 | 110:05 | 1081:40 | 112:35 | 18:46 | 97.534 | 97.478 | 1128:30 | 188:05 | 97.2685 | 97.1503
66 | Mahalingapur | 2 | 2 | 0:05 | 15:01 | 22:44 | 4:56 | 27:40 | 330:22 | 27:45 | 13:53 | 98.1407 | 98.1351 | 345:23 | 172:42 | 97.4972 | 97.3835
67 | Rannabelagali | 1 | 1 | 0:00 | 16:32 | 11:35 | 1:20 | 12:55 | 184:54 | 12:55 | 12:55 | 98.2639 | 98.2639 | 201:26 | 201:26 | 97.1985 | 96.948
68 | Rabakavi | 2 | 2 | 0:20 | 45:40 | 10:10 | 1:35 | 11:45 | 195:25 | 12:05 | 6:02 | 99.2103 | 99.1879 | 241:05 | 120:32 | 98.5196 | 98.1736
69 | Banahatti | 2 | 2 | 0:46 | 9:56 | 26:25 | 0:15 | 26:40 | 324:10 | 27:26 | 13:43 | 98.2079 | 98.1564 | 334:06 | 167:03 | 97.5442 | 97.4689
70 | Terdal | 2 | 2 | 0:00 | 26:30 | 21:25 | 4:30 | 25:55 | 455:32 | 25:55 | 12:58 | 98.2583 | 98.2583 | 482:02 | 241:01 | 96.549 | 96.3482
71 | Mudhol | 4 | 4 | 0:00 | 101:17 | 60:00 | 10:01 | 70:01 | 814:17 | 70:01 | 17:30 | 97.6473 | 97.6473 | 915:34 | 228:54 | 96.9156 | 96.5319
72 | Bilagi | 1 | 1 | 8:09 | 26:54 | 7:10 | 1:55 | 9:05 | 207:58 | 17:14 | 17:14 | 98.7791 | 97.6837 | 234:52 | 234:52 | 96.849 | 96.4414
73 | Lokapur | 2 | 2 | 0:00 | 7:49 | 52:40 | 10:45 | 63:25 | 710:30 | 63:25 | 31:42 | 95.7381 | 95.7381 | 718:19 | 359:10 | 94.6174 | 94.5582
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of Jan-2023
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Jan-2023 |  |  |  | Reliability for cumulative period from Apr-22 to Jan-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi(U) | 86 | 86 | 19:44 | 713:06 | 134:24 | 166:52 | 301:16 | 6170:01 | 321:00 | 3:44 | 99.5292 | 99.4983 | 6883:07 | 80:02 | 99.0231 | 98.9102
2 | Dharwad(R) | 14 | 14 | 15:25 | 131:12 | 138:14 | 34:30 | 172:44 | 2184:12 | 188:09 | 13:26 | 98.3417 | 98.1936 | 2315:24 | 165:23 | 97.8756 | 97.748
3 | Kundagol | 1 | 1 | 7:20 | 116:17 | 22:39 | 1:42 | 24:21 | 135:48 | 31:41 | 31:41 | 96.7272 | 95.7415 | 252:05 | 252:05 | 98.1509 | 96.5675
4 | Navalgund | 1 | 1 | 0:00 | 0:00 | 2:57 | 1:29 | 4:26 | 188:24 | 4:26 | 4:26 | 99.4041 | 99.4041 | 188:24 | 188:24 | 97.4346 | 97.4346
5 | Annigeri | 1 | 1 | 0:00 | 0:00 | 10:05 | 4:16 | 14:21 | 225:19 | 14:21 | 14:21 | 98.0712 | 98.0712 | 225:19 | 225:19 | 96.932 | 96.932
6 | Kalghatagi | 2 | 2 | 0:00 | 4:55 | 24:00 | 5:25 | 29:25 | 465:45 | 29:25 | 14:42 | 98.0231 | 98.0231 | 470:40 | 235:20 | 96.829 | 96.7956
7 | Alnavar | 2 | 2 | 0:00 | 0:00 | 2:30 | 1:50 | 4:20 | 279:25 | 4:20 | 2:10 | 99.7088 | 99.7088 | 279:25 | 139:42 | 98.0977 | 98.0977
8 | Naragund | 2 | 2 | 1:20 | 80:30 | 27:00 | 23:45 | 50:45 | 464:05 | 52:05 | 26:02 | 96.5894 | 96.4998 | 544:35 | 272:18 | 96.8404 | 96.2923
9 | Shirahatti | 1 | 1 | 0:00 | 0:00 | 3:40 | 2:30 | 6:10 | 161:35 | 6:10 | 6:10 | 99.1711 | 99.1711 | 161:35 | 161:35 | 97.7998 | 97.7998
10 | Laxmeshwar | 3 | 3 | 0:00 | 0:00 | 13:38 | 5:02 | 18:40 | 533:43 | 18:40 | 6:13 | 99.1637 | 99.1637 | 533:43 | 177:54 | 97.5775 | 97.5775
11 | Naregal | 1 | 1 | 1:55 | 10:25 | 1:40 | 0:30 | 2:10 | 101:00 | 4:05 | 4:05 | 99.7088 | 99.4512 | 111:25 | 111:25 | 98.6247 | 98.4829
12 | Gajendragad | 2 | 2 | 0:00 | 0:00 | 7:05 | 5:00 | 12:05 | 319:20 | 12:05 | 6:02 | 99.1879 | 99.1879 | 319:20 | 159:40 | 97.8259 | 97.8259
13 | Ron | 3 | 3 | 0:00 | 0:00 | 12:00 | 7:10 | 19:10 | 463:41 | 19:10 | 6:23 | 99.1413 | 99.1413 | 463:41 | 154:34 | 97.8954 | 97.8954
14 | Mundaragi | 1 | 1 | 0:25 | 20:15 | 3:41 | 5:15 | 8:56 | 257:31 | 9:21 | 9:21 | 98.7993 | 98.7433 | 277:46 | 277:46 | 96.4935 | 96.2178
15 | Mulagund | 1 | 1 | 0:00 | 0:00 | 12:11 | 6:14 | 18:25 | 553:39 | 18:25 | 18:25 | 97.5246 | 97.5246 | 553:39 | 553:39 | 92.4612 | 92.4612
16 | Savanur | 2 | 2 | 6:50 | 29:35 | 11:25 | 4:55 | 16:20 | 400:45 | 23:10 | 11:35 | 98.9023 | 98.4431 | 430:20 | 215:10 | 97.2716 | 97.0702
17 | Shiggaon | 3 | 3 | 35:41 | 264:46 | 12:00 | 3:00 | 15:00 | 467:05 | 50:41 | 16:54 | 99.328 | 97.7292 | 731:51 | 243:57 | 97.88 | 96.6782
18 | Bankapur | 1 | 1 | 10:15 | 138:50 | 11:35 | 5:20 | 16:55 | 319:55 | 27:10 | 27:10 | 97.7263 | 96.3486 | 458:45 | 458:45 | 95.6438 | 93.7534
19 | Hangal | 2 | 2 | 13:10 | 91:29 | 11:35 | 2:40 | 14:15 | 388:00 | 27:25 | 13:42 | 99.0423 | 98.1575 | 479:29 | 239:44 | 97.3584 | 96.7355
20 | Ranebennur | 10 | 10 | 20:22 | 85:35 | 73:20 | 19:19 | 92:39 | 1251:35 | 113:01 | 11:18 | 98.7547 | 98.481 | 1337:10 | 133:43 | 98.2958 | 98.1792
21 | Tumminakatti | 1 | 1 | 2:35 | 11:10 | 9:50 | 2:05 | 11:55 | 199:00 | 14:30 | 14:30 | 98.3983 | 98.0511 | 210:10 | 210:10 | 97.2903 | 97.1383
22 | Rattihalli | 1 | 1 | 3:20 | 16:45 | 6:05 | 8:35 | 14:40 | 208:00 | 18:00 | 18:00 | 98.0287 | 97.5806 | 224:45 | 224:45 | 97.1678 | 96.9397
23 | Hirekerur | 1 | 1 | 3:30 | 12:30 | 4:05 | 5:05 | 9:10 | 226:35 | 12:40 | 12:40 | 98.7679 | 98.2975 | 239:05 | 239:05 | 96.9147 | 96.7445
24 | Byadagi | 5 | 5 | 21:33 | 236:57 | 79:50 | 17:55 | 97:45 | 994:22 | 119:18 | 23:52 | 97.3723 | 96.793 | 1231:19 | 246:16 | 97.292 | 96.6467
25 | Sirsi | 6 | 6 | 21:07 | 245:08 | 97:39 | 17:12 | 114:51 | 785:51 | 135:58 | 22:40 | 97.4272 | 96.9542 | 1030:59 | 171:50 | 98.2166 | 97.6603
26 | Yellapur | 1 | 1 | 5:55 | 92:25 | 17:55 | 7:00 | 24:55 | 137:00 | 30:50 | 30:50 | 96.651 | 95.8557 | 229:25 | 229:25 | 98.1345 | 96.8761
27 | Mundagod | 1 | 1 | 2:05 | 30:27 | 27:55 | 1:45 | 29:40 | 145:25 | 31:45 | 31:45 | 96.0125 | 95.7325 | 175:52 | 175:52 | 98.0199 | 97.6053
28 | Siddapur | 1 | 1 | 7:45 | 70:00 | 1:25 | 3:40 | 5:05 | 97:05 | 12:50 | 12:50 | 99.3168 | 98.2751 | 167:05 | 167:05 | 98.6781 | 97.7249
29 | Dandeli | 7 | 7 | 42:35 | 139:22 | 87:14 | 24:27 | 111:41 | 953:26 | 154:16 | 22:02 | 97.8555 | 97.0379 | 1092:48 | 156:07 | 98.1454 | 97.8743
30 | Haliyal | 2 | 2 | 0:00 | 8:56 | 8:40 | 6:55 | 15:35 | 206:59 | 15:35 | 7:48 | 98.9527 | 98.9527 | 215:55 | 107:57 | 98.5908 | 98.53
31 | Ankola | 2 | 2 | 3:00 | 197:02 | 15:37 | 5:48 | 21:25 | 273:55 | 24:25 | 12:12 | 98.5607 | 98.3591 | 470:57 | 235:29 | 98.1351 | 96.7936
32 | Kumta | 3 | 3 | 1:15 | 30:57 | 6:43 | 3:23 | 10:06 | 297:05 | 11:21 | 3:47 | 99.5475 | 99.4915 | 328:02 | 109:21 | 98.6516 | 98.5111
33 | Gokarna | 1 | 1 | 6:04 | 87:59 | 5:20 | 5:25 | 10:45 | 63:50 | 16:49 | 16:49 | 98.5551 | 97.7397 | 151:49 | 151:49 | 99.1308 | 97.9328
34 | Kasarkod | 1 | 1 | 16:51 | 181:46 | 5:52 | 7:01 | 12:53 | 152:41 | 29:44 | 29:44 | 98.2684 | 96.0036 | 334:27 | 334:27 | 97.921 | 95.4459
35 | Honnavar | 3 | 3 | 3:42 | 58:39 | 27:49 | 3:43 | 31:32 | 498:03 | 35:14 | 11:45 | 98.5872 | 98.4214 | 556:42 | 185:34 | 97.7394 | 97.4732
36 | Murdeshwar | 4 | 4 | 4:56 | 83:36 | 22:32 | 10:02 | 32:34 | 524:16 | 37:30 | 9:22 | 98.9057 | 98.7399 | 607:52 | 151:58 | 98.2153 | 97.9307
37 | Bhatkal | 3 | 3 | 4:06 | 183:15 | 24:20 | 2:19 | 26:39 | 298:38 | 30:45 | 10:15 | 98.806 | 98.6223 | 481:53 | 160:38 | 98.6445 | 97.8128
38 | Khanapur | 2 | 2 | 2:10 | 81:25 | 9:30 | 3:30 | 13:00 | 625:20 | 15:10 | 7:35 | 99.1263 | 98.9807 | 706:45 | 353:22 | 95.7426 | 95.1882
39 | Bailhongal | 3 | 3 | 0:00 | 2:15 | 92:05 | 3:30 | 95:35 | 611:25 | 95:35 | 31:52 | 95.7176 | 95.7176 | 613:40 | 204:33 | 97.2249 | 97.2147
40 | Kittur | 1 | 1 | 0:20 | 4:51 | 16:35 | 11:15 | 27:50 | 209:02 | 28:10 | 28:10 | 96.259 | 96.2142 | 213:53 | 213:53 | 97.1537 | 97.0876
41 | M K Hubli | 1 | 1 | 0:00 | 0:45 | 19:10 | 7:55 | 27:05 | 264:25 | 27:05 | 27:05 | 96.3598 | 96.3598 | 265:10 | 265:10 | 96.3996 | 96.3893
42 | Soundatti | 3 | 3 | 3:25 | 85:44 | 4:42 | 1:27 | 6:09 | 348:42 | 9:34 | 3:11 | 99.7245 | 99.5714 | 434:26 | 144:49 | 98.4173 | 98.0282
43 | Munavalli | 1 | 1 | 2:25 | 77:25 | 21:10 | 0:25 | 21:35 | 363:55 | 24:00 | 24:00 | 97.099 | 96.7742 | 441:20 | 441:20 | 95.0447 | 93.9906
44 | Yaragatti | 1 | 1 | 0:13 | 47:21 | 26:21 | 1:07 | 27:28 | 412:49 | 27:41 | 27:41 | 96.3082 | 96.2791 | 460:10 | 460:10 | 94.3789 | 93.7341
45 | Ramdurg | 2 | 2 | 0:20 | 36:44 | 11:03 | 2:40 | 13:43 | 301:47 | 14:03 | 7:01 | 99.0782 | 99.0558 | 338:31 | 169:16 | 97.9454 | 97.6953
46 | Gokak | 10 | 10 | 4:56 | 274:39 | 2:58 | 14:26 | 17:24 | 462:45 | 22:20 | 2:14 | 99.7661 | 99.6998 | 737:24 | 73:44 | 99.3699 | 98.9959
47 | Mudalagi | 2 | 2 | 1:20 | 16:45 | 14:10 | 0:55 | 15:05 | 408:45 | 16:25 | 8:12 | 98.9863 | 98.8967 | 425:30 | 212:45 | 97.2171 | 97.1031
48 | Konnur | 1 | 1 | 0:35 | 3:35 | 11:45 | 2:10 | 13:55 | 250:45 | 14:30 | 14:30 | 98.1295 | 98.0511 | 254:20 | 254:20 | 96.5856 | 96.5369
49 | Raibag | 1 | 1 | 0:00 | 0:00 | 35:10 | 1:40 | 36:50 | 396:51 | 36:50 | 36:50 | 95.0493 | 95.0493 | 396:51 | 396:51 | 94.5963 | 94.5963
50 | Kudachi | 1 | 1 | 1:00 | 2:20 | 9:35 | 1:00 | 10:35 | 452:45 | 11:35 | 11:35 | 98.5775 | 98.4431 | 455:05 | 455:05 | 93.8351 | 93.8033
51 | Athani | 7 | 7 | 35:15 | 281:11 | 412:06 | 68:08 | 480:14 | 2074:27 | 515:29 | 73:38 | 90.7789 | 90.1021 | 2355:38 | 336:31 | 95.9647 | 95.4178
52 | Chikkodi | 4 | 4 | 0:00 | 16:20 | 6:46 | 7:59 | 14:45 | 362:53 | 14:45 | 3:41 | 99.5044 | 99.5044 | 379:13 | 94:48 | 98.7647 | 98.7091
53 | Nippani | 5 | 5 | 0:00 | 0:00 | 50:10 | 22:35 | 72:45 | 961:52 | 72:45 | 14:33 | 98.0444 | 98.0444 | 961:52 | 192:22 | 97.3805 | 97.3805
54 | Sadalaga | 1 | 1 | 9:23 | 32:26 | 7:45 | 1:15 | 9:00 | 230:05 | 18:23 | 18:23 | 98.7903 | 97.5291 | 262:31 | 262:31 | 96.8671 | 96.4254
55 | Muddebihal | 2 | 2 | 1:20 | 84:05 | 19:10 | 1:50 | 21:00 | 621:45 | 22:20 | 11:10 | 98.5887 | 98.4991 | 705:50 | 352:55 | 95.767 | 95.1945
56 | Talikoti | 1 | 1 | 6:00 | 86:25 | 4:30 | 1:25 | 5:55 | 295:00 | 11:55 | 11:55 | 99.2047 | 98.3983 | 381:25 | 381:25 | 95.9831 | 94.8064
57 | B.Bagewadi | 1 | 1 | 1:48 | 27:51 | 6:12 | 0:36 | 6:48 | 147:02 | 8:36 | 8:36 | 99.086 | 98.8441 | 174:53 | 174:53 | 97.9979 | 97.6187
58 | Indi | 3 | 3 | 11:16 | 134:27 | 5:49 | 5:01 | 10:50 | 211:42 | 22:06 | 7:22 | 99.5146 | 99.0099 | 346:09 | 115:23 | 99.0391 | 98.4289
59 | Sindagi | 2 | 2 | 0:00 | 146:50 | 21:30 | 7:40 | 29:10 | 411:25 | 29:10 | 14:35 | 98.0399 | 98.0399 | 558:15 | 279:08 | 97.199 | 96.1993
60 | Guledgudda | 2 | 2 | 27:12 | 48:14 | 22:15 | 7:26 | 29:41 | 215:21 | 56:53 | 28:26 | 98.0052 | 96.1772 | 263:35 | 131:47 | 98.5338 | 98.2055
61 | Ilkal | 7 | 7 | 13:35 | 139:31 | 38:16 | 45:58 | 84:14 | 1998:36 | 97:49 | 13:58 | 98.3826 | 98.1218 | 2138:07 | 305:27 | 96.1123 | 95.8409
62 | Kerur | 1 | 1 | 0:00 | 27:58 | 7:02 | 2:10 | 9:12 | 284:33 | 9:12 | 9:12 | 98.7634 | 98.7634 | 312:31 | 312:31 | 96.1254 | 95.7446
63 | Hungund | 4 | 4 | 9:52 | 90:31 | 43:15 | 22:43 | 65:58 | 1093:12 | 75:50 | 18:57 | 97.7834 | 97.4518 | 1183:43 | 295:56 | 96.2786 | 95.9705
64 | Badami | 2 | 2 | 0:12 | 17:13 | 11:45 | 7:18 | 19:03 | 212:59 | 19:15 | 9:38 | 98.7198 | 98.7063 | 230:12 | 115:06 | 98.55 | 98.4327
65 | Jamkhandi | 6 | 6 | 2:00 | 48:50 | 29:10 | 3:25 | 32:35 | 1114:15 | 34:35 | 5:46 | 99.2701 | 99.2253 | 1163:05 | 193:51 | 97.4713 | 97.3605
66 | Mahalingapur | 2 | 2 | 0:20 | 15:21 | 17:35 | 1:56 | 19:31 | 349:53 | 19:51 | 9:56 | 98.6884 | 98.666 | 365:14 | 182:37 | 97.6179 | 97.5134
67 | Rannabelagali | 1 | 1 | 0:15 | 16:47 | 13:55 | 0:10 | 14:05 | 198:59 | 14:20 | 14:20 | 98.1071 | 98.0735 | 215:46 | 215:46 | 97.2905 | 97.062
68 | Rabakavi | 2 | 2 | 0:00 | 45:40 | 42:25 | 1:55 | 44:20 | 239:45 | 44:20 | 22:10 | 97.0206 | 97.0206 | 285:25 | 142:42 | 98.3677 | 98.0568
69 | Banahatti | 2 | 2 | 0:00 | 9:56 | 10:45 | 0:20 | 11:05 | 335:15 | 11:05 | 5:32 | 99.2552 | 99.2552 | 345:11 | 172:36 | 97.7175 | 97.6499
70 | Terdal | 2 | 2 | 1:10 | 27:40 | 22:20 | 1:35 | 23:55 | 479:27 | 25:05 | 12:32 | 98.3927 | 98.3143 | 507:07 | 253:34 | 96.7358 | 96.5474
71 | Mudhol | 4 | 4 | 2:24 | 103:41 | 28:03 | 8:51 | 36:54 | 851:11 | 39:18 | 9:50 | 98.7601 | 98.6794 | 954:52 | 238:43 | 97.1025 | 96.7495
72 | Bilagi | 1 | 1 | 1:00 | 27:54 | 7:30 | 1:25 | 8:55 | 216:53 | 9:55 | 9:55 | 98.8015 | 98.6671 | 244:47 | 244:47 | 97.0468 | 96.6669
73 | Lokapur | 2 | 2 | 0:00 | 7:49 | 48:40 | 9:25 | 58:05 | 768:35 | 58:05 | 29:02 | 96.0966 | 96.0966 | 776:24 | 388:12 | 94.7673 | 94.7141
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]

## RURAL (Incl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Apr-22
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 387:10 | 387:10 | 5505:33 | 2950:22 | 8455:55 | 8455:55 | 8843:05 | 192:14 | 74.4689 | 73.2999 | 8843:05 | 192:14 | 74.4689 | 73.2999
2 | Dharwad Rural | 91 | 91 | 60:35 | 60:35 | 16984:51 | 7363:00 | 1014.4938 | 1014.4938 | 1017.0181 | 268:13 | 62.8391 | 62.7466 | 1017.0181 | 268:13 | 62.8391 | 62.7466
3 | Gadag | 113 | 113 | 105:20 | 105:20 | 23309:01 | 3687:12 | 1124.8424 | 1124.8424 | 1129.2313 | 239:50 | 66.8188 | 66.6893 | 1129.2313 | 239:50 | 66.8188 | 66.6893
4 | Ron | 58 | 58 | 267:37 | 267:37 | 14520:42 | 1415:39 | 15936:21 | 15936:21 | 16203:58 | 279:23 | 61.8382 | 61.1974 | 16203:58 | 279:23 | 61.8382 | 61.1974
5 | Haveri | 204 | 204 | 2018:12 | 2018:12 | 2450.8479 | 10752:39 | 2898.875 | 2898.875 | 2982.9667 | 350:56 | 52.6328 | 51.2587 | 2982.9667 | 350:56 | 52.6328 | 51.2587
6 | Ranebennur | 201 | 201 | 1632:38 | 1632:38 | 2524.6611 | 10276:01 | 2952.8285 | 2952.8285 | 3020.8549 | 360:42 | 51.031 | 49.9029 | 3020.8549 | 360:42 | 51.031 | 49.9029
7 | Sirsi | 63 | 63 | 597:16 | 597:16 | 607:37 | 2438:26 | 3046:03 | 3046:03 | 3643:19 | 57:50 | 93.2847 | 91.968 | 3643:19 | 57:50 | 93.2847 | 91.968
8 | Dandeli | 25 | 25 | 4:58 | 4:58 | 372:16 | 634:46 | 1007:02 | 1007:02 | 1012:00 | 40:29 | 94.4054 | 94.3778 | 1012:00 | 40:29 | 94.4054 | 94.3778
9 | Karwar | 33 | 33 | 322:49 | 322:49 | 339:39 | 502:59 | 842:38 | 842:38 | 1165:27 | 35:19 | 96.4536 | 95.0949 | 1165:27 | 35:19 | 96.4536 | 95.0949
10 | Honnavar | 40 | 40 | 509:40 | 509:40 | 516:01 | 679:05 | 1195:06 | 1195:06 | 1704:46 | 42:37 | 95.8503 | 94.0807 | 1704:46 | 42:37 | 95.8503 | 94.0807
11 | Belagavi | 149 | 149 | 1452:49 | 1452:49 | 16899:11 | 6408:04 | 23307:15 | 23307:15 | 1031.6694 | 166:10 | 78.2744 | 76.9201 | 1031.6694 | 166:10 | 78.2744 | 76.9201
12 | Bailhongal | 193 | 193 | 2284:40 | 2284:40 | 1936.1694 | 6009:09 | 2186.5507 | 2186.5507 | 2281.7451 | 283:44 | 62.2357 | 60.5916 | 2281.7451 | 283:44 | 62.2357 | 60.5916
13 | Ramdurg | 88 | 88 | 548:55 | 548:55 | 1123.4403 | 2736:32 | 1237.4625 | 1237.4625 | 1260.334 | 343:44 | 53.1264 | 52.2601 | 1260.334 | 343:44 | 53.1264 | 52.2601
14 | Ghataprabha | 168 | 168 | 693:28 | 693:28 | 1536.884 | 5868:12 | 1781.3924 | 1781.3924 | 1810.2868 | 258:37 | 64.6549 | 64.0816 | 1810.2868 | 258:37 | 64.6549 | 64.0816
15 | Raibag | 175 | 175 | 850:55 | 850:55 | 1808.6736 | 4709:21 | 2004.8965 | 2004.8965 | 2040.3514 | 279:49 | 61.8115 | 61.1362 | 2040.3514 | 279:49 | 61.8115 | 61.1362
16 | Athani | 200 | 200 | 1579:00 | 1579:00 | 1697.191 | 4934:10 | 1902.7812 | 1902.7812 | 1968.5729 | 236:14 | 68.287 | 67.1905 | 1968.5729 | 236:14 | 68.287 | 67.1905
17 | Chikkodi | 192 | 192 | 911:22 | 911:22 | 1958.1729 | 4750:36 | 2156.1146 | 2156.1146 | 2194.0882 | 274:16 | 62.5675 | 61.9082 | 2194.0882 | 274:16 | 62.5675 | 61.9082
18 | Vijayapur | 183 | 183 | 985:20 | 985:20 | 1969.1 | 6169:46 | 2226.1736 | 2226.1736 | 2267.2292 | 297:20 | 59.4504 | 58.7026 | 2267.2292 | 297:20 | 59.4504 | 58.7026
19 | Indi | 259 | 259 | 1037:24 | 1037:24 | 2574.8458 | 5591:36 | 2807.8292 | 2807.8292 | 2851.0542 | 264:11 | 63.8632 | 63.3069 | 2851.0542 | 264:11 | 63.8632 | 63.3069
20 | B.Bagewadi | 149 | 149 | 1169:20 | 1169:20 | 1512.2146 | 4869:55 | 1715.1278 | 1715.1278 | 1763.85 | 284:07 | 61.6303 | 60.5403 | 1763.85 | 284:07 | 61.6303 | 60.5403
21 | Bagalkot | 198 | 198 | 895:07 | 895:07 | 2169.325 | 5235:53 | 2387.4868 | 2387.4868 | 2424.7833 | 293:55 | 59.8066 | 59.1787 | 2424.7833 | 293:55 | 59.8066 | 59.1787
22 | Jamkhandi | 213 | 213 | 1204:22 | 1204:22 | 2412.5549 | 2941:48 | 2535.1299 | 2535.1299 | 2585.3118 | 291:18 | 60.3266 | 59.5413 | 2585.3118 | 291:18 | 60.3266 | 59.5413
23 | Mudhol | 195 | 195 | 551:07 | 551:07 | 2698.7271 | 2773:52 | 2814.3049 | 2814.3049 | 2837.2681 | 349:12 | 51.8922 | 51.4997 | 2837.2681 | 349:12 | 51.8922 | 51.4997
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2022 |  |  |  | Reliability for cumulative period from Apr-22 to May-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 243:11 | 630:21 | 6102:22 | 2397:15 | 8499:37 | 16955:32 | 8742:48 | 190:04 | 75.1647 | 74.4542 | 17585:53 | 382:18 | 74.8225 | 73.8865
2 | Dharwad Rural | 92 | 92 | 355:55 | 416:30 | 16771:46 | 5105:25 | 21877:11 | 1926.0431 | 22233:06 | 241:40 | 68.0382 | 67.5183 | 1943.3972 | 506:58 | 65.6799 | 65.3707
3 | Gadag | 113 | 113 | 317:30 | 422:50 | 22306:43 | 5964:36 | 1177.9715 | 2302.8139 | 1191.2007 | 253:00 | 66.3725 | 65.9948 | 2320.4319 | 492:50 | 66.592 | 66.3364
4 | Ron | 59 | 59 | 320:20 | 587:57 | 15727:55 | 1400:47 | 17128:42 | 1377.7104 | 17449:02 | 295:45 | 60.9789 | 60.2491 | 1402.2083 | 570:23 | 61.7196 | 61.0389
5 | Haveri | 205 | 205 | 2696:43 | 4714:55 | 2222.7917 | 1045.9306 | 3268.7222 | 6167.5972 | 3381.0854 | 395:50 | 48.5646 | 46.7965 | 6364.0521 | 745:04 | 50.679 | 49.1079
6 | Ranebennur | 204 | 204 | 1723:37 | 3356:15 | 2460.7118 | 19182:42 | 3259.991 | 6212.8194 | 3331.8083 | 391:59 | 48.4505 | 47.3149 | 6352.6632 | 747:22 | 50.0738 | 48.95
7 | Sirsi | 63 | 63 | 396:53 | 994:09 | 798:36 | 3201:18 | 3999:54 | 7045:57 | 4396:47 | 69:47 | 91.4663 | 90.6196 | 8040:06 | 127:37 | 92.3606 | 91.2827
8 | Dandeli | 25 | 25 | 278:09 | 283:07 | 378:30 | 506:37 | 885:07 | 1892:09 | 1163:16 | 46:32 | 95.2413 | 93.7459 | 2175:16 | 87:01 | 94.8302 | 94.0566
9 | Karwar | 33 | 33 | 315:09 | 637:58 | 321:58 | 643:52 | 965:50 | 1808:28 | 1280:59 | 38:49 | 96.0662 | 94.7826 | 2446:26 | 74:08 | 96.2567 | 94.9362
10 | Honnavar | 40 | 40 | 747:15 | 1256:55 | 588:20 | 1202:16 | 1790:36 | 2985:42 | 2537:51 | 63:27 | 93.9832 | 91.4723 | 4242:37 | 106:04 | 94.9015 | 92.7551
11 | Belagavi | 149 | 149 | 730:59 | 2183:48 | 15216:33 | 4259:01 | 19475:34 | 1782.6174 | 20206:33 | 135:37 | 82.4317 | 81.7723 | 1873.609 | 301:47 | 80.3871 | 79.386
12 | Bailhongal | 193 | 193 | 1302:00 | 3586:40 | 1965.2722 | 6516:39 | 2236.7993 | 4423.35 | 2291.0493 | 284:54 | 62.6141 | 61.7073 | 4572.7944 | 568:38 | 62.428 | 61.1586
13 | Ramdurg | 88 | 88 | 429:49 | 978:44 | 1188.7319 | 3608:59 | 1339.1062 | 2576.5687 | 1357.0153 | 370:06 | 50.9125 | 50.256 | 2617.3493 | 713:49 | 52.0013 | 51.2416
14 | Ghataprabha | 168 | 168 | 328:42 | 1022:10 | 1596.35 | 4386:09 | 1779.1063 | 3560.4986 | 1792.8021 | 256:07 | 65.839 | 65.576 | 3603.0889 | 514:44 | 65.2566 | 64.8411
15 | Raibag | 177 | 177 | 311:39 | 1162:34 | 1810.4215 | 3902:28 | 1973.0243 | 3977.9208 | 1986.0097 | 269:17 | 64.0418 | 63.8052 | 4026.3611 | 545:57 | 63.1572 | 62.7085
16 | Athani | 201 | 201 | 990:57 | 2569:57 | 1525.0035 | 5352:55 | 1748.0417 | 3650.8229 | 1789.3312 | 213:39 | 71.946 | 71.2834 | 3757.9042 | 448:42 | 70.2241 | 69.3508
17 | Chikkodi | 192 | 192 | 627:15 | 1538:37 | 1980.9264 | 2125:13 | 2069.4771 | 4225.5917 | 2095.6125 | 261:57 | 65.2306 | 64.7915 | 4289.7007 | 536:13 | 63.9208 | 63.3735
18 | Vijayapur | 189 | 189 | 958:18 | 1943:38 | 2543.1111 | 5502:47 | 2772.3938 | 4998.5674 | 2812.3229 | 357:07 | 52.6815 | 52 | 5079.5521 | 645:01 | 56.6435 | 55.9411
19 | Indi | 259 | 259 | 1969:19 | 3006:43 | 2866.9146 | 7124:07 | 3163.7528 | 5971.5819 | 3245.8076 | 300:46 | 60.5959 | 59.5739 | 6096.8618 | 564:58 | 62.2028 | 61.4098
20 | B.Bagewadi | 151 | 151 | 904:54 | 2074:14 | 1633.2486 | 5807:05 | 1875.2104 | 3590.3382 | 1912.9146 | 304:02 | 59.94 | 59.1345 | 3676.7646 | 584:23 | 61.0212 | 60.0829
21 | Bagalkot | 198 | 198 | 1023:00 | 1918:07 | 2142.8167 | 9598:43 | 2542.7632 | 4930.25 | 2585.3882 | 313:23 | 58.5734 | 57.879 | 5010.1715 | 607:18 | 59.1799 | 58.5182
22 | Jamkhandi | 213 | 213 | 587:11 | 1791:33 | 2485.3806 | 3596:22 | 2635.2292 | 5170.359 | 2659.6951 | 299:41 | 60.0904 | 59.7199 | 5245.0069 | 590:59 | 60.2066 | 59.6321
23 | Mudhol | 196 | 196 | 450:04 | 1001:11 | 2770.875 | 4424:44 | 2955.2389 | 5769.5438 | 2973.9917 | 364:10 | 51.3621 | 51.0535 | 5811.2597 | 711:35 | 51.7435 | 51.3946
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2022 |  |  |  | Reliability for cumulative period from Apr-22 to June-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 215:40 | 846:01 | 6554:33 | 1964:24 | 8518:57 | 1061.4368 | 8734:37 | 189:53 | 74.2785 | 73.6274 | 1096.6875 | 572:11 | 74.6432 | 73.8011
2 | Dharwad Rural | 92 | 92 | 140:50 | 557:20 | 16778:31 | 3557:03 | 20335:34 | 2773.3583 | 20476:24 | 222:34 | 69.3002 | 69.0876 | 2796.5806 | 729:33 | 66.8734 | 66.596
3 | Gadag | 113 | 113 | 285:25 | 708:15 | 21799:50 | 3859:03 | 1069.1201 | 3371.934 | 1081.0125 | 229:36 | 68.4625 | 68.1117 | 3401.4444 | 722:26 | 67.2087 | 66.9217
4 | Ron | 59 | 59 | 204:30 | 792:27 | 15036:05 | 1155:21 | 16191:26 | 2052.3535 | 16395:56 | 277:54 | 61.8846 | 61.4032 | 2085.3722 | 848:17 | 61.774 | 61.159
5 | Haveri | 205 | 205 | 1588:16 | 6303:11 | 2378.7465 | 11715:43 | 2866.9014 | 9034.4986 | 2933.0792 | 343:23 | 53.3837 | 52.3077 | 9297.1312 | 1088:27 | 51.5706 | 50.1628
6 | Ranebennur | 205 | 205 | 1155:23 | 4511:38 | 2571.3514 | 8863:58 | 2940.6833 | 9153.5028 | 2988.8243 | 349:55 | 52.184 | 51.4012 | 9341.4875 | 1093:38 | 50.9327 | 49.925
7 | Sirsi | 62 | 62 | 585:04 | 1579:13 | 754:47 | 2147:46 | 2902:33 | 9948:30 | 3487:37 | 56:15 | 93.4979 | 92.1872 | 11527:43 | 185:56 | 92.6529 | 91.4867
8 | Dandeli | 25 | 25 | 82:04 | 365:11 | 280:46 | 371:50 | 652:36 | 2544:45 | 734:40 | 29:23 | 96.3744 | 95.9185 | 2909:56 | 116:24 | 95.3393 | 94.6705
9 | Karwar | 29 | 29 | 369:00 | 1006:58 | 419:31 | 761:41 | 1181:12 | 2989:40 | 1550:12 | 53:27 | 94.3429 | 92.5757 | 3996:38 | 137:49 | 95.2797 | 93.6898
10 | Honnavar | 40 | 40 | 632:18 | 1889:13 | 654:36 | 1334:40 | 1989:16 | 4974:58 | 2621:34 | 65:32 | 93.0928 | 90.8973 | 6864:11 | 171:36 | 94.3052 | 92.1426
11 | Belagavi | 149 | 149 | 461:47 | 2645:35 | 14992:54 | 3018:00 | 18010:54 | 2533.0715 | 18472:41 | 123:59 | 83.2113 | 82.7809 | 2643.3042 | 425:46 | 81.3182 | 80.5052
12 | Bailhongal | 193 | 193 | 1597:58 | 5184:38 | 1907.8556 | 5162:26 | 2122.9569 | 6546.3069 | 2189.5389 | 272:16 | 63.3341 | 62.1841 | 6762.3333 | 840:55 | 62.7267 | 61.4967
13 | Ramdurg | 88 | 88 | 544:17 | 1523:01 | 1220.2785 | 3116:36 | 1350.1368 | 3926.7056 | 1372.8153 | 374:24 | 48.8585 | 47.9994 | 3990.1646 | 1088:14 | 50.9652 | 50.1728
14 | Ghataprabha | 170 | 170 | 532:08 | 1554:18 | 1527.8313 | 2084:42 | 1614.6938 | 5175.1924 | 1636.866 | 231:05 | 68.3393 | 67.9046 | 5239.9549 | 739:46 | 66.5469 | 66.1283
15 | Raibag | 178 | 178 | 511:06 | 1673:40 | 1754.9181 | 1578:02 | 1820.6694 | 5798.5903 | 1841.9653 | 248:21 | 65.9051 | 65.5063 | 5868.3264 | 791:14 | 64.2018 | 63.7713
16 | Athani | 201 | 201 | 661:13 | 3231:10 | 1662.8292 | 2032:14 | 1747.5056 | 5398.3285 | 1775.0562 | 211:57 | 71.0198 | 70.5629 | 5532.9604 | 660:39 | 70.4864 | 69.7504
17 | Chikkodi | 191 | 191 | 443:39 | 1982:16 | 1912.2097 | 1929:33 | 1992.6076 | 6218.1993 | 2011.0931 | 252:42 | 65.225 | 64.9024 | 6300.7937 | 791:43 | 64.2242 | 63.749
18 | Vijayapur | 190 | 190 | 745:36 | 2689:14 | 2504.3833 | 4392:19 | 2687.3965 | 7685.9639 | 2718.4632 | 343:23 | 52.8527 | 52.3077 | 7798.0153 | 985:01 | 55.5468 | 54.8987
19 | Indi | 261 | 261 | 1756:20 | 4763:03 | 2735.9396 | 9661:58 | 3138.5215 | 9110.1035 | 3211.7021 | 295:20 | 59.9167 | 58.9821 | 9308.5639 | 855:58 | 61.6433 | 60.8077
20 | B.Bagewadi | 151 | 151 | 423:46 | 2498:00 | 1574.9521 | 4895:05 | 1778.9139 | 5369.2521 | 1796.5708 | 285:33 | 60.7304 | 60.3406 | 5473.3354 | 869:56 | 60.9253 | 60.1679
21 | Bagalkot | 198 | 198 | 1050:23 | 2968:30 | 2134.1361 | 6714:09 | 2413.8924 | 7344.1424 | 2457.6583 | 297:54 | 59.3621 | 58.6253 | 7467.8299 | 905:11 | 59.24 | 58.5535
22 | Jamkhandi | 213 | 213 | 969:31 | 2761:04 | 2328.3472 | 1822:39 | 2404.291 | 7574.65 | 2444.6875 | 275:27 | 62.3742 | 61.742 | 7689.6944 | 866:27 | 60.9212 | 60.3276
23 | Mudhol | 196 | 196 | 477:05 | 1478:16 | 2676.9236 | 3771:11 | 2834.0562 | 8603.6 | 2853.9347 | 349:28 | 51.8018 | 51.4637 | 8665.1944 | 1061:03 | 51.7627 | 51.4174
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of July-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2022 |  |  |  | Reliability for cumulative period from Apr-22 to July-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 47 | 47 | 55:28 | 901:29 | 6392:33 | 2034:15 | 8426:48 | 1412.5535 | 8482:16 | 180:28 | 75.9014 | 75.7428 | 1450.1153 | 740:29 | 75.3653 | 74.7102
2 | Dharwad Rural | 92 | 92 | 188:49 | 746:09 | 18234:45 | 3190:52 | 21425:37 | 3666.0924 | 21614:26 | 234:56 | 68.698 | 68.4221 | 3697.1819 | 964:29 | 67.337 | 67.06
3 | Gadag | 113 | 113 | 127:10 | 835:25 | 23666:03 | 3637:13 | 1137.6361 | 4509.5701 | 1142.9347 | 242:45 | 67.5239 | 67.3727 | 4544.3792 | 965:11 | 67.2888 | 67.0363
4 | Ron | 59 | 59 | 70:20 | 862:47 | 15601:45 | 1094:58 | 16696:43 | 2748.05 | 16767:03 | 284:11 | 61.963 | 61.8028 | 2783.9993 | 1132:28 | 61.822 | 61.3226
5 | Haveri | 205 | 205 | 1015:31 | 7318:42 | 2321.4285 | 19500:54 | 3133.966 | 12168.4646 | 3176.2792 | 371:51 | 50.685 | 50.0192 | 12473.4104 | 1460:18 | 51.3456 | 50.1263
6 | Ranebennur | 205 | 205 | 683:25 | 5195:03 | 2569.4653 | 13906:17 | 3148.8937 | 12302.3965 | 3177.3694 | 371:59 | 50.4501 | 50.0021 | 12518.8569 | 1465:37 | 50.8101 | 49.9446
7 | Sirsi | 63 | 63 | 562:38 | 2141:51 | 698:22 | 2157:25 | 2855:47 | 12804:17 | 3418:25 | 54:16 | 93.9073 | 92.7069 | 14946:08 | 237:14 | 93.0587 | 91.8975
8 | Dandeli | 26 | 26 | 55:25 | 420:36 | 352:43 | 989:43 | 1342:26 | 3887:11 | 1397:51 | 53:46 | 93.0602 | 92.7737 | 4307:47 | 165:41 | 94.8939 | 94.3414
9 | Karwar | 30 | 30 | 439:21 | 1446:19 | 527:21 | 1148:26 | 1675:47 | 4665:27 | 2115:08 | 70:30 | 92.492 | 90.5236 | 6111:46 | 203:44 | 94.6887 | 93.0422
10 | Honnavar | 41 | 41 | 409:14 | 2298:27 | 859:59 | 1791:14 | 2651:13 | 7626:11 | 3060:27 | 74:39 | 91.3086 | 89.9671 | 9924:38 | 242:04 | 93.6474 | 91.7328
11 | Belagavi | 149 | 149 | 334:20 | 2979:55 | 16264:52 | 4246:41 | 20511:33 | 3387.7194 | 20845:53 | 139:54 | 81.4971 | 81.1955 | 3511.8826 | 565:40 | 81.3636 | 80.6806
12 | Bailhongal | 192 | 192 | 912:34 | 6097:12 | 1971.4493 | 6480:56 | 2241.4882 | 8787.7951 | 2279.5118 | 284:56 | 62.3406 | 61.7018 | 9041.8451 | 1130:14 | 62.4838 | 61.3992
13 | Ramdurg | 88 | 88 | 765:46 | 2288:47 | 1277.5917 | 2603:33 | 1386.0729 | 5312.7785 | 1417.9799 | 386:43 | 49.1909 | 48.0213 | 5408.1444 | 1474:57 | 50.5144 | 49.6261
14 | Ghataprabha | 171 | 171 | 219:23 | 1773:41 | 1717.3097 | 3017:48 | 1843.0514 | 7018.2438 | 1852.1924 | 259:57 | 65.232 | 65.0596 | 7092.1472 | 995:23 | 66.3587 | 66.0045
15 | Raibag | 178 | 178 | 172:23 | 1846:03 | 1774.5861 | 2081:09 | 1861.3007 | 7659.891 | 1868.4833 | 251:56 | 66.2686 | 66.1384 | 7736.8097 | 1043:10 | 64.727 | 64.3728
16 | Athani | 200 | 200 | 483:35 | 3714:45 | 1702.0917 | 1936:22 | 1782.7736 | 7181.1021 | 1802.9229 | 216:21 | 71.2456 | 70.9206 | 7335.8833 | 880:18 | 70.5693 | 69.9349
17 | Chikkodi | 191 | 191 | 422:43 | 2404:59 | 2094.0819 | 2250:21 | 2187.8465 | 8406.0458 | 2205.4597 | 277:08 | 63.0494 | 62.7519 | 8506.2535 | 1068:51 | 63.9256 | 63.4956
18 | Vijayapur | 190 | 190 | 238:20 | 2927:34 | 2374.8465 | 6326:41 | 2638.4583 | 10324.4222 | 2648.3889 | 334:32 | 55.2044 | 55.0358 | 10446.4042 | 1319:33 | 55.4598 | 54.9335
19 | Indi | 264 | 264 | 999:56 | 5762:59 | 2993.9174 | 9216:31 | 3377.9389 | 12488.0424 | 3419.6028 | 310:52 | 58.7251 | 58.216 | 12728.1667 | 1157:06 | 61.2269 | 60.4814
20 | B.Bagewadi | 150 | 150 | 411:59 | 2909:59 | 1568.4986 | 5487:22 | 1797.1389 | 7166.391 | 1814.3049 | 290:17 | 61.3519 | 60.9827 | 7287.6403 | 1166:01 | 60.8394 | 60.1768
21 | Bagalkot | 198 | 198 | 701:21 | 3669:51 | 2210.434 | 6694:36 | 2489.3757 | 9833.5181 | 2518.5986 | 305:17 | 59.4432 | 58.9671 | 9986.4285 | 1210:29 | 59.2916 | 58.6586
22 | Jamkhandi | 213 | 213 | 235:53 | 2996:57 | 2374.0111 | 2028:27 | 2458.5299 | 10033.1799 | 2468.3583 | 278:07 | 62.7665 | 62.6176 | 10158.0528 | 1144:34 | 61.3901 | 60.9095
23 | Mudhol | 196 | 196 | 169:35 | 1647:51 | 2767.3903 | 2590:12 | 2875.3153 | 11478.9153 | 2882.3812 | 352:57 | 52.6775 | 52.5612 | 11547.5757 | 1413:59 | 51.9952 | 51.708
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of Aug-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Aug-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Aug-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 47 | 47 | 86:55 | 988:24 | 4779:04 | 1475:27 | 6254:31 | 1673.1583 | 6341:26 | 134:55 | 82.1136 | 81.865 | 1714.3417 | 875:25 | 76.7326 | 76.1599
2 | Dharwad Rural | 93 | 93 | 170:35 | 916:44 | 16413:20 | 3054:27 | 19467:47 | 4477.25 | 19638:22 | 211:10 | 71.8641 | 71.6176 | 4515.4472 | 1165:17 | 68.5343 | 68.2659
3 | Gadag | 113 | 113 | 126:00 | 961:25 | 23205:54 | 4216:19 | 1142.5924 | 5652.1625 | 1147.8424 | 243:47 | 67.3825 | 67.2326 | 5692.2215 | 1208:58 | 67.3078 | 67.0761
4 | Ron | 59 | 59 | 198:42 | 1061:29 | 15738:05 | 946:10 | 16684:15 | 3443.2271 | 16882:57 | 286:09 | 61.9914 | 61.5388 | 3487.4556 | 1418:38 | 61.8564 | 61.3664
5 | Haveri | 205 | 205 | 1819:29 | 9138:11 | 2189.3618 | 1021.6132 | 3210.975 | 15379.4396 | 3286.7868 | 384:48 | 49.4732 | 48.2803 | 15760.1972 | 1845:06 | 50.9662 | 49.7523
6 | Ranebennur | 205 | 205 | 594:22 | 5789:25 | 2827.3451 | 11501:15 | 3306.5639 | 15608.9604 | 3331.3292 | 390:01 | 47.9691 | 47.5794 | 15850.1861 | 1855:38 | 50.2345 | 49.4654
7 | Sirsi | 63 | 63 | 353:21 | 2495:12 | 767:05 | 998:08 | 1765:13 | 14569:30 | 2118:34 | 33:38 | 96.234 | 95.4801 | 17064:42 | 270:52 | 93.702 | 92.6234
8 | Dandeli | 27 | 27 | 29:02 | 449:38 | 437:04 | 973:26 | 1410:30 | 5297:41 | 1439:32 | 53:19 | 92.9784 | 92.8339 | 5747:19 | 212:52 | 94.6566 | 94.2031
9 | Karwar | 31 | 31 | 276:41 | 1723:00 | 391:13 | 702:59 | 1094:12 | 5759:39 | 1370:53 | 44:13 | 95.2558 | 94.0562 | 7482:39 | 241:23 | 94.9402 | 93.4266
10 | Honnavar | 43 | 43 | 378:30 | 2676:57 | 697:43 | 866:17 | 1564:00 | 9190:11 | 1942:30 | 45:10 | 95.1113 | 93.9282 | 11867:08 | 275:59 | 94.1796 | 92.4842
11 | Belagavi | 149 | 149 | 523:52 | 3503:47 | 18369:06 | 5301:41 | 23670:47 | 4374.0021 | 1008.1104 | 162:23 | 78.6473 | 78.1747 | 4519.9931 | 728:03 | 80.8133 | 80.1729
12 | Bailhongal | 194 | 194 | 618:55 | 6716:07 | 2170.0042 | 6032:27 | 2421.3563 | 11209.1514 | 2447.1444 | 302:44 | 59.738 | 59.3092 | 11488.9896 | 1421:19 | 62.2359 | 61.2931
13 | Ramdurg | 88 | 88 | 558:51 | 2847:38 | 1352.6271 | 2102:13 | 1440.2194 | 6752.9979 | 1463.5049 | 399:08 | 47.206 | 46.3525 | 6871.6493 | 1874:05 | 49.844 | 48.9628
14 | Ghataprabha | 171 | 171 | 315:33 | 2089:14 | 1928.9222 | 1844:03 | 2005.7576 | 9024.0014 | 2018.9056 | 283:21 | 62.1627 | 61.9146 | 9111.0528 | 1278:45 | 65.5085 | 65.1758
15 | Raibag | 177 | 177 | 235:24 | 2081:27 | 2048.9903 | 1476:57 | 2110.5299 | 9770.4208 | 2120.3382 | 287:30 | 61.5358 | 61.3571 | 9857.1479 | 1336:34 | 63.9215 | 63.6012
16 | Athani | 202 | 202 | 951:55 | 4666:40 | 1644.1931 | 2153:41 | 1733.9299 | 8915.0319 | 1773.5931 | 210:43 | 72.3103 | 71.6769 | 9109.4764 | 1082:19 | 71.1544 | 70.5252
17 | Chikkodi | 191 | 191 | 397:55 | 2802:54 | 2107.5444 | 2037:18 | 2192.4319 | 10598.4778 | 2209.0118 | 277:34 | 62.9719 | 62.6919 | 10715.2653 | 1346:25 | 63.7324 | 63.3328
18 | Vijayapur | 190 | 190 | 361:28 | 3289:02 | 2199.1806 | 5867:26 | 2443.6569 | 12768.0792 | 2458.7181 | 310:34 | 58.5118 | 58.2561 | 12905.1222 | 1630:07 | 56.0782 | 55.6067
19 | Indi | 266 | 266 | 2867:58 | 8630:57 | 3089.7382 | 10696:05 | 3535.4083 | 16023.4507 | 3654.9069 | 329:46 | 57.1258 | 55.6766 | 16383.0736 | 1478:10 | 60.6284 | 59.7448
20 | B.Bagewadi | 150 | 150 | 637:37 | 3547:36 | 1624.6764 | 4969:53 | 1831.7549 | 8998.1458 | 1858.3222 | 297:20 | 60.6074 | 60.0361 | 9145.9625 | 1463:21 | 60.7924 | 60.1483
21 | Bagalkot | 198 | 198 | 836:49 | 4506:40 | 2290.0889 | 6534:41 | 2562.3674 | 12395.8854 | 2597.2347 | 314:49 | 58.254 | 57.686 | 12583.6632 | 1525:18 | 59.0814 | 58.4615
22 | Jamkhandi | 213 | 213 | 734:49 | 3731:46 | 2430.2493 | 1671:38 | 2499.9007 | 12533.0806 | 2530.5181 | 285:08 | 62.1399 | 61.6762 | 12688.5708 | 1429:42 | 61.542 | 61.0649
23 | Mudhol | 197 | 197 | 471:36 | 2119:27 | 2818.4458 | 2486:13 | 2922.0382 | 14400.9535 | 2941.6882 | 358:23 | 52.1526 | 51.8309 | 14489.2639 | 1765:11 | 52.2214 | 51.9284
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of Sept-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Sept-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Sept-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 47 | 47 | 95:20 | 1083:44 | 7194:44 | 1755:16 | 8950:00 | 2046.075 | 9045:20 | 192:27 | 73.552 | 73.2703 | 2091.2306 | 1067:52 | 76.2112 | 75.6862
2 | Dharwad Rural | 93 | 93 | 192:00 | 1108:44 | 12985:43 | 3042:39 | 16028:22 | 5145.0986 | 16220:22 | 174:25 | 76.0628 | 75.776 | 5191.2958 | 1339:41 | 69.7685 | 69.4971
3 | Gadag | 113 | 113 | 509:44 | 1471:09 | 21740:59 | 5121:48 | 1119.2826 | 6771.4451 | 1140.5215 | 242:14 | 66.9828 | 66.3563 | 6832.7431 | 1451:12 | 67.2545 | 66.9581
4 | Ron | 61 | 61 | 160:02 | 1221:31 | 13159:45 | 1250:57 | 14410:42 | 4043.6729 | 14570:44 | 238:52 | 67.1888 | 66.8244 | 4094.5694 | 1610:59 | 63.7761 | 63.3202
5 | Haveri | 206 | 206 | 1432:59 | 10571:10 | 2703.6111 | 11433:13 | 3179.9951 | 18559.4347 | 3239.7028 | 377:26 | 48.5438 | 47.5776 | 18999.9 | 2213:35 | 50.7681 | 49.5997
6 | Ranebennur | 205 | 205 | 1064:57 | 6854:22 | 2899.8465 | 5845:40 | 3143.416 | 18752.3764 | 3187.7889 | 373:12 | 48.8875 | 48.166 | 19037.975 | 2228:50 | 50.0137 | 49.2524
7 | Sirsi | 62 | 62 | 310:17 | 2805:29 | 625:35 | 1995:02 | 2620:37 | 17190:07 | 2930:54 | 47:16 | 94.1294 | 93.4344 | 19995:36 | 322:31 | 93.6872 | 92.6569
8 | Dandeli | 27 | 27 | 12:01 | 461:39 | 173:54 | 344:23 | 518:17 | 5815:58 | 530:18 | 19:38 | 97.3339 | 97.2721 | 6277:37 | 232:30 | 95.0955 | 94.7062
9 | Karwar | 30 | 30 | 195:04 | 1918:04 | 265:36 | 606:42 | 872:18 | 6631:57 | 1067:22 | 35:35 | 95.9616 | 95.0585 | 8550:01 | 285:00 | 94.9666 | 93.5109
10 | Honnavar | 43 | 43 | 515:10 | 3192:07 | 496:32 | 584:35 | 1081:07 | 10271:18 | 1596:17 | 37:07 | 96.508 | 94.844 | 13463:25 | 313:06 | 94.5613 | 92.8711
11 | Belagavi | 149 | 149 | 235:57 | 3739:44 | 15261:00 | 4430:56 | 19691:56 | 5194.4993 | 19927:53 | 133:45 | 81.6444 | 81.4244 | 5350.3215 | 861:48 | 80.9495 | 80.378
12 | Bailhongal | 194 | 194 | 1151:10 | 7867:17 | 2052.4479 | 5851:23 | 2296.2556 | 13505.4069 | 2344.2208 | 290:00 | 60.5454 | 59.7213 | 13833.2104 | 1711:19 | 61.9587 | 61.0354
13 | Ramdurg | 89 | 89 | 749:57 | 3597:35 | 1190.3361 | 2901:08 | 1311.2167 | 8064.2146 | 1342.4646 | 362:01 | 50.8908 | 49.7204 | 8214.1139 | 2215:03 | 50.4868 | 49.5664
14 | Ghataprabha | 171 | 171 | 304:05 | 2393:19 | 1773.4521 | 2690:21 | 1885.55 | 10909.5514 | 1898.2201 | 266:25 | 63.2446 | 62.9977 | 11009.2729 | 1545:10 | 65.1374 | 64.8187
15 | Raibag | 180 | 180 | 528:45 | 2610:12 | 1922.0604 | 1636:04 | 1990.2299 | 11760.6507 | 2012.2611 | 268:18 | 63.1439 | 62.7359 | 11869.409 | 1582:35 | 64.2967 | 63.9666
16 | Athani | 203 | 203 | 432:35 | 5099:15 | 1602.7632 | 2036:31 | 1687.6181 | 10602.65 | 1705.6424 | 201:39 | 72.2887 | 71.9927 | 10815.1187 | 1278:38 | 71.4591 | 70.8872
17 | Chikkodi | 192 | 192 | 276:50 | 3079:44 | 1998.3354 | 1678:20 | 2068.266 | 12666.7437 | 2079.8007 | 259:59 | 64.0926 | 63.8923 | 12795.066 | 1599:23 | 63.9494 | 63.5842
18 | Vijayapur | 191 | 191 | 925:26 | 4214:28 | 2376.3174 | 5838:21 | 2619.5819 | 15387.6611 | 2658.1417 | 334:00 | 54.283 | 53.6101 | 15563.2639 | 1955:36 | 55.9761 | 55.4737
19 | Indi | 270 | 270 | 669:23 | 9300:20 | 3053.7035 | 7387:28 | 3361.5146 | 19384.9653 | 3389.4056 | 301:17 | 58.4998 | 58.1555 | 19772.4792 | 1757:33 | 60.7671 | 59.9828
20 | B.Bagewadi | 152 | 152 | 615:28 | 4163:04 | 1588.3424 | 4830:23 | 1789.6083 | 10787.7542 | 1815.2528 | 286:37 | 60.7542 | 60.1918 | 10961.2153 | 1730:43 | 61.2174 | 60.5938
21 | Bagalkot | 200 | 200 | 1195:45 | 5702:25 | 2137.0174 | 8408:30 | 2487.3715 | 14883.2569 | 2537.1944 | 304:28 | 58.5438 | 57.7134 | 15120.8576 | 1814:30 | 59.3354 | 58.6862
22 | Jamkhandi | 213 | 213 | 309:40 | 4041:26 | 2325.4882 | 2040:16 | 2410.4993 | 14943.5799 | 2423.4021 | 273:04 | 62.277 | 62.0751 | 15111.9729 | 1702:45 | 61.6625 | 61.2305
23 | Mudhol | 197 | 197 | 286:51 | 2406:18 | 2657.75 | 2808:27 | 2774.7687 | 17175.7222 | 2786.7208 | 339:30 | 53.0496 | 52.8474 | 17275.9847 | 2104:41 | 52.3572 | 52.079
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of Oct-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Oct-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Oct-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 47 | 47 | 75:13 | 1158:57 | 5703:24 | 1747:41 | 7451:05 | 2356.5368 | 7526:18 | 160:08 | 78.6917 | 78.4766 | 2404.8264 | 1228:00 | 76.5705 | 76.0904
2 | Dharwad Rural | 93 | 93 | 104:35 | 1213:19 | 12055:21 | 4102:24 | 16157:45 | 5818.3382 | 16262:20 | 174:52 | 76.648 | 76.4968 | 5868.8931 | 1514:33 | 70.7651 | 70.511
3 | Gadag | 113 | 113 | 219:25 | 1690:34 | 20701:06 | 4590:42 | 1053.825 | 7825.2701 | 1062.9674 | 225:46 | 69.9165 | 69.6555 | 7895.7104 | 1676:58 | 67.6401 | 67.3488
4 | Ron | 61 | 61 | 134:05 | 1355:36 | 14688:15 | 833:45 | 15522:00 | 4690.4229 | 15656:05 | 256:39 | 65.7985 | 65.5031 | 4746.9062 | 1867:38 | 64.0691 | 63.6364
5 | Haveri | 206 | 206 | 1642:43 | 12213:53 | 2895.8431 | 10622:38 | 3338.4528 | 21897.8875 | 3406.8993 | 396:55 | 47.7223 | 46.6505 | 22406.7993 | 2610:30 | 50.3269 | 49.1725
6 | Ranebennur | 205 | 205 | 442:57 | 7297:19 | 2918.2285 | 7051:48 | 3212.0535 | 21964.4299 | 3230.5097 | 378:12 | 49.4563 | 49.1659 | 22268.4847 | 2607:03 | 49.9329 | 49.2398
7 | Sirsi | 63 | 63 | 307:10 | 3112:39 | 514:25 | 1281:58 | 1796:23 | 18986:30 | 2103:33 | 33:23 | 96.1675 | 95.5121 | 22099:09 | 350:47 | 94.1321 | 93.1702
8 | Dandeli | 27 | 27 | 33:20 | 494:59 | 392:00 | 717:51 | 1109:51 | 6925:49 | 1143:11 | 42:20 | 94.4751 | 94.3091 | 7420:48 | 274:51 | 95.0056 | 94.6487
9 | Karwar | 30 | 30 | 222:42 | 2140:46 | 279:54 | 379:55 | 659:49 | 7291:46 | 882:31 | 29:25 | 97.0438 | 96.0461 | 9432:32 | 314:25 | 95.2675 | 93.8782
10 | Honnavar | 43 | 43 | 223:16 | 3415:23 | 324:15 | 310:08 | 634:23 | 10905:41 | 857:39 | 19:57 | 98.0171 | 97.3192 | 14321:04 | 333:03 | 95.0619 | 93.5154
11 | Belagavi | 149 | 149 | 222:05 | 3961:49 | 15898:22 | 3954:40 | 19853:02 | 6021.709 | 20075:07 | 134:44 | 82.0912 | 81.8908 | 6186.7847 | 996:32 | 81.1149 | 80.5972
12 | Bailhongal | 194 | 194 | 678:49 | 8546:06 | 2083.1694 | 6183:55 | 2340.8326 | 15846.2396 | 2369.1167 | 293:05 | 61.0769 | 60.6066 | 16202.3271 | 2004:25 | 61.831 | 60.9733
13 | Ramdurg | 89 | 89 | 510:07 | 4107:42 | 1154.5944 | 3384:44 | 1295.625 | 9359.8396 | 1316.8799 | 355:07 | 53.0401 | 52.2697 | 9530.9937 | 2570:09 | 50.8567 | 49.958
14 | Ghataprabha | 171 | 171 | 197:13 | 2590:32 | 1762.7257 | 2990:58 | 1887.3493 | 12796.9007 | 1895.5667 | 266:03 | 64.3964 | 64.2413 | 12904.8396 | 1811:12 | 65.0301 | 64.7351
15 | Raibag | 182 | 182 | 216:22 | 2826:34 | 1885.5194 | 2418:04 | 1986.2722 | 13746.9229 | 1995.2875 | 263:07 | 64.7949 | 64.6351 | 13864.6965 | 1828:19 | 64.7044 | 64.402
16 | Athani | 203 | 203 | 402:20 | 5501:35 | 1617.9125 | 2004:10 | 1701.4194 | 12304.0694 | 1718.1833 | 203:08 | 72.9633 | 72.6969 | 12533.3021 | 1481:46 | 71.677 | 71.1493
17 | Chikkodi | 192 | 192 | 360:11 | 3439:55 | 2087.5833 | 2910:02 | 2208.8347 | 14875.5785 | 2223.8424 | 277:59 | 62.8892 | 62.6371 | 15018.9083 | 1877:22 | 63.7958 | 63.447
18 | Vijayapur | 191 | 191 | 99:36 | 4314:04 | 2559.6201 | 4962:59 | 2766.4111 | 18154.0722 | 2770.5611 | 348:08 | 53.278 | 53.2079 | 18333.825 | 2303:44 | 55.5853 | 55.1455
19 | Indi | 274 | 274 | 613:34 | 9913:54 | 2964.2187 | 6637:37 | 3240.7861 | 22625.7514 | 3266.3514 | 286:06 | 61.8462 | 61.5452 | 23038.8306 | 2018:00 | 61.4132 | 60.7087
20 | B.Bagewadi | 152 | 152 | 643:24 | 4806:28 | 1630.5813 | 4871:02 | 1833.541 | 12621.2951 | 1860.3493 | 293:44 | 61.0878 | 60.5189 | 12821.5646 | 2024:27 | 61.1987 | 60.583
21 | Bagalkot | 201 | 201 | 425:56 | 6128:21 | 2192.334 | 8004:27 | 2525.8528 | 17409.1097 | 2543.6 | 303:43 | 59.4631 | 59.1783 | 17664.4576 | 2109:11 | 59.5269 | 58.9332
22 | Jamkhandi | 213 | 213 | 111:04 | 4152:30 | 2369.2653 | 1626:46 | 2437.0472 | 17380.6271 | 2441.675 | 275:07 | 63.0918 | 63.0217 | 17553.6479 | 1977:53 | 61.8695 | 61.49
23 | Mudhol | 197 | 197 | 156:18 | 2562:36 | 2706.3132 | 3148:30 | 2837.5007 | 20013.2229 | 2844.0132 | 346:29 | 53.5369 | 53.4303 | 20119.9979 | 2451:10 | 52.5281 | 52.2748
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of Nov-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Nov-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Nov-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 47 | 47 | 60:39 | 1219:36 | 7053:05 | 620:16 | 7673:21 | 2676.2597 | 7734:00 | 164:33 | 77.3246 | 77.1454 | 2727.0764 | 1392:33 | 76.6632 | 76.2201
2 | Dharwad Rural | 93 | 93 | 133:55 | 1347:14 | 12983:09 | 1825:58 | 14809:07 | 6435.3847 | 14943:02 | 160:41 | 77.8836 | 77.6836 | 6491.5194 | 1675:14 | 71.6403 | 71.3929
3 | Gadag | 113 | 113 | 138:28 | 1829:02 | 23305:10 | 786:28 | 1003.8181 | 8829.0882 | 1009.5875 | 214:26 | 70.3888 | 70.2187 | 8905.2979 | 1891:23 | 67.9781 | 67.7017
4 | Ron | 61 | 61 | 80:25 | 1436:01 | 14925:08 | 705:47 | 15630:55 | 5341.7111 | 15711:20 | 257:34 | 64.4105 | 64.2274 | 5401.5451 | 2125:12 | 64.1111 | 63.709
5 | Haveri | 206 | 206 | 1455:14 | 13669:07 | 2668.9979 | 3828:48 | 2828.5312 | 24726.4188 | 2889.166 | 336:36 | 54.2309 | 53.2497 | 25295.9653 | 2947:06 | 50.8069 | 49.6738
6 | Ranebennur | 206 | 206 | 894:41 | 8192:00 | 2719.5271 | 2857:59 | 2838.6097 | 24803.0396 | 2875.8882 | 335:03 | 54.0678 | 53.4646 | 25144.3729 | 2929:26 | 50.6545 | 49.9754
7 | Sirsi | 63 | 63 | 267:59 | 3380:38 | 643:00 | 1255:47 | 1898:47 | 20885:17 | 2166:46 | 34:24 | 95.814 | 95.2232 | 1011.0799 | 385:10 | 94.3389 | 93.4226
8 | Dandeli | 27 | 27 | 63:43 | 558:42 | 423:34 | 240:33 | 664:07 | 7589:56 | 727:50 | 26:57 | 96.5838 | 96.256 | 8148:38 | 301:48 | 95.1996 | 94.8463
9 | Karwar | 30 | 30 | 194:35 | 2335:21 | 276:45 | 347:33 | 624:18 | 7916:04 | 818:53 | 27:18 | 97.1097 | 96.2089 | 10251:25 | 341:43 | 95.494 | 94.1647
10 | Honnavar | 43 | 43 | 435:21 | 3850:44 | 446:30 | 285:32 | 732:02 | 11637:43 | 1167:23 | 27:09 | 97.6356 | 96.2294 | 15488:27 | 360:12 | 95.3783 | 93.8491
11 | Belagavi | 149 | 149 | 500:09 | 4461:58 | 16954:32 | 1621:38 | 18576:10 | 6795.716 | 19076:19 | 128:02 | 82.6844 | 82.2182 | 6981.6313 | 1124:33 | 81.3079 | 80.7965
12 | Bailhongal | 199 | 199 | 2059:16 | 10605:22 | 2142.159 | 1895:35 | 2221.1417 | 18067.3812 | 2306.9444 | 278:13 | 62.7949 | 61.3577 | 18509.2715 | 2232:16 | 62.7906 | 61.8806
13 | Ramdurg | 89 | 89 | 541:08 | 4648:50 | 1233.2146 | 815:08 | 1267.1785 | 10627.0181 | 1289.7257 | 347:47 | 52.5401 | 51.6957 | 10820.7194 | 2917:57 | 51.0636 | 50.1717
14 | Ghataprabha | 171 | 171 | 322:10 | 2912:42 | 1752.6625 | 876:48 | 1789.1958 | 14586.0965 | 1802.6194 | 253:00 | 65.1229 | 64.8612 | 14707.459 | 2064:12 | 65.0415 | 64.7506
15 | Raibag | 182 | 182 | 326:31 | 3153:05 | 1783.9424 | 820:27 | 1818.1278 | 15565.0507 | 1831.7326 | 241:33 | 66.701 | 66.4518 | 15696.4292 | 2069:52 | 64.9499 | 64.6541
16 | Athani | 203 | 203 | 622:20 | 6123:55 | 1692.5083 | 939:44 | 1731.6639 | 14035.7333 | 1757.5944 | 207:48 | 71.5655 | 71.1397 | 14290.8965 | 1689:34 | 71.6633 | 71.1482
17 | Chikkodi | 193 | 193 | 269:00 | 3708:55 | 1965.7965 | 634:47 | 1992.2458 | 16867.8243 | 2003.4542 | 249:08 | 65.5916 | 65.398 | 17022.3625 | 2116:46 | 64.1811 | 63.853
18 | Vijayapur | 194 | 194 | 326:39 | 4640:43 | 2524.6021 | 1115:35 | 2571.0847 | 20725.1569 | 2584.6951 | 319:45 | 55.8233 | 55.5894 | 20918.5201 | 2587:51 | 56.2169 | 55.8084
19 | Indi | 275 | 275 | 2144:14 | 12058:08 | 2873.2694 | 1641:46 | 2941.6764 | 25567.4278 | 3031.0194 | 264:32 | 64.3433 | 63.2604 | 26069.85 | 2275:11 | 61.8965 | 61.1478
20 | B.Bagewadi | 152 | 152 | 1069:40 | 5876:08 | 1598.1174 | 1155:31 | 1646.2639 | 14267.559 | 1690.8333 | 266:58 | 63.8977 | 62.9203 | 14512.3979 | 2291:26 | 61.5305 | 60.8704
21 | Bagalkot | 203 | 203 | 284:28 | 6412:49 | 2289.9361 | 2218:26 | 2382.3708 | 19791.4806 | 2394.2236 | 283:04 | 60.8806 | 60.686 | 20058.6813 | 2371:28 | 60.043 | 59.5036
22 | Jamkhandi | 213 | 213 | 394:45 | 4547:15 | 2281.884 | 684:55 | 2310.4222 | 19691.0493 | 2326.8701 | 262:11 | 63.8432 | 63.5858 | 19880.5181 | 2240:04 | 62.1122 | 61.7476
23 | Mudhol | 197 | 197 | 363:38 | 2926:14 | 2659.1111 | 828:40 | 2693.6389 | 22706.8618 | 2708.7903 | 330:00 | 54.4224 | 54.166 | 22828.7882 | 2781:10 | 52.761 | 52.5073
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of Dec-2022
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Dec-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Dec-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 47 | 47 | 131:33 | 1351:09 | 7561:12 | 657:28 | 8218:40 | 3018.7042 | 8350:13 | 177:40 | 76.4966 | 76.1204 | 3075.0021 | 1570:13 | 76.6445 | 76.2089
2 | Dharwad Rural | 98 | 98 | 235:42 | 1582:56 | 15072:38 | 1500:11 | 16572:49 | 7125.9188 | 16808:31 | 171:31 | 77.2701 | 76.9468 | 7191.8743 | 1761:17 | 73.5587 | 73.314
3 | Gadag | 113 | 113 | 866:55 | 2695:57 | 23603:09 | 1628:38 | 1051.3243 | 9880.4125 | 1087.4458 | 230:58 | 69.9879 | 68.9567 | 9992.7437 | 2122:21 | 68.2046 | 67.8431
4 | Ron | 61 | 61 | 192:44 | 1628:45 | 15392:00 | 866:50 | 16258:50 | 6019.1625 | 16451:34 | 269:42 | 64.175 | 63.7503 | 6087.0274 | 2394:54 | 64.1183 | 63.7137
5 | Haveri | 208 | 208 | 1499:17 | 15168:24 | 2727.7326 | 3230:06 | 2862.3201 | 27588.7389 | 2924.7903 | 337:29 | 55.6092 | 54.6403 | 28220.7556 | 3256:14 | 51.7679 | 50.663
6 | Ranebennur | 207 | 207 | 921:44 | 9113:44 | 2788.966 | 2827:49 | 2906.7917 | 27709.8312 | 2945.1972 | 341:28 | 54.7017 | 54.1032 | 28089.5701 | 3256:46 | 51.3222 | 50.6551
7 | Sirsi | 63 | 63 | 480:05 | 3860:43 | 625:15 | 967:10 | 1592:25 | 22477:42 | 2072:30 | 32:54 | 96.6026 | 95.5784 | 1097.434 | 418:04 | 94.5941 | 93.6656
8 | Dandeli | 27 | 27 | 48:20 | 607:02 | 489:28 | 240:09 | 729:37 | 8319:33 | 777:57 | 28:49 | 96.3679 | 96.1273 | 8926:35 | 330:37 | 95.3313 | 94.9907
9 | Karwar | 30 | 30 | 274:09 | 2609:30 | 195:30 | 320:01 | 515:31 | 8431:35 | 789:40 | 26:19 | 97.6903 | 96.4621 | 11041:05 | 368:02 | 95.7416 | 94.4237
10 | Honnavar | 44 | 44 | 645:39 | 4496:23 | 435:47 | 253:31 | 689:18 | 12327:01 | 1334:57 | 30:20 | 97.8944 | 95.9221 | 16823:24 | 382:21 | 95.7552 | 94.2068
11 | Belagavi | 150 | 150 | 402:51 | 4864:49 | 17057:57 | 1612:46 | 18670:43 | 7573.6625 | 19073:34 | 127:09 | 83.27 | 82.909 | 7776.3632 | 1244:13 | 81.6396 | 81.1482
12 | Bailhongal | 201 | 201 | 845:12 | 11450:34 | 2259.2854 | 2318:40 | 2355.8965 | 20423.2778 | 2391.1132 | 285:30 | 62.1907 | 61.6255 | 20900.3847 | 2495:34 | 63.0515 | 62.1884
13 | Ramdurg | 89 | 89 | 494:40 | 5143:30 | 1280.2118 | 999:30 | 1321.8576 | 11948.8757 | 1342.4687 | 362:01 | 52.0892 | 51.3422 | 12163.1882 | 3279:58 | 51.1793 | 50.3036
14 | Ghataprabha | 171 | 171 | 172:24 | 3085:06 | 1794.8715 | 923:19 | 1833.3431 | 16419.4396 | 1840.5264 | 258:19 | 65.4151 | 65.2796 | 16547.9854 | 2322:31 | 65.0836 | 64.8102
15 | Raibag | 181 | 181 | 225:25 | 3378:30 | 1917.375 | 622:16 | 1943.3028 | 17508.3535 | 1952.6951 | 258:55 | 65.3662 | 65.1988 | 17649.1243 | 2340:13 | 64.825 | 64.5422
16 | Athani | 203 | 203 | 1221:55 | 7345:50 | 1615.1396 | 1034:08 | 1658.2285 | 15693.9618 | 1709.1417 | 202:04 | 73.6496 | 72.8406 | 16000.0382 | 1891:38 | 71.8872 | 71.3389
17 | Chikkodi | 194 | 194 | 310:25 | 4019:20 | 2036.4861 | 847:58 | 2071.8181 | 18939.6424 | 2084.7521 | 257:54 | 65.5501 | 65.335 | 19107.1146 | 2363:46 | 64.4993 | 64.1854
18 | Vijayapur | 200 | 200 | 617:51 | 5258:34 | 2715.959 | 1428:35 | 2775.4833 | 23500.6403 | 2801.2271 | 336:09 | 55.2341 | 54.8189 | 23719.7472 | 2846:22 | 57.2716 | 56.8732
19 | Indi | 275 | 275 | 508:29 | 12566:37 | 2855.6194 | 2077:27 | 2942.1799 | 28509.6076 | 2963.3667 | 258:37 | 65.4876 | 65.2391 | 29033.2167 | 2533:48 | 62.3013 | 61.609
20 | B.Bagewadi | 152 | 152 | 728:55 | 6605:03 | 1600.525 | 1290:06 | 1654.2792 | 15921.8382 | 1684.6507 | 266:00 | 64.8922 | 64.2477 | 16197.0486 | 2557:26 | 61.9095 | 61.2511
21 | Bagalkot | 207 | 207 | 995:02 | 7407:51 | 2355.5278 | 3245:42 | 2490.7653 | 22282.2458 | 2532.225 | 293:35 | 61.1849 | 60.5388 | 22590.9063 | 2619:14 | 60.8568 | 60.3146
22 | Jamkhandi | 213 | 213 | 289:21 | 4836:36 | 2388.0993 | 698:28 | 2417.2021 | 22108.2514 | 2429.2583 | 273:43 | 63.3924 | 63.2098 | 22309.7764 | 2513:47 | 62.2565 | 61.9125
23 | Mudhol | 200 | 200 | 293:53 | 3220:07 | 2814.8049 | 697:12 | 2843.8549 | 25550.7167 | 2856.1 | 342:44 | 54.1314 | 53.9339 | 25684.8882 | 3082:11 | 53.5442 | 53.3002
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of Jan-2023
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Jan-2023 |  |  |  | Reliability for cumulative period from Apr-22 to Jan-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 47 | 47 | 71:14 | 1422:23 | 7585:12 | 215:18 | 7800:30 | 3343.725 | 7871:44 | 167:29 | 77.6925 | 77.4888 | 3402.991 | 1737:42 | 76.7506 | 76.3385
2 | Dharwad Rural | 98 | 98 | 188:36 | 1771:32 | 15518:40 | 1014:34 | 16533:14 | 7814.8035 | 16721:50 | 170:38 | 77.3244 | 77.0657 | 7888.6174 | 1931:54 | 73.9402 | 73.6941
3 | Gadag | 113 | 113 | 82:30 | 2778:27 | 1013.1944 | 579:13 | 1037.3285 | 10917.741 | 1040.766 | 221:03 | 70.3874 | 70.2893 | 11033.5097 | 2343:24 | 68.4258 | 68.091
4 | Ron | 61 | 61 | 76:45 | 1705:30 | 15652:30 | 1170:50 | 16823:20 | 6720.1347 | 16900:05 | 277:03 | 62.9311 | 62.762 | 6791.1976 | 2671:57 | 63.998 | 63.6173
5 | Haveri | 209 | 209 | 1627:42 | 16796:06 | 2747.4444 | 2313:34 | 2843.8431 | 30432.5819 | 2911.6639 | 334:21 | 56.1068 | 55.06 | 31132.4194 | 3575:01 | 52.4149 | 51.3206
6 | Ranebennur | 209 | 209 | 1066:56 | 10180:40 | 2787.2875 | 1568:06 | 2852.625 | 30562.4562 | 2897.0806 | 332:41 | 55.9712 | 55.2851 | 30986.6507 | 3558:17 | 52.2118 | 51.5485
7 | Sirsi | 63 | 63 | 434:12 | 4294:55 | 701:22 | 780:03 | 1481:25 | 23959:07 | 1915:37 | 30:24 | 96.8394 | 95.9131 | 1177.2514 | 448:29 | 94.8216 | 93.8933
8 | Dandeli | 27 | 27 | 52:45 | 659:47 | 438:03 | 209:07 | 647:10 | 8966:43 | 699:55 | 25:55 | 96.7783 | 96.5157 | 9626:30 | 356:32 | 95.4779 | 95.1452
9 | Karwar | 31 | 31 | 178:13 | 2787:43 | 214:57 | 190:01 | 404:58 | 8836:33 | 583:11 | 18:49 | 98.2442 | 97.4715 | 11624:16 | 374:59 | 96.1186 | 94.8941
10 | Honnavar | 44 | 44 | 238:23 | 4734:46 | 397:16 | 236:13 | 633:29 | 12960:30 | 871:52 | 19:49 | 98.0649 | 97.3367 | 17695:16 | 402:10 | 95.9892 | 94.5239
11 | Belagavi | 150 | 150 | 158:55 | 5023:44 | 17571:40 | 1078:23 | 18650:03 | 8350.7479 | 18808:58 | 125:24 | 83.2885 | 83.1461 | 8560.0701 | 1369:37 | 81.8066 | 81.3506
12 | Bailhongal | 201 | 201 | 630:46 | 12081:20 | 2327.7174 | 1346:34 | 2383.8243 | 22807.1021 | 2410.1063 | 287:46 | 61.7425 | 61.3207 | 23310.491 | 2783:21 | 62.9189 | 62.1005
13 | Ramdurg | 89 | 89 | 103:08 | 5246:38 | 1318.3542 | 455:03 | 1337.3146 | 13286.1903 | 1341.6118 | 361:47 | 51.529 | 51.3733 | 13504.8 | 3641:45 | 51.2147 | 50.412
14 | Ghataprabha | 174 | 174 | 184:22 | 3269:28 | 1819.9639 | 602:09 | 1845.0535 | 18264.4931 | 1852.7354 | 255:33 | 65.7943 | 65.6519 | 18400.7208 | 2538:02 | 65.6966 | 65.4408
15 | Raibag | 181 | 181 | 261:26 | 3639:56 | 1884.1451 | 413:39 | 1901.3806 | 19409.734 | 1912.2736 | 253:34 | 66.1133 | 65.9192 | 19561.3979 | 2593:47 | 64.9555 | 64.6817
16 | Athani | 203 | 203 | 576:00 | 7921:50 | 1784.5118 | 634:56 | 1810.9674 | 17504.9292 | 1834.9674 | 216:57 | 71.2225 | 70.8411 | 17835.0056 | 2108:34 | 71.8199 | 71.2885
17 | Chikkodi | 197 | 197 | 547:55 | 4567:15 | 2053.8069 | 961:24 | 2093.8653 | 21033.5076 | 2116.6951 | 257:52 | 65.7137 | 65.3399 | 21223.8097 | 2585:39 | 65.1081 | 64.7925
18 | Vijayapur | 204 | 204 | 372:32 | 5631:06 | 2781.5597 | 988:12 | 2822.7347 | 26323.375 | 2838.2569 | 333:55 | 55.3647 | 55.1193 | 26558.0042 | 3124:28 | 57.8313 | 57.4555
19 | Indi | 276 | 276 | 559:10 | 13125:47 | 2926.8882 | 1658:33 | 2995.9944 | 31505.6021 | 3019.2931 | 262:33 | 64.9837 | 64.7114 | 32052.5097 | 2787:10 | 62.6958 | 62.0483
20 | B.Bagewadi | 154 | 154 | 464:07 | 7069:10 | 1647.8042 | 730:50 | 1678.2556 | 17600.0938 | 1697.5938 | 264:34 | 64.8459 | 64.4409 | 17894.6424 | 2788:47 | 62.6515 | 62.0265
21 | Bagalkot | 208 | 208 | 995:54 | 8403:45 | 2458.9153 | 1851:05 | 2536.0437 | 24818.2896 | 2577.5396 | 297:25 | 60.6693 | 60.0258 | 25168.4458 | 2904:03 | 61.007 | 60.4568
22 | Jamkhandi | 213 | 213 | 150:05 | 4986:41 | 2400.6694 | 503:34 | 2421.6514 | 24529.9028 | 2427.9049 | 273:34 | 63.325 | 63.2303 | 24737.6813 | 2787:21 | 62.3648 | 62.046
23 | Mudhol | 203 | 203 | 127:16 | 3347:23 | 2800.2632 | 492:22 | 2820.7785 | 28371.4951 | 2826.0813 | 334:07 | 55.1759 | 55.0917 | 28510.9694 | 3370:45 | 54.3265 | 54.1019
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]

## RURAL(Excl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of April-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Apr-22
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 387:10 | 387:10 | 960:29 | 2950:22 | 3910:51 | 3910:51 | 4298:01 | 93:26 | 88.1919 | 87.0229 | 4298:01 | 93:26 | 88.1919 | 87.0229
2 | Dharwad Rural | 91 | 91 | 60:35 | 60:35 | 2872:52 | 7363:00 | 10235:52 | 10235:52 | 10296:27 | 113:09 | 84.3775 | 84.285 | 10296:27 | 113:09 | 84.3775 | 84.285
3 | Gadag | 113 | 113 | 105:20 | 105:20 | 1699:33 | 3687:12 | 5386:45 | 5386:45 | 5492:05 | 48:36 | 93.3791 | 93.2497 | 5492:05 | 48:36 | 93.3791 | 93.2497
4 | Ron | 58 | 58 | 267:37 | 267:37 | 1001:07 | 1415:39 | 2416:46 | 2416:46 | 2684:23 | 46:17 | 94.2127 | 93.5719 | 2684:23 | 46:17 | 94.2127 | 93.5719
5 | Haveri | 204 | 204 | 2018:12 | 2018:12 | 3507:35 | 10752:39 | 14260:14 | 14260:14 | 16278:26 | 79:48 | 90.2912 | 88.9172 | 16278:26 | 79:48 | 90.2912 | 88.9172
6 | Ranebennur | 201 | 201 | 1632:38 | 1632:38 | 4527:49 | 10276:01 | 14803:50 | 14803:50 | 16436:28 | 81:46 | 89.7707 | 88.6426 | 16436:28 | 81:46 | 89.7707 | 88.6426
7 | Sirsi | 63 | 63 | 597:16 | 597:16 | 607:37 | 2438:26 | 3046:03 | 3046:03 | 3643:19 | 57:50 | 93.2847 | 91.968 | 3643:19 | 57:50 | 93.2847 | 91.968
8 | Dandeli | 25 | 25 | 4:58 | 4:58 | 372:16 | 634:46 | 1007:02 | 1007:02 | 1012:00 | 40:29 | 94.4054 | 94.3778 | 1012:00 | 40:29 | 94.4054 | 94.3778
9 | Karwar | 33 | 33 | 322:49 | 322:49 | 337:49 | 502:59 | 840:48 | 840:48 | 1163:37 | 35:16 | 96.4613 | 95.1026 | 1163:37 | 35:16 | 96.4613 | 95.1026
10 | Honnavar | 40 | 40 | 509:40 | 509:40 | 516:01 | 679:05 | 1195:06 | 1195:06 | 1704:46 | 42:37 | 95.8503 | 94.0807 | 1704:46 | 42:37 | 95.8503 | 94.0807
11 | Belagavi | 149 | 149 | 1452:49 | 1452:49 | 4010:57 | 6408:04 | 10419:01 | 10419:01 | 11871:50 | 79:41 | 90.288 | 88.9338 | 11871:50 | 79:41 | 90.288 | 88.9338
12 | Bailhongal | 193 | 193 | 2284:40 | 2284:40 | 3713:37 | 6009:09 | 9722:46 | 9722:46 | 12007:26 | 62:13 | 93.0032 | 91.3591 | 12007:26 | 62:13 | 93.0032 | 91.3591
13 | Ramdurg | 88 | 88 | 548:55 | 548:55 | 1615:46 | 2736:32 | 4352:18 | 4352:18 | 4901:13 | 55:42 | 93.1308 | 92.2645 | 4901:13 | 55:42 | 93.1308 | 92.2645
14 | Ghataprabha | 168 | 168 | 693:28 | 693:28 | 2117:17 | 5868:12 | 7985:29 | 7985:29 | 8678:57 | 51:40 | 93.3982 | 92.8249 | 8678:57 | 51:40 | 93.3982 | 92.8249
15 | Raibag | 175 | 175 | 850:55 | 850:55 | 6864:34 | 4709:21 | 11573:55 | 11573:55 | 12424:50 | 71:00 | 90.8144 | 90.139 | 12424:50 | 71:00 | 90.8144 | 90.139
16 | Athani | 200 | 200 | 1579:00 | 1579:00 | 4500:32 | 4934:10 | 9434:42 | 9434:42 | 11013:42 | 55:04 | 93.4481 | 92.3516 | 11013:42 | 55:04 | 93.4481 | 92.3516
17 | Chikkodi | 192 | 192 | 911:22 | 911:22 | 2351:18 | 4750:36 | 7101:54 | 7101:54 | 8013:16 | 41:44 | 94.8626 | 94.2034 | 8013:16 | 41:44 | 94.8626 | 94.2034
18 | Vijayapur | 183 | 183 | 985:20 | 985:20 | 2544:37 | 6169:46 | 8714:23 | 8714:23 | 9699:43 | 53:00 | 93.3862 | 92.6383 | 9699:43 | 53:00 | 93.3862 | 92.6383
19 | Indi | 259 | 259 | 1037:24 | 1037:24 | 3434:10 | 5591:36 | 9025:46 | 9025:46 | 10063:10 | 38:51 | 95.1599 | 94.6036 | 10063:10 | 38:51 | 95.1599 | 94.6036
20 | B.Bagewadi | 149 | 149 | 1169:20 | 1169:20 | 2784:18 | 4869:55 | 7654:13 | 7654:13 | 8823:33 | 59:13 | 92.8652 | 91.7752 | 8823:33 | 59:13 | 92.8652 | 91.7752
21 | Bagalkot | 198 | 198 | 895:07 | 895:07 | 2965:43 | 5235:53 | 8201:36 | 8201:36 | 9096:43 | 45:57 | 94.2469 | 93.619 | 9096:43 | 45:57 | 94.2469 | 93.619
22 | Jamkhandi | 213 | 213 | 1204:22 | 1204:22 | 4892:27 | 2941:48 | 7834:15 | 7834:15 | 9038:37 | 42:26 | 94.8916 | 94.1063 | 9038:37 | 42:26 | 94.8916 | 94.1063
23 | Mudhol | 195 | 195 | 551:07 | 551:07 | 2195:49 | 2773:52 | 4969:41 | 4969:41 | 5520:48 | 28:19 | 96.4421 | 96.0475 | 5520:48 | 28:19 | 96.4421 | 96.0475
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of May-2022 |  |  |  | Reliability for cumulative period from Apr-22 to May-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 243:11 | 630:21 | 1024:57 | 2397:15 | 3422:12 | 7333:03 | 3665:23 | 79:41 | 90.0006 | 89.29 | 7963:24 | 173:07 | 89.1111 | 88.175
2 | Dharwad Rural | 92 | 92 | 355:55 | 416:30 | 2402:39 | 5105:25 | 7508:04 | 17743:56 | 7863:59 | 85:29 | 89.031 | 88.511 | 18160:26 | 197:24 | 86.8259 | 86.5167
3 | Gadag | 113 | 113 | 317:30 | 422:50 | 3056:10 | 5964:36 | 9020:46 | 14407:31 | 9338:16 | 82:38 | 89.2702 | 88.8925 | 14830:21 | 131:15 | 91.291 | 91.0354
4 | Ron | 59 | 59 | 320:20 | 587:57 | 1366:23 | 1400:47 | 2767:10 | 5183:56 | 3087:30 | 52:20 | 93.6961 | 92.9663 | 5771:53 | 97:50 | 93.9984 | 93.3177
5 | Haveri | 205 | 205 | 2696:43 | 4714:55 | 5266:35 | 1045.9306 | 1265.3715 | 1859.5479 | 1377.7347 | 161:18 | 80.0886 | 78.3205 | 2056.0028 | 240:42 | 85.1296 | 83.5586
6 | Ranebennur | 204 | 204 | 1723:37 | 3356:15 | 6995:48 | 19182:42 | 1090.7708 | 1707.5972 | 1162.5882 | 136:47 | 82.7519 | 81.6163 | 1847.441 | 217:21 | 86.2777 | 85.154
7 | Sirsi | 63 | 63 | 396:53 | 994:09 | 798:36 | 3201:18 | 3999:54 | 7045:57 | 4396:47 | 69:47 | 91.4663 | 90.6196 | 8040:06 | 127:37 | 92.3606 | 91.2827
8 | Dandeli | 25 | 25 | 278:09 | 283:07 | 378:30 | 506:37 | 885:07 | 1892:09 | 1163:16 | 46:32 | 95.2413 | 93.7459 | 2175:16 | 87:01 | 94.8302 | 94.0566
9 | Karwar | 33 | 33 | 315:09 | 637:58 | 319:23 | 643:52 | 963:15 | 1804:03 | 1278:24 | 38:44 | 96.0767 | 94.7931 | 2442:01 | 74:00 | 96.2658 | 94.9453
10 | Honnavar | 40 | 40 | 747:15 | 1256:55 | 588:20 | 1202:16 | 1790:36 | 2985:42 | 2537:51 | 63:27 | 93.9832 | 91.4723 | 4242:37 | 106:04 | 94.9015 | 92.7551
11 | Belagavi | 149 | 149 | 730:59 | 2183:48 | 2930:46 | 4259:01 | 7189:47 | 17608:48 | 7920:46 | 53:10 | 93.5143 | 92.8549 | 19792:36 | 132:50 | 91.9276 | 90.9265
12 | Bailhongal | 193 | 193 | 1302:00 | 3586:40 | 3578:27 | 6516:39 | 10095:06 | 19817:52 | 11397:06 | 59:03 | 92.9696 | 92.0629 | 23404:32 | 121:16 | 92.9861 | 91.7167
13 | Ramdurg | 88 | 88 | 429:49 | 978:44 | 1949:13 | 3608:59 | 5558:12 | 9910:30 | 5988:01 | 68:03 | 91.5106 | 90.8541 | 10889:14 | 123:44 | 92.3074 | 91.5477
14 | Ghataprabha | 168 | 168 | 328:42 | 1022:10 | 1734:17 | 4386:09 | 6120:26 | 14105:55 | 6449:08 | 38:23 | 95.1033 | 94.8404 | 15128:05 | 90:03 | 94.2648 | 93.8492
15 | Raibag | 177 | 177 | 311:39 | 1162:34 | 7100:50 | 3902:28 | 11003:18 | 22577:13 | 11314:57 | 63:56 | 91.6444 | 91.4078 | 23739:47 | 134:07 | 91.2872 | 90.8386
16 | Athani | 201 | 201 | 990:57 | 2569:57 | 3646:11 | 5352:55 | 8999:06 | 18433:48 | 9990:03 | 49:42 | 93.9823 | 93.3197 | 21003:45 | 104:30 | 93.7356 | 92.8623
17 | Chikkodi | 192 | 192 | 627:15 | 1538:37 | 2053:57 | 2125:13 | 4179:10 | 11281:04 | 4806:25 | 25:02 | 97.0744 | 96.6353 | 12819:41 | 66:46 | 95.9866 | 95.4393
18 | Vijayapur | 189 | 189 | 958:18 | 1943:38 | 2392:04 | 5502:47 | 7894:51 | 16609:14 | 8853:09 | 46:51 | 94.3855 | 93.704 | 18552:52 | 98:10 | 93.9973 | 93.2949
19 | Indi | 259 | 259 | 1969:19 | 3006:43 | 4284:16 | 7124:07 | 11408:23 | 20434:09 | 13377:42 | 51:39 | 94.0796 | 93.0576 | 23440:52 | 90:30 | 94.6109 | 93.8179
20 | B.Bagewadi | 151 | 151 | 904:54 | 2074:14 | 2924:47 | 5807:05 | 8731:52 | 16386:05 | 9636:46 | 63:49 | 92.2276 | 91.4221 | 18460:19 | 122:15 | 92.5876 | 91.6493
21 | Bagalkot | 198 | 198 | 1023:00 | 1918:07 | 4031:57 | 9598:43 | 13630:40 | 21832:16 | 14653:40 | 74:01 | 90.7471 | 90.0526 | 23750:23 | 119:57 | 92.4683 | 91.8066
22 | Jamkhandi | 213 | 213 | 587:11 | 1791:33 | 4337:43 | 3596:22 | 7934:05 | 15768:20 | 8521:16 | 40:00 | 94.9934 | 94.6229 | 17559:53 | 82:26 | 94.9433 | 94.3688
23 | Mudhol | 196 | 196 | 450:04 | 1001:11 | 2452:47 | 4424:44 | 6877:31 | 11847:12 | 7327:35 | 37:23 | 95.2837 | 94.975 | 12848:23 | 65:33 | 95.8713 | 95.5223
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of June-2022 |  |  |  | Reliability for cumulative period from Apr-22 to June-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 46 | 46 | 215:40 | 846:01 | 1067:42 | 1964:24 | 3032:06 | 10365:09 | 3247:46 | 70:36 | 90.8451 | 90.1939 | 11211:10 | 243:43 | 89.6827 | 88.8406
2 | Dharwad Rural | 92 | 92 | 140:50 | 557:20 | 1893:46 | 3557:03 | 5450:49 | 23194:45 | 5591:39 | 60:47 | 91.7711 | 91.5585 | 23752:05 | 258:10 | 88.4562 | 88.1788
3 | Gadag | 113 | 113 | 285:25 | 708:15 | 2002:07 | 3859:03 | 5861:10 | 20268:41 | 6146:35 | 54:24 | 92.796 | 92.4452 | 20976:56 | 185:38 | 91.7871 | 91.5002
4 | Ron | 59 | 59 | 204:30 | 792:27 | 913:00 | 1155:21 | 2068:21 | 7252:17 | 2272:51 | 38:31 | 95.131 | 94.6496 | 8044:44 | 136:21 | 94.3718 | 93.7568
5 | Haveri | 205 | 205 | 1588:16 | 6303:11 | 3959:53 | 11715:43 | 15675:36 | 2512.6979 | 17263:52 | 84:13 | 89.3797 | 88.3036 | 2775.3306 | 324:55 | 86.5307 | 85.1229
6 | Ranebennur | 205 | 205 | 1155:23 | 4511:38 | 4829:42 | 8863:58 | 13693:40 | 2278.1667 | 14849:03 | 72:26 | 90.7224 | 89.9397 | 2466.1514 | 288:43 | 87.7879 | 86.7802
7 | Sirsi | 62 | 62 | 585:04 | 1579:13 | 754:47 | 2147:46 | 2902:33 | 9948:30 | 3487:37 | 56:15 | 93.4979 | 92.1872 | 11527:43 | 185:56 | 92.6529 | 91.4867
8 | Dandeli | 25 | 25 | 82:04 | 365:11 | 280:46 | 371:50 | 652:36 | 2544:45 | 734:40 | 29:23 | 96.3744 | 95.9185 | 2909:56 | 116:24 | 95.3393 | 94.6705
9 | Karwar | 29 | 29 | 369:00 | 1006:58 | 419:31 | 761:41 | 1181:12 | 2985:15 | 1550:12 | 53:27 | 94.3429 | 92.5757 | 3992:13 | 137:40 | 95.2866 | 93.6968
10 | Honnavar | 40 | 40 | 632:18 | 1889:13 | 654:36 | 1334:40 | 1989:16 | 4974:58 | 2621:34 | 65:32 | 93.0928 | 90.8973 | 6864:11 | 171:36 | 94.3052 | 92.1426
11 | Belagavi | 149 | 149 | 461:47 | 2645:35 | 2546:37 | 3018:00 | 5564:37 | 23173:25 | 6026:24 | 40:27 | 94.813 | 94.3826 | 1075.7917 | 173:17 | 92.8788 | 92.0658
12 | Bailhongal | 193 | 193 | 1597:58 | 5184:38 | 3270:41 | 5162:26 | 8433:07 | 1177.1243 | 10031:05 | 51:58 | 93.9313 | 92.7813 | 1393.1507 | 173:14 | 93.2977 | 92.0677
13 | Ramdurg | 88 | 88 | 544:17 | 1523:01 | 1680:45 | 3116:36 | 4797:21 | 14707:51 | 5341:38 | 60:42 | 92.4284 | 91.5694 | 16230:52 | 184:26 | 92.3473 | 91.5549
14 | Ghataprabha | 170 | 170 | 532:08 | 1554:18 | 1602:54 | 2084:42 | 3687:36 | 17793:31 | 4219:44 | 24:49 | 96.9873 | 96.5525 | 19347:49 | 113:49 | 95.2075 | 94.7889
15 | Raibag | 178 | 178 | 511:06 | 1673:40 | 5793:30 | 1578:02 | 7371:32 | 1247.8646 | 7882:38 | 44:17 | 94.2482 | 93.8494 | 1317.6007 | 177:39 | 92.2962 | 91.8657
16 | Athani | 201 | 201 | 661:13 | 3231:10 | 3803:32 | 2032:14 | 5835:46 | 1011.2319 | 6496:59 | 32:19 | 95.9675 | 95.5107 | 1145.8639 | 136:49 | 94.4714 | 93.7354
17 | Chikkodi | 191 | 191 | 443:39 | 1982:16 | 1675:17 | 1929:33 | 3604:50 | 14885:54 | 4048:29 | 21:12 | 97.3787 | 97.0561 | 16868:10 | 88:19 | 96.4315 | 95.9563
18 | Vijayapur | 190 | 190 | 745:36 | 2689:14 | 2232:24 | 4392:19 | 6624:43 | 23233:57 | 7370:19 | 38:47 | 95.1574 | 94.6123 | 1080.1326 | 136:26 | 94.4009 | 93.7528
19 | Indi | 261 | 261 | 1756:20 | 4763:03 | 4043:47 | 9661:58 | 13705:45 | 1422.4958 | 15462:05 | 59:15 | 92.7066 | 91.772 | 1620.9562 | 149:03 | 94.0108 | 93.1752
20 | B.Bagewadi | 151 | 151 | 423:46 | 2498:00 | 3160:56 | 4895:05 | 8056:01 | 1018.4208 | 8479:47 | 56:09 | 92.5901 | 92.2003 | 1122.5042 | 178:25 | 92.5885 | 91.831
21 | Bagalkot | 198 | 198 | 1050:23 | 2968:30 | 3761:31 | 6714:09 | 10475:40 | 1346.1639 | 11526:03 | 58:13 | 92.6517 | 91.9149 | 1469.8514 | 178:10 | 92.5288 | 91.8423
22 | Jamkhandi | 213 | 213 | 969:31 | 2761:04 | 3281:08 | 1822:39 | 5103:47 | 20872:07 | 6073:18 | 28:31 | 96.672 | 96.0398 | 23633:11 | 110:57 | 95.5132 | 94.9197
23 | Mudhol | 196 | 196 | 477:05 | 1478:16 | 2772:33 | 3771:11 | 6543:44 | 18390:56 | 7020:49 | 35:49 | 95.363 | 95.0249 | 19869:12 | 101:22 | 95.7037 | 95.3584
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of July-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of July-2022 |  |  |  | Reliability for cumulative period from Apr-22 to July-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 47 | 47 | 55:28 | 901:29 | 656:51 | 2034:15 | 2691:06 | 13056:15 | 2746:34 | 58:26 | 92.3041 | 92.1455 | 13957:44 | 296:58 | 90.5125 | 89.8575
2 | Dharwad Rural | 92 | 92 | 188:49 | 746:09 | 2398:36 | 3190:52 | 5589:28 | 1199.3424 | 5778:17 | 62:48 | 91.834 | 91.5581 | 1230.4319 | 320:59 | 89.3145 | 89.0375
3 | Gadag | 113 | 113 | 127:10 | 835:25 | 1926:57 | 3637:13 | 5564:10 | 1076.3688 | 5691:20 | 50:22 | 93.3817 | 93.2304 | 1111.1778 | 236:00 | 92.1923 | 91.9398
4 | Ron | 59 | 59 | 70:20 | 862:47 | 770:55 | 1094:58 | 1865:53 | 9118:10 | 1936:13 | 32:49 | 95.7493 | 95.5891 | 9980:57 | 169:10 | 94.7218 | 94.2224
5 | Haveri | 205 | 205 | 1015:31 | 7318:42 | 3189:50 | 19500:54 | 22690:44 | 3458.1451 | 23706:15 | 115:38 | 85.1228 | 84.457 | 3763.091 | 440:33 | 86.173 | 84.9537
6 | Ranebennur | 205 | 205 | 683:25 | 5195:03 | 3562:33 | 13906:17 | 17468:50 | 3006.0347 | 18152:15 | 88:33 | 88.5465 | 88.0984 | 3222.4951 | 377:16 | 87.9807 | 87.1152
7 | Sirsi | 63 | 63 | 562:38 | 2141:51 | 698:22 | 2157:25 | 2855:47 | 12804:17 | 3418:25 | 54:16 | 93.9073 | 92.7069 | 14946:08 | 237:14 | 93.0587 | 91.8975
8 | Dandeli | 26 | 26 | 55:25 | 420:36 | 352:43 | 989:43 | 1342:26 | 3887:11 | 1397:51 | 53:46 | 93.0602 | 92.7737 | 4307:47 | 165:41 | 94.8939 | 94.3414
9 | Karwar | 30 | 30 | 439:21 | 1446:19 | 527:21 | 1148:26 | 1675:47 | 4661:02 | 2115:08 | 70:30 | 92.492 | 90.5236 | 6107:21 | 203:35 | 94.6937 | 93.0472
10 | Honnavar | 41 | 41 | 409:14 | 2298:27 | 859:59 | 1791:14 | 2651:13 | 7626:11 | 3060:27 | 74:39 | 91.3086 | 89.9671 | 9924:38 | 242:04 | 93.6474 | 91.7328
11 | Belagavi | 149 | 149 | 334:20 | 2979:55 | 2864:52 | 4246:41 | 7111:33 | 1261.8736 | 7445:53 | 49:58 | 93.5849 | 93.2833 | 1386.0368 | 223:15 | 93.0582 | 92.3752
12 | Bailhongal | 192 | 192 | 912:34 | 6097:12 | 3241:51 | 6480:56 | 9722:47 | 1582.2403 | 10635:21 | 55:24 | 93.1936 | 92.5548 | 1836.2903 | 229:32 | 93.2452 | 92.1606
13 | Ramdurg | 88 | 88 | 765:46 | 2288:47 | 1100:02 | 2603:33 | 3703:35 | 18411:26 | 4469:21 | 50:47 | 94.3433 | 93.1736 | 20700:13 | 235:14 | 92.8545 | 91.9662
14 | Ghataprabha | 171 | 171 | 219:23 | 1773:41 | 1820:59 | 3017:48 | 4838:47 | 22632:18 | 5058:10 | 29:35 | 96.1966 | 96.0242 | 1016.916 | 142:44 | 95.4798 | 95.1255
15 | Raibag | 178 | 178 | 172:23 | 1846:03 | 5008:56 | 2081:09 | 7090:05 | 1543.2847 | 7262:28 | 40:48 | 94.6462 | 94.5161 | 1620.2035 | 218:27 | 92.8933 | 92.5391
16 | Athani | 200 | 200 | 483:35 | 3714:45 | 3193:02 | 1936:22 | 5129:24 | 1224.9569 | 5612:59 | 28:04 | 96.5528 | 96.2278 | 1379.7382 | 165:34 | 94.9797 | 94.3453
17 | Chikkodi | 191 | 191 | 422:43 | 2404:59 | 1513:06 | 2250:21 | 3763:27 | 18649:21 | 4186:10 | 21:55 | 97.3516 | 97.0542 | 21054:20 | 110:14 | 96.6653 | 96.2352
18 | Vijayapur | 190 | 190 | 238:20 | 2927:34 | 2864:26 | 6326:41 | 9191:07 | 1351.0444 | 9429:27 | 49:38 | 93.4981 | 93.3295 | 1473.0264 | 186:04 | 94.1715 | 93.6453
19 | Indi | 264 | 264 | 999:56 | 5762:59 | 5585:09 | 9216:31 | 14801:40 | 2039.2319 | 15801:36 | 59:51 | 92.4641 | 91.955 | 2279.3562 | 207:13 | 93.6686 | 92.923
20 | B.Bagewadi | 150 | 150 | 411:59 | 2909:59 | 2992:06 | 5487:22 | 8479:28 | 1371.7319 | 8891:27 | 59:17 | 92.4019 | 92.0328 | 1492.9813 | 238:53 | 92.5042 | 91.8416
21 | Bagalkot | 198 | 198 | 701:21 | 3669:51 | 3175:59 | 6694:36 | 9870:35 | 1757.4382 | 10571:56 | 53:24 | 93.2995 | 92.8234 | 1910.3486 | 231:33 | 92.7246 | 92.0916
22 | Jamkhandi | 213 | 213 | 235:53 | 2996:57 | 2572:59 | 2028:27 | 4601:26 | 1061.3979 | 4837:19 | 22:43 | 97.0964 | 96.9475 | 1186.2708 | 133:40 | 95.9155 | 95.435
23 | Mudhol | 196 | 196 | 169:35 | 1647:51 | 2178:41 | 2590:12 | 4768:53 | 23159:49 | 4938:28 | 25:12 | 96.7297 | 96.6134 | 1033.6528 | 126:34 | 95.9644 | 95.6773
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of Aug-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of Aug-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Aug-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 47 | 47 | 86:55 | 988:24 | 1074:40 | 1475:27 | 2550:07 | 15606:22 | 2637:02 | 56:06 | 92.7073 | 92.4587 | 16594:46 | 353:05 | 90.9572 | 90.3845
2 | Dharwad Rural | 93 | 93 | 170:35 | 916:44 | 1474:28 | 3054:27 | 4528:55 | 1388.0472 | 4699:30 | 50:32 | 93.4546 | 93.208 | 1426.2444 | 368:04 | 90.2449 | 89.9765
3 | Gadag | 113 | 113 | 126:00 | 961:25 | 1643:58 | 4216:19 | 5860:17 | 1320.5472 | 5986:17 | 52:59 | 93.0294 | 92.8796 | 1360.6063 | 288:59 | 92.3619 | 92.1302
4 | Ron | 59 | 59 | 198:42 | 1061:29 | 933:20 | 946:10 | 1879:30 | 10997:40 | 2078:12 | 35:13 | 95.7183 | 95.2656 | 12059:09 | 204:24 | 94.9237 | 94.4338
5 | Haveri | 205 | 205 | 1819:29 | 9138:11 | 2909:57 | 1021.6132 | 1142.8611 | 4601.0063 | 1218.6729 | 142:40 | 82.0163 | 80.8234 | 4981.7639 | 583:14 | 85.3308 | 84.1168
6 | Ranebennur | 205 | 205 | 594:22 | 5789:25 | 3472:13 | 11501:15 | 14973:28 | 3629.9292 | 15567:50 | 75:56 | 90.1826 | 89.7929 | 3871.1549 | 453:13 | 88.4268 | 87.6577
7 | Sirsi | 63 | 63 | 353:21 | 2495:12 | 767:05 | 998:08 | 1765:13 | 14569:30 | 2118:34 | 33:38 | 96.234 | 95.4801 | 17064:42 | 270:52 | 93.702 | 92.6234
8 | Dandeli | 27 | 27 | 29:02 | 449:38 | 437:04 | 973:26 | 1410:30 | 5297:41 | 1439:32 | 53:19 | 92.9784 | 92.8339 | 5747:19 | 212:52 | 94.6566 | 94.2031
9 | Karwar | 31 | 31 | 276:41 | 1723:00 | 391:13 | 702:59 | 1094:12 | 5755:14 | 1370:53 | 44:13 | 95.2558 | 94.0562 | 7478:14 | 241:14 | 94.9441 | 93.4305
10 | Honnavar | 43 | 43 | 378:30 | 2676:57 | 697:43 | 866:17 | 1564:00 | 9190:11 | 1942:30 | 45:10 | 95.1113 | 93.9282 | 11867:08 | 275:59 | 94.1796 | 92.4842
11 | Belagavi | 149 | 149 | 523:52 | 3503:47 | 4016:25 | 5301:41 | 9318:06 | 1650.1278 | 9841:58 | 66:03 | 91.5944 | 91.1218 | 1796.1188 | 289:18 | 92.7616 | 92.1212
12 | Bailhongal | 194 | 194 | 618:55 | 6716:07 | 3101:31 | 6032:27 | 9133:58 | 1962.8222 | 9752:53 | 50:16 | 93.6717 | 93.2429 | 2242.6604 | 277:27 | 93.3872 | 92.4444
13 | Ramdurg | 88 | 88 | 558:51 | 2847:38 | 1100:06 | 2102:13 | 3202:19 | 21613:45 | 3761:10 | 42:44 | 95.1089 | 94.2553 | 1019.2243 | 277:58 | 93.3113 | 92.43
14 | Ghataprabha | 171 | 171 | 315:33 | 2089:14 | 1692:56 | 1844:03 | 3536:59 | 1090.3868 | 3852:32 | 22:32 | 97.2199 | 96.9719 | 1177.4382 | 165:15 | 95.8323 | 95.4996
15 | Raibag | 177 | 177 | 235:24 | 2081:27 | 5594:08 | 1476:57 | 7071:05 | 1837.9132 | 7306:29 | 41:17 | 94.6304 | 94.4517 | 1924.6403 | 260:58 | 93.2133 | 92.893
16 | Athani | 202 | 202 | 951:55 | 4666:40 | 2934:28 | 2153:41 | 5088:09 | 1436.9632 | 6040:04 | 29:54 | 96.6144 | 95.981 | 1631.4076 | 193:50 | 95.3505 | 94.7214
17 | Chikkodi | 191 | 191 | 397:55 | 2802:54 | 1550:45 | 2037:18 | 3588:03 | 22237:24 | 3985:58 | 20:52 | 97.4751 | 97.195 | 1043.3458 | 131:06 | 96.8294 | 96.4297
18 | Vijayapur | 190 | 190 | 361:28 | 3289:02 | 2478:29 | 5867:26 | 8345:55 | 1698.791 | 8707:23 | 45:50 | 94.096 | 93.8403 | 1835.834 | 231:54 | 94.1562 | 93.6848
19 | Indi | 266 | 266 | 2867:58 | 8630:57 | 4041:57 | 10696:05 | 14738:02 | 2653.3167 | 17606:00 | 66:11 | 92.5529 | 91.1038 | 3012.9396 | 271:51 | 93.4805 | 92.5968
20 | B.Bagewadi | 150 | 150 | 637:37 | 3547:36 | 3054:34 | 4969:53 | 8024:27 | 1706.084 | 8662:04 | 57:45 | 92.8096 | 92.2383 | 1853.9007 | 296:37 | 92.5661 | 91.922
21 | Bagalkot | 198 | 198 | 836:49 | 4506:40 | 3209:54 | 6534:41 | 9744:35 | 2163.4625 | 10581:24 | 53:26 | 93.3851 | 92.817 | 2351.2403 | 285:00 | 92.8584 | 92.2386
22 | Jamkhandi | 213 | 213 | 734:49 | 3731:46 | 2557:59 | 1671:38 | 4229:37 | 1237.6319 | 4964:26 | 23:18 | 97.331 | 96.8673 | 1393.1222 | 156:58 | 96.2023 | 95.7252
23 | Mudhol | 197 | 197 | 471:36 | 2119:27 | 3205:24 | 2486:13 | 5691:37 | 1202.1431 | 6163:13 | 31:17 | 96.1167 | 95.795 | 1290.4535 | 157:13 | 96.0116 | 95.7186
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of Sept-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of Sept-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Sept-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 47 | 47 | 95:20 | 1083:44 | 1228:40 | 1755:16 | 2983:56 | 18590:18 | 3079:16 | 65:31 | 91.1822 | 90.9005 | 19674:02 | 418:36 | 90.9941 | 90.4691
2 | Dharwad Rural | 93 | 93 | 192:00 | 1108:44 | 1513:20 | 3042:39 | 4555:59 | 1577.8799 | 4747:59 | 51:03 | 93.196 | 92.9092 | 1624.0771 | 419:07 | 90.7287 | 90.4573
3 | Gadag | 113 | 113 | 509:44 | 1471:09 | 2870:00 | 5121:48 | 7991:48 | 1653.5389 | 8501:32 | 75:14 | 90.1772 | 89.5507 | 1714.8368 | 364:13 | 92.0038 | 91.7074
4 | Ron | 61 | 61 | 160:02 | 1221:31 | 821:50 | 1250:57 | 2072:47 | 13070:27 | 2232:49 | 36:36 | 95.2805 | 94.9162 | 14291:58 | 234:18 | 95.1214 | 94.6654
5 | Haveri | 206 | 206 | 1432:59 | 10571:10 | 2896:44 | 11433:13 | 14329:57 | 5198.0875 | 15762:56 | 76:31 | 90.3385 | 89.3723 | 5638.5528 | 656:55 | 86.2112 | 85.0428
6 | Ranebennur | 205 | 205 | 1064:57 | 6854:22 | 3332:18 | 5845:40 | 9177:58 | 4012.3444 | 10242:55 | 49:58 | 93.7819 | 93.0604 | 4297.9431 | 503:10 | 89.3047 | 88.5434
7 | Sirsi | 62 | 62 | 310:17 | 2805:29 | 625:35 | 1995:02 | 2620:37 | 17190:07 | 2930:54 | 47:16 | 94.1294 | 93.4344 | 19995:36 | 322:31 | 93.6872 | 92.6569
8 | Dandeli | 27 | 27 | 12:01 | 461:39 | 173:54 | 344:23 | 518:17 | 5815:58 | 530:18 | 19:38 | 97.3339 | 97.2721 | 6277:37 | 232:30 | 95.0955 | 94.7062
9 | Karwar | 30 | 30 | 195:04 | 1918:04 | 265:36 | 606:42 | 872:18 | 6627:32 | 1067:22 | 35:35 | 95.9616 | 95.0585 | 8545:36 | 284:51 | 94.97 | 93.5143
10 | Honnavar | 43 | 43 | 515:10 | 3192:07 | 496:32 | 584:35 | 1081:07 | 10271:18 | 1596:17 | 37:07 | 96.508 | 94.844 | 13463:25 | 313:06 | 94.5613 | 92.8711
11 | Belagavi | 149 | 149 | 235:57 | 3739:44 | 3151:44 | 4430:56 | 7582:40 | 1966.0722 | 7818:37 | 52:28 | 92.9319 | 92.712 | 2121.8944 | 341:47 | 92.7896 | 92.2181
12 | Bailhongal | 194 | 194 | 1151:10 | 7867:17 | 3316:32 | 5851:23 | 9167:55 | 2344.8187 | 10319:05 | 53:11 | 93.4365 | 92.6123 | 2672.6222 | 330:38 | 93.3952 | 92.4719
13 | Ramdurg | 89 | 89 | 749:57 | 3597:35 | 870:16 | 2901:08 | 3771:24 | 1057.7146 | 4521:21 | 50:48 | 94.1145 | 92.9442 | 1207.6139 | 325:39 | 93.5058 | 92.5854
14 | Ghataprabha | 171 | 171 | 304:05 | 2393:19 | 1558:25 | 2690:21 | 4248:46 | 1267.4188 | 4552:51 | 26:37 | 96.5491 | 96.3021 | 1367.1403 | 191:53 | 95.9498 | 95.6312
15 | Raibag | 180 | 180 | 528:45 | 2610:12 | 4953:57 | 1636:04 | 6590:01 | 2112.4972 | 7118:46 | 39:33 | 94.9151 | 94.5071 | 2221.2556 | 296:10 | 93.5868 | 93.2567
16 | Athani | 203 | 203 | 432:35 | 5099:15 | 3011:39 | 2036:31 | 5048:10 | 1647.3035 | 5480:45 | 27:00 | 96.5461 | 96.2502 | 1859.7722 | 219:52 | 95.5657 | 94.9937
17 | Chikkodi | 192 | 192 | 276:50 | 3079:44 | 1434:11 | 1678:20 | 3112:31 | 1056.2465 | 3389:21 | 17:39 | 97.7485 | 97.5482 | 1184.5687 | 148:04 | 96.9938 | 96.6286
18 | Vijayapur | 191 | 191 | 925:26 | 4214:28 | 2083:34 | 5838:21 | 7921:55 | 2028.8708 | 8847:21 | 46:19 | 94.2394 | 93.5665 | 2204.4736 | 277:00 | 94.1954 | 93.693
19 | Indi | 270 | 270 | 669:23 | 9300:20 | 3047:20 | 7387:28 | 10434:48 | 3088.1 | 11104:11 | 41:08 | 94.6323 | 94.288 | 3475.6139 | 308:57 | 93.7501 | 92.9658
20 | B.Bagewadi | 152 | 152 | 615:28 | 4163:04 | 2226:31 | 4830:23 | 7056:54 | 2000.1215 | 7672:22 | 50:29 | 93.5518 | 92.9894 | 2173.5826 | 343:12 | 92.8095 | 92.1859
21 | Bagalkot | 200 | 200 | 1195:45 | 5702:25 | 3797:28 | 8408:30 | 12205:58 | 2672.0444 | 13401:43 | 67:01 | 91.5236 | 90.6933 | 2909.6451 | 349:09 | 92.6993 | 92.0501
22 | Jamkhandi | 213 | 213 | 309:40 | 4041:26 | 2510:59 | 2040:16 | 4551:15 | 1427.2674 | 4860:55 | 22:49 | 97.0323 | 96.8304 | 1595.6604 | 179:48 | 96.3384 | 95.9064
23 | Mudhol | 197 | 197 | 286:51 | 2406:18 | 2847:22 | 2808:27 | 5655:49 | 1437.8021 | 5942:40 | 30:10 | 96.0125 | 95.8103 | 1538.0646 | 187:23 | 96.0118 | 95.7336
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of Oct-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of Oct-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Oct-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 47 | 47 | 75:13 | 1158:57 | 1022:58 | 1747:41 | 2770:39 | 21360:57 | 2845:52 | 60:33 | 92.0766 | 91.8615 | 22519:54 | 479:09 | 91.1509 | 90.6708
2 | Dharwad Rural | 93 | 93 | 104:35 | 1213:19 | 1355:53 | 4102:24 | 5458:17 | 1805.3083 | 5562:52 | 59:49 | 92.1114 | 91.9602 | 1855.8632 | 478:56 | 90.929 | 90.675
3 | Gadag | 113 | 113 | 219:25 | 1690:34 | 1571:39 | 4590:42 | 6162:21 | 1910.3035 | 6381:46 | 56:29 | 92.6702 | 92.4092 | 1980.7438 | 420:41 | 92.1003 | 91.809
4 | Ron | 61 | 61 | 134:05 | 1355:36 | 693:25 | 833:45 | 1527:10 | 14597:37 | 1661:15 | 27:14 | 96.635 | 96.3396 | 15953:13 | 261:32 | 95.3406 | 94.9079
5 | Haveri | 206 | 206 | 1642:43 | 12213:53 | 2418:25 | 10622:38 | 13041:03 | 5741.4646 | 14683:46 | 71:17 | 91.4911 | 90.4193 | 6250.3764 | 728:12 | 86.9761 | 85.8217
6 | Ranebennur | 205 | 205 | 442:57 | 7297:19 | 2651:19 | 7051:48 | 9703:07 | 4416.641 | 10146:04 | 49:30 | 93.6381 | 93.3477 | 4720.6958 | 552:40 | 89.9324 | 89.2394
7 | Sirsi | 63 | 63 | 307:10 | 3112:39 | 514:25 | 1281:58 | 1796:23 | 18986:30 | 2103:33 | 33:23 | 96.1675 | 95.5121 | 22099:09 | 350:47 | 94.1321 | 93.1702
8 | Dandeli | 27 | 27 | 33:20 | 494:59 | 392:00 | 717:51 | 1109:51 | 6925:49 | 1143:11 | 42:20 | 94.4751 | 94.3091 | 7420:48 | 274:51 | 95.0056 | 94.6487
9 | Karwar | 30 | 30 | 222:42 | 2140:46 | 279:54 | 379:55 | 659:49 | 7287:21 | 882:31 | 29:25 | 97.0438 | 96.0461 | 9428:07 | 314:16 | 95.2704 | 93.881
10 | Honnavar | 43 | 43 | 223:16 | 3415:23 | 324:15 | 310:08 | 634:23 | 10905:41 | 857:39 | 19:57 | 98.0171 | 97.3192 | 14321:04 | 333:03 | 95.0619 | 93.5154
11 | Belagavi | 149 | 149 | 222:05 | 3961:49 | 2849:57 | 3954:40 | 6804:37 | 2249.5979 | 7026:42 | 47:10 | 93.8618 | 93.6614 | 2414.6736 | 388:56 | 92.9449 | 92.4272
12 | Bailhongal | 194 | 194 | 678:49 | 8546:06 | 2849:55 | 6183:55 | 9033:50 | 2721.2285 | 9712:39 | 50:04 | 93.7411 | 93.2708 | 3077.316 | 380:42 | 93.4454 | 92.5876
13 | Ramdurg | 89 | 89 | 510:07 | 4107:42 | 920:38 | 3384:44 | 4305:22 | 1237.1049 | 4815:29 | 54:06 | 93.498 | 92.7276 | 1408.259 | 379:45 | 93.5046 | 92.606
14 | Ghataprabha | 171 | 171 | 197:13 | 2590:32 | 1194:43 | 2990:58 | 4185:41 | 1441.8222 | 4382:54 | 25:38 | 96.71 | 96.555 | 1549.7611 | 217:31 | 96.0599 | 95.765
15 | Raibag | 182 | 182 | 216:22 | 2826:34 | 4369:02 | 2418:04 | 6787:06 | 2395.2931 | 7003:28 | 38:29 | 94.9877 | 94.8279 | 2513.0667 | 331:24 | 93.85 | 93.5476
16 | Athani | 203 | 203 | 402:20 | 5501:35 | 2487:29 | 2004:10 | 4491:39 | 1834.4556 | 4893:59 | 24:06 | 97.026 | 96.7596 | 2063.6882 | 243:59 | 95.7772 | 95.2496
17 | Chikkodi | 192 | 192 | 360:11 | 3439:55 | 1420:51 | 2910:02 | 4330:53 | 1236.7 | 4691:04 | 24:26 | 96.9682 | 96.716 | 1380.0299 | 172:30 | 96.9901 | 96.6413
18 | Vijayapur | 191 | 191 | 99:36 | 4314:04 | 1793:41 | 4962:59 | 6756:40 | 2310.3986 | 6856:16 | 35:54 | 95.2453 | 95.1752 | 2490.1514 | 312:54 | 94.3475 | 93.9077
19 | Indi | 274 | 274 | 613:34 | 9913:54 | 2475:43 | 6637:37 | 9113:20 | 3467.8222 | 9726:54 | 35:30 | 95.5295 | 95.2285 | 3880.9014 | 339:56 | 94.0858 | 93.3814
20 | B.Bagewadi | 152 | 152 | 643:24 | 4806:28 | 2512:00 | 4871:02 | 7383:02 | 2307.7479 | 8026:26 | 52:48 | 93.4714 | 92.9025 | 2508.0174 | 396:00 | 92.9053 | 92.2897
21 | Bagalkot | 201 | 201 | 425:56 | 6128:21 | 3137:47 | 8004:27 | 11142:14 | 3136.3042 | 11568:10 | 57:33 | 92.5492 | 92.2644 | 3391.6521 | 404:58 | 92.7086 | 92.115
22 | Jamkhandi | 213 | 213 | 111:04 | 4152:30 | 1972:32 | 1626:46 | 3599:18 | 1577.2382 | 3710:22 | 17:25 | 97.7287 | 97.6587 | 1750.259 | 197:13 | 96.5398 | 96.1602
23 | Mudhol | 197 | 197 | 156:18 | 2562:36 | 1955:16 | 3148:30 | 5103:46 | 1650.459 | 5260:04 | 26:42 | 96.5178 | 96.4112 | 1757.234 | 214:05 | 96.0851 | 95.8318
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of Nov-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of Nov-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Nov-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 47 | 47 | 60:39 | 1219:36 | 1012:15 | 620:16 | 1632:31 | 22993:28 | 1693:10 | 36:01 | 95.1758 | 94.9966 | 1008.8778 | 515:10 | 91.6458 | 91.2027
2 | Dharwad Rural | 93 | 93 | 133:55 | 1347:14 | 2500:50 | 1825:58 | 4326:48 | 1985.5917 | 4460:43 | 47:58 | 93.5382 | 93.3382 | 2041.7264 | 526:54 | 91.2498 | 91.0024
3 | Gadag | 113 | 113 | 138:28 | 1829:02 | 1545:18 | 786:28 | 2331:46 | 2007.4604 | 2470:14 | 21:52 | 97.134 | 96.9638 | 2083.6701 | 442:33 | 92.7192 | 92.4428
4 | Ron | 61 | 61 | 80:25 | 1436:01 | 839:43 | 705:47 | 1545:30 | 16143:07 | 1625:55 | 26:39 | 96.4811 | 96.298 | 17579:08 | 288:11 | 95.4809 | 95.0789
5 | Haveri | 206 | 206 | 1455:14 | 13669:07 | 3561:52 | 3828:48 | 7390:40 | 6049.409 | 8845:54 | 42:56 | 95.0171 | 94.0359 | 6618.9556 | 771:08 | 87.9647 | 86.8316
6 | Ranebennur | 206 | 206 | 894:41 | 8192:00 | 4006:10 | 2857:59 | 6864:09 | 4702.6472 | 7758:50 | 37:40 | 95.3721 | 94.7689 | 5043.9806 | 587:39 | 90.6441 | 89.965
7 | Sirsi | 63 | 63 | 267:59 | 3380:38 | 643:00 | 1255:47 | 1898:47 | 20885:17 | 2166:46 | 34:24 | 95.814 | 95.2232 | 1011.0799 | 385:10 | 94.3389 | 93.4226
8 | Dandeli | 27 | 27 | 63:43 | 558:42 | 423:34 | 240:33 | 664:07 | 7589:56 | 727:50 | 26:57 | 96.5838 | 96.256 | 8148:38 | 301:48 | 95.1996 | 94.8463
9 | Karwar | 30 | 30 | 194:35 | 2335:21 | 276:45 | 347:33 | 624:18 | 7911:39 | 818:53 | 27:18 | 97.1097 | 96.2089 | 10247:00 | 341:34 | 95.4966 | 94.1672
10 | Honnavar | 43 | 43 | 435:21 | 3850:44 | 446:30 | 285:32 | 732:02 | 11637:43 | 1167:23 | 27:09 | 97.6356 | 96.2294 | 15488:27 | 360:12 | 95.3783 | 93.8491
11 | Belagavi | 149 | 149 | 500:09 | 4461:58 | 3583:51 | 1621:38 | 5205:29 | 2466.4931 | 5705:38 | 38:18 | 95.1478 | 94.6815 | 2652.4083 | 427:14 | 93.2157 | 92.7043
12 | Bailhongal | 199 | 199 | 2059:16 | 10605:22 | 3530:30 | 1895:35 | 5426:05 | 2947.3153 | 7485:21 | 37:37 | 96.213 | 94.7757 | 3389.2056 | 408:45 | 93.9301 | 93.02
13 | Ramdurg | 89 | 89 | 541:08 | 4648:50 | 1139:19 | 815:08 | 1954:27 | 1318.5403 | 2495:35 | 28:02 | 96.95 | 96.1055 | 1512.2417 | 407:48 | 93.9283 | 93.0363
14 | Ghataprabha | 171 | 171 | 322:10 | 2912:42 | 1541:39 | 876:48 | 2418:27 | 1542.591 | 2740:37 | 16:02 | 98.0357 | 97.774 | 1663.9535 | 233:32 | 96.3029 | 96.012
15 | Raibag | 182 | 182 | 326:31 | 3153:05 | 4625:55 | 820:27 | 5446:22 | 2622.225 | 5772:53 | 31:43 | 95.8437 | 95.5946 | 2753.6035 | 363:07 | 94.0952 | 93.7993
16 | Athani | 203 | 203 | 622:20 | 6123:55 | 3515:25 | 939:44 | 4455:09 | 2020.0868 | 5077:29 | 25:01 | 96.9519 | 96.5261 | 2275.25 | 269:00 | 95.9217 | 95.4065
17 | Chikkodi | 193 | 193 | 269:00 | 3708:55 | 1203:13 | 634:47 | 1838:00 | 1313.2833 | 2107:00 | 10:55 | 98.6773 | 98.4837 | 1467.8215 | 182:32 | 97.2112 | 96.8831
18 | Vijayapur | 194 | 194 | 326:39 | 4640:43 | 1145:52 | 1115:35 | 2261:27 | 2404.6257 | 2588:06 | 13:20 | 98.381 | 98.1471 | 2597.9889 | 321:24 | 94.9201 | 94.5116
19 | Indi | 275 | 275 | 2144:14 | 12058:08 | 2246:55 | 1641:46 | 3888:41 | 3629.8507 | 6032:55 | 21:56 | 98.036 | 96.9531 | 4132.2729 | 360:38 | 94.5904 | 93.8416
20 | B.Bagewadi | 152 | 152 | 1069:40 | 5876:08 | 1873:29 | 1155:31 | 3029:00 | 2433.9563 | 4098:40 | 26:58 | 97.2323 | 96.2549 | 2678.7951 | 422:58 | 93.4373 | 92.7772
21 | Bagalkot | 203 | 203 | 284:28 | 6412:49 | 2809:03 | 2218:26 | 5027:29 | 3345.7826 | 5311:57 | 26:10 | 96.5603 | 96.3657 | 3612.9833 | 427:09 | 93.2452 | 92.7058
22 | Jamkhandi | 213 | 213 | 394:45 | 4547:15 | 2305:41 | 684:55 | 2990:36 | 1701.8465 | 3385:21 | 15:54 | 98.0499 | 97.7925 | 1891.3153 | 213:06 | 96.7255 | 96.3609
23 | Mudhol | 197 | 197 | 363:38 | 2926:14 | 1658:29 | 828:40 | 2487:09 | 1754.0903 | 2850:47 | 14:28 | 98.2465 | 97.9901 | 1876.0167 | 228:33 | 96.3508 | 96.0972
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of Dec-2022 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of Dec-2022 |  |  |  | Reliability for cumulative period from Apr-22 to Dec-22
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 47 | 47 | 131:33 | 1351:09 | 1201:13 | 657:28 | 1858:41 | 1035.5063 | 1990:14 | 42:21 | 94.6846 | 94.3084 | 1091.8042 | 557:31 | 91.9883 | 91.5528
2 | Dharwad Rural | 98 | 98 | 235:42 | 1582:56 | 2170:19 | 1500:11 | 3670:30 | 2138.5292 | 3906:12 | 39:52 | 94.9658 | 94.6426 | 2204.4847 | 539:52 | 92.0648 | 91.8201
3 | Gadag | 113 | 113 | 866:55 | 2695:57 | 1915:51 | 1628:38 | 3544:29 | 2155.1472 | 4411:24 | 39:02 | 95.784 | 94.7528 | 2267.4785 | 481:35 | 93.0647 | 92.7032
4 | Ron | 61 | 61 | 192:44 | 1628:45 | 622:55 | 866:50 | 1489:45 | 17632:52 | 1682:30 | 27:35 | 96.7175 | 96.2928 | 19261:38 | 315:46 | 95.6203 | 95.2157
5 | Haveri | 208 | 208 | 1499:17 | 15168:24 | 3332:13 | 3230:06 | 6562:19 | 6322.8389 | 8061:36 | 38:45 | 95.7595 | 94.7906 | 6954.8556 | 802:29 | 88.9461 | 87.8412
6 | Ranebennur | 207 | 207 | 921:44 | 9113:44 | 3697:23 | 2827:49 | 6525:12 | 4974.5306 | 7446:56 | 35:59 | 95.7631 | 95.1646 | 5354.2694 | 620:47 | 91.2613 | 90.5942
7 | Sirsi | 63 | 63 | 480:05 | 3860:43 | 625:15 | 967:10 | 1592:25 | 22477:42 | 2072:30 | 32:54 | 96.6026 | 95.5784 | 1097.434 | 418:04 | 94.5941 | 93.6656
8 | Dandeli | 27 | 27 | 48:20 | 607:02 | 489:28 | 240:09 | 729:37 | 8319:33 | 777:57 | 28:49 | 96.3679 | 96.1273 | 8926:35 | 330:37 | 95.3313 | 94.9907
9 | Karwar | 30 | 30 | 274:09 | 2609:30 | 195:30 | 320:01 | 515:31 | 8427:10 | 789:40 | 26:19 | 97.6903 | 96.4621 | 11036:40 | 367:53 | 95.7439 | 94.4259
10 | Honnavar | 44 | 44 | 645:39 | 4496:23 | 435:47 | 253:31 | 689:18 | 12327:01 | 1334:57 | 30:20 | 97.8944 | 95.9221 | 16823:24 | 382:21 | 95.7552 | 94.2068
11 | Belagavi | 150 | 150 | 402:51 | 4864:49 | 4188:04 | 1612:46 | 5800:50 | 2708.1944 | 6203:41 | 41:21 | 94.8021 | 94.4411 | 2910.8951 | 465:45 | 93.4347 | 92.9433
12 | Bailhongal | 201 | 201 | 845:12 | 11450:34 | 4602:23 | 2318:40 | 6921:03 | 3235.6924 | 7766:15 | 38:38 | 95.3719 | 94.8067 | 3712.7993 | 443:19 | 94.1462 | 93.283
13 | Ramdurg | 89 | 89 | 494:40 | 5143:30 | 799:10 | 999:30 | 1798:40 | 1393.4847 | 2293:20 | 25:46 | 97.2836 | 96.5366 | 1607.7972 | 433:34 | 94.3065 | 93.4309
14 | Ghataprabha | 171 | 171 | 172:24 | 3085:06 | 1276:40 | 923:19 | 2199:59 | 1634.2569 | 2372:23 | 13:52 | 98.2708 | 98.1353 | 1762.8028 | 247:25 | 96.5247 | 96.2513
15 | Raibag | 181 | 181 | 225:25 | 3378:30 | 3146:02 | 622:16 | 3768:18 | 2779.2375 | 3993:43 | 22:04 | 97.2017 | 97.0343 | 2920.0083 | 387:11 | 94.4164 | 94.1336
16 | Athani | 203 | 203 | 1221:55 | 7345:50 | 6079:41 | 1034:08 | 7113:49 | 2316.4958 | 8335:44 | 41:04 | 95.2899 | 94.4808 | 2622.5722 | 310:03 | 95.8504 | 95.3022
17 | Chikkodi | 194 | 194 | 310:25 | 4019:20 | 1358:55 | 847:58 | 2206:53 | 1405.2368 | 2517:18 | 12:59 | 98.471 | 98.2559 | 1572.709 | 194:34 | 97.366 | 97.0521
18 | Vijayapur | 200 | 200 | 617:51 | 5258:34 | 1211:05 | 1428:35 | 2639:40 | 2514.6118 | 3257:31 | 16:17 | 98.226 | 97.8108 | 2733.7188 | 328:03 | 95.428 | 95.0296
19 | Indi | 275 | 275 | 508:29 | 12566:37 | 1832:36 | 2077:27 | 3910:03 | 3792.7694 | 4418:32 | 16:04 | 98.0889 | 97.8404 | 4316.3785 | 376:42 | 94.9848 | 94.2924
20 | B.Bagewadi | 152 | 152 | 728:55 | 6605:03 | 1885:16 | 1290:06 | 3175:22 | 2566.2632 | 3904:17 | 25:41 | 97.1921 | 96.5476 | 2841.4736 | 448:39 | 93.8606 | 93.2022
21 | Bagalkot | 207 | 207 | 995:02 | 7407:51 | 2725:49 | 3245:42 | 5971:31 | 3594.5958 | 6966:33 | 33:39 | 96.1226 | 95.4765 | 3903.2563 | 452:33 | 93.6854 | 93.1432
22 | Jamkhandi | 213 | 213 | 289:21 | 4836:36 | 2024:35 | 698:28 | 2723:03 | 1815.3069 | 3012:24 | 14:09 | 98.2817 | 98.0991 | 2016.8319 | 227:15 | 96.9009 | 96.5568
23 | Mudhol | 200 | 200 | 293:53 | 3220:07 | 1686:28 | 697:12 | 2383:40 | 1853.4097 | 2677:33 | 13:23 | 98.3981 | 98.2006 | 1987.5812 | 238:31 | 96.6302 | 96.3862
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of Jan-2023 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 22-23 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of Jan-2023 |  |  |  | Reliability for cumulative period from Apr-22 to Jan-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 22-23 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | Hubballi Rural | 47 | 47 | 71:14 | 1422:23 | 674:05 | 215:18 | 889:23 | 1072.5639 | 960:37 | 20:26 | 97.4566 | 97.2529 | 1131.8299 | 577:57 | 92.5423 | 92.1302
2 | Dharwad Rural | 98 | 98 | 188:36 | 1771:32 | 2084:57 | 1014:34 | 3099:31 | 2267.6757 | 3288:07 | 33:33 | 95.749 | 95.4903 | 2341.4896 | 573:26 | 92.4381 | 92.1919
3 | Gadag | 113 | 113 | 82:30 | 2778:27 | 1041:18 | 579:13 | 1620:31 | 2222.6688 | 1703:01 | 15:04 | 98.0725 | 97.9743 | 2338.4375 | 496:40 | 93.572 | 93.2372
4 | Ron | 61 | 61 | 76:45 | 1705:30 | 1093:55 | 1170:50 | 2264:45 | 19897:37 | 2341:30 | 38:23 | 95.0098 | 94.8407 | 21603:08 | 354:09 | 95.5584 | 95.1777
5 | Haveri | 209 | 209 | 1627:42 | 16796:06 | 3190:17 | 2313:34 | 5503:51 | 6552.166 | 7131:33 | 34:07 | 96.4605 | 95.4137 | 7252.0035 | 832:46 | 89.7549 | 88.6606
6 | Ranebennur | 209 | 209 | 1066:56 | 10180:40 | 3416:41 | 1568:06 | 4984:47 | 5182.2299 | 6051:43 | 28:57 | 96.7943 | 96.1081 | 5606.4243 | 643:48 | 91.8969 | 91.2337
7 | Sirsi | 63 | 63 | 434:12 | 4294:55 | 701:22 | 780:03 | 1481:25 | 23959:07 | 1915:37 | 30:24 | 96.8394 | 95.9131 | 1177.2514 | 448:29 | 94.8216 | 93.8933
8 | Dandeli | 27 | 27 | 52:45 | 659:47 | 438:03 | 209:07 | 647:10 | 8966:43 | 699:55 | 25:55 | 96.7783 | 96.5157 | 9626:30 | 356:32 | 95.4779 | 95.1452
9 | Karwar | 31 | 31 | 178:13 | 2787:43 | 214:57 | 190:01 | 404:58 | 8832:08 | 583:11 | 18:49 | 98.2442 | 97.4715 | 11619:51 | 374:50 | 96.1205 | 94.8961
10 | Honnavar | 44 | 44 | 238:23 | 4734:46 | 397:16 | 236:13 | 633:29 | 12960:30 | 871:52 | 19:49 | 98.0649 | 97.3367 | 17695:16 | 402:10 | 95.9892 | 94.5239
11 | Belagavi | 150 | 150 | 158:55 | 5023:44 | 3149:10 | 1078:23 | 4227:33 | 2884.3424 | 4386:28 | 29:15 | 96.2119 | 96.0695 | 3093.6646 | 494:59 | 93.716 | 93.26
12 | Bailhongal | 201 | 201 | 630:46 | 12081:20 | 3550:11 | 1346:34 | 4896:45 | 3439.7236 | 5527:31 | 27:30 | 96.7255 | 96.3038 | 3943.1125 | 470:49 | 94.4075 | 93.5891
13 | Ramdurg | 89 | 89 | 103:08 | 5246:38 | 843:46 | 455:03 | 1298:49 | 1447.6021 | 1401:57 | 15:45 | 98.0385 | 97.8828 | 1666.2118 | 449:19 | 94.6846 | 93.8819
14 | Ghataprabha | 174 | 174 | 184:22 | 3269:28 | 1001:22 | 602:09 | 1603:31 | 1701.0701 | 1787:53 | 10:17 | 98.7613 | 98.6189 | 1837.2979 | 253:25 | 96.8051 | 96.5493
15 | Raibag | 181 | 181 | 261:26 | 3639:56 | 2792:50 | 413:39 | 3206:29 | 2912.841 | 3467:55 | 19:10 | 97.6189 | 97.4248 | 3064.5049 | 406:21 | 94.7408 | 94.467
16 | Athani | 203 | 203 | 576:00 | 7921:50 | 4348:57 | 634:56 | 4983:53 | 2524.1576 | 5559:53 | 27:23 | 96.7001 | 96.3187 | 2854.234 | 337:27 | 95.9365 | 95.4051
17 | Chikkodi | 197 | 197 | 547:55 | 4567:15 | 1561:04 | 961:24 | 2522:28 | 1510.3396 | 3070:23 | 15:35 | 98.279 | 97.9051 | 1700.6417 | 207:11 | 97.4945 | 97.1789
18 | Vijayapur | 204 | 204 | 372:32 | 5631:06 | 1445:04 | 988:12 | 2433:16 | 2615.9979 | 2805:48 | 13:45 | 98.3968 | 98.1514 | 2850.6271 | 335:22 | 95.8093 | 95.4334
19 | Indi | 276 | 276 | 559:10 | 13125:47 | 1971:06 | 1658:33 | 3629:39 | 3944.0049 | 4188:49 | 15:11 | 98.2324 | 97.9601 | 4490.9125 | 390:31 | 95.3301 | 94.6825
20 | B.Bagewadi | 154 | 154 | 464:07 | 7069:10 | 1374:24 | 730:50 | 2105:14 | 2653.9813 | 2569:21 | 16:41 | 98.1626 | 97.7575 | 2948.5299 | 459:31 | 94.3681 | 93.743
21 | Bagalkot | 208 | 208 | 995:54 | 8403:45 | 2096:35 | 1851:05 | 3947:40 | 3759.0819 | 4943:34 | 23:46 | 97.449 | 96.8055 | 4109.2382 | 474:09 | 94.094 | 93.5438
22 | Jamkhandi | 213 | 213 | 150:05 | 4986:41 | 1562:50 | 503:34 | 2066:24 | 1901.4069 | 2216:29 | 10:24 | 98.696 | 98.6013 | 2109.1854 | 237:39 | 97.0827 | 96.764
23 | Mudhol | 203 | 203 | 127:16 | 3347:23 | 1321:03 | 492:22 | 1813:25 | 1928.9688 | 1940:41 | 9:34 | 98.7993 | 98.7151 | 2068.4431 | 244:33 | 96.8947 | 96.6701
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]