## DHQ
Annex-1 | [13 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of April-2023
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Apr-23
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 41 | 41 | 10:05 | 10:05 | 589:57 | 188:44 | 778:41 | 778:41 | 788:46 | 19:14 | 97.3622 | 97.328 | 788:46 | 19:14 | 97.3622 | 97.328
2 | GADAG | 12 | 12 | 75:00 | 75:00 | 130:37 | 33:01 | 163:38 | 163:38 | 238:38 | 19:53 | 98.1061 | 97.238 | 238:38 | 19:53 | 98.1061 | 97.238
3 | HAVERI | 8 | 8 | 0:00 | 0:00 | 47:36 | 22:11 | 69:47 | 69:47 | 69:47 | 8:43 | 98.7885 | 98.7885 | 69:47 | 8:43 | 98.7885 | 98.7885
4 | KARWAR | 10 | 10 | 24:12 | 24:12 | 25:32 | 50:41 | 76:13 | 76:13 | 100:25 | 10:03 | 98.9414 | 98.6053 | 100:25 | 10:03 | 98.9414 | 98.6053
5 | BELAGAVI | 77 | 75 | 112:16 | 112:16 | 129:22 | 142:27 | 271:49 | 271:49 | 384:05 | 4:59 | 99.5097 | 99.3072 | 384:05 | 4:59 | 99.5097 | 99.3072
6 | VIJAYAPUR | 41 | 40 | 74:41 | 74:41 | 231:29 | 218:06 | 449:35 | 449:35 | 524:16 | 12:47 | 98.477 | 98.224 | 524:16 | 12:47 | 98.477 | 98.224
7 | BAGALKOT | 24 | 24 | 134:17 | 134:17 | 112:56 | 302:41 | 415:37 | 415:37 | 549:54 | 22:55 | 97.5948 | 96.8177 | 549:54 | 22:55 | 97.5948 | 96.8177
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of May-2023
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2023 |  |  |  | Reliability for cumulative period from Apr-23 to May-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 41 | 41 | 32:33 | 42:38 | 645:02 | 296:09 | 941:11 | 1719:52 | 973:44 | 23:45 | 96.9146 | 96.8079 | 1762:30 | 42:59 | 97.1347 | 97.0637
2 | GADAG | 12 | 12 | 19:30 | 94:30 | 60:52 | 37:38 | 98:30 | 262:08 | 118:00 | 9:50 | 98.8967 | 98.6783 | 356:38 | 29:43 | 98.5079 | 97.97
3 | HAVERI | 8 | 8 | 0:00 | 0:00 | 14:44 | 41:41 | 56:25 | 126:12 | 56:25 | 7:03 | 99.0521 | 99.0521 | 126:12 | 15:47 | 98.9225 | 98.9225
4 | KARWAR | 10 | 10 | 162:38 | 186:50 | 74:46 | 95:35 | 170:21 | 246:34 | 332:59 | 33:18 | 97.7103 | 95.5244 | 433:24 | 43:20 | 98.3158 | 97.0396
5 | BELAGAVI | 76 | 76 | 240:01 | 352:17 | 271:29 | 316:53 | 588:22 | 860:11 | 828:23 | 10:54 | 98.9595 | 98.535 | 1212:28 | 15:57 | 99.2269 | 98.9103
6 | VIJAYAPUR | 41 | 41 | 9:27 | 84:08 | 211:07 | 227:48 | 438:55 | 888:30 | 448:22 | 10:56 | 98.5611 | 98.5301 | 972:38 | 23:43 | 98.5198 | 98.3796
7 | BAGALKOT | 24 | 24 | 0:00 | 134:17 | 68:01 | 46:59 | 115:00 | 530:37 | 115:00 | 4:48 | 99.356 | 99.356 | 664:54 | 27:42 | 98.4898 | 98.1076
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of June-2023
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2023 |  |  |  | Reliability for cumulative period from Apr-23 to June-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 41 | 41 | 4:21 | 46:59 | 589:26 | 192:53 | 782:19 | 2502:11 | 786:40 | 19:11 | 97.3499 | 97.3351 | 2549:10 | 62:10 | 97.2056 | 97.1532
2 | GADAG | 12 | 12 | 16:30 | 111:00 | 49:33 | 49:04 | 98:37 | 360:45 | 115:07 | 9:36 | 98.8586 | 98.6676 | 471:45 | 39:19 | 98.6235 | 98.2
3 | HAVERI | 8 | 8 | 0:00 | 0:00 | 113:49 | 37:14 | 151:03 | 277:15 | 151:03 | 18:53 | 97.3776 | 97.3776 | 277:15 | 34:39 | 98.4132 | 98.4132
4 | KARWAR | 10 | 10 | 10:30 | 197:20 | 70:49 | 135:26 | 206:15 | 452:49 | 216:45 | 21:40 | 97.1354 | 96.9896 | 650:09 | 65:01 | 97.9267 | 97.0231
5 | BELAGAVI | 76 | 76 | 99:17 | 451:34 | 261:12 | 143:25 | 404:37 | 1264:48 | 503:54 | 6:38 | 99.2606 | 99.0791 | 1716:22 | 22:35 | 99.238 | 98.9659
6 | VIJAYAPUR | 41 | 41 | 311:56 | 396:04 | 223:12 | 370:15 | 593:27 | 1481:57 | 905:23 | 22:05 | 97.9897 | 96.933 | 1878:01 | 45:48 | 98.345 | 97.9027
7 | BAGALKOT | 24 | 24 | 185:01 | 319:18 | 162:01 | 68:35 | 230:36 | 761:13 | 415:37 | 17:19 | 98.6655 | 97.5948 | 1080:31 | 45:01 | 98.5477 | 97.9386
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of July-2023
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2023 |  |  |  | Reliability for cumulative period from Apr-23 to July-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 41 | 41 | 19:30 | 66:29 | 680:06 | 276:26 | 956:32 | 3458:43 | 976:02 | 23:48 | 96.8642 | 96.8003 | 3525:12 | 85:59 | 97.1189 | 97.0635
2 | GADAG | 12 | 12 | 10:00 | 121:00 | 60:01 | 39:14 | 99:15 | 460:00 | 109:15 | 9:06 | 98.8883 | 98.7763 | 581:00 | 48:25 | 98.6908 | 98.3464
3 | HAVERI | 8 | 8 | 0:00 | 0:00 | 179:19 | 40:48 | 220:07 | 497:22 | 220:07 | 27:31 | 96.3018 | 96.3018 | 497:22 | 62:10 | 97.8767 | 97.8767
4 | KARWAR | 10 | 10 | 4:18 | 201:38 | 139:18 | 124:19 | 263:37 | 716:26 | 267:55 | 26:48 | 96.4568 | 96.399 | 918:04 | 91:48 | 97.5532 | 96.8645
5 | BELAGAVI | 78 | 78 | 205:50 | 657:24 | 232:58 | 268:24 | 501:22 | 1766:10 | 707:12 | 9:04 | 99.1361 | 98.7814 | 2423:34 | 31:04 | 99.2267 | 98.9388
6 | VIJAYAPUR | 42 | 41 | 60:26 | 456:30 | 247:00 | 268:05 | 515:05 | 1997:02 | 575:31 | 13:42 | 98.3516 | 98.1582 | 2453:32 | 58:25 | 98.3761 | 98.0049
7 | BAGALKOT | 25 | 25 | 9:46 | 329:04 | 117:43 | 162:15 | 279:58 | 1041:11 | 289:44 | 11:35 | 98.4948 | 98.4423 | 1370:15 | 54:49 | 98.5776 | 98.1281
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of August-2023
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Aug-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Aug-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 42 | 42 | 41:40 | 108:09 | 854:24 | 111:22 | 965:46 | 4424:29 | 1007:26 | 23:59 | 96.9093 | 96.776 | 4532:38 | 107:55 | 97.1311 | 97.061
2 | GADAG | 12 | 12 | 10:00 | 131:00 | 60:01 | 39:14 | 99:15 | 559:15 | 109:15 | 9:06 | 98.8883 | 98.7763 | 690:15 | 57:31 | 98.7308 | 98.4335
3 | HAVERI | 8 | 8 | 0:00 | 0:00 | 91:56 | 19:33 | 111:29 | 608:51 | 111:29 | 13:56 | 98.127 | 98.127 | 608:51 | 76:06 | 97.9274 | 97.9274
4 | KARWAR | 10 | 10 | 9:08 | 210:46 | 73:46 | 55:10 | 128:56 | 845:22 | 138:04 | 13:48 | 98.267 | 98.1443 | 1056:08 | 105:37 | 97.6978 | 97.1238
5 | BELAGAVI | 78 | 77 | 113:47 | 771:11 | 238:10 | 170:29 | 408:39 | 2174:49 | 522:26 | 6:42 | 99.2958 | 99.0997 | 2946:00 | 37:46 | 99.2407 | 98.9714
6 | VIJAYAPUR | 41 | 41 | 1:09 | 457:39 | 212:22 | 147:04 | 359:26 | 2356:28 | 360:35 | 8:48 | 98.8217 | 98.8179 | 2814:07 | 68:38 | 98.4348 | 98.1308
7 | BAGALKOT | 25 | 25 | 254:05 | 583:09 | 61:37 | 97:41 | 159:18 | 1200:29 | 413:23 | 16:32 | 99.1435 | 97.7775 | 1783:38 | 71:21 | 98.6923 | 98.057
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of September-2023
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Sept-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Sept-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 41 | 40 | 24:00 | 132:09 | 467:40 | 169:30 | 637:10 | 5061:39 | 661:10 | 16:08 | 97.8416 | 97.7603 | 5193:48 | 126:41 | 97.1891 | 97.1157
2 | GADAG | 12 | 12 | 35:20 | 166:20 | 118:53 | 24:48 | 143:41 | 702:56 | 179:01 | 14:55 | 98.337 | 97.928 | 869:16 | 72:26 | 98.6663 | 98.3507
3 | HAVERI | 8 | 8 | 24:28 | 24:28 | 61:08 | 38:28 | 99:36 | 708:27 | 124:04 | 15:30 | 98.2708 | 97.8461 | 732:55 | 91:37 | 97.9837 | 97.9141
4 | KARWAR | 10 | 10 | 21:06 | 231:52 | 40:34 | 102:55 | 143:29 | 988:51 | 164:35 | 16:28 | 98.0072 | 97.7141 | 1220:43 | 122:04 | 97.7485 | 97.2206
5 | BELAGAVI | 78 | 78 | 274:02 | 1045:13 | 503:07 | 123:56 | 627:03 | 2801:52 | 901:05 | 11:33 | 98.8835 | 98.3955 | 3847:05 | 49:19 | 99.1821 | 98.877
6 | VIJAYAPUR | 41 | 41 | 323:18 | 780:57 | 241:55 | 195:58 | 437:53 | 2794:21 | 761:11 | 18:34 | 98.5167 | 97.4215 | 3575:18 | 87:12 | 98.4482 | 98.0145
7 | BAGALKOT | 25 | 25 | 173:24 | 756:33 | 60:56 | 57:43 | 118:39 | 1319:08 | 292:03 | 11:41 | 99.3408 | 98.3775 | 2075:41 | 83:02 | 98.7986 | 98.1096
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of October-2023
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of October-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Oct-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 42 | 41 | 1:30 | 133:39 | 640:13 | 177:12 | 817:25 | 5879:04 | 818:55 | 19:30 | 97.3841 | 97.3793 | 6012:43 | 143:10 | 97.2746 | 97.2126
2 | GADAG | 12 | 12 | 5:24 | 171:44 | 83:34 | 13:24 | 96:58 | 799:54 | 102:22 | 8:32 | 98.9139 | 98.8534 | 971:38 | 80:58 | 98.7021 | 98.4235
3 | HAVERI | 8 | 8 | 2:00 | 26:28 | 41:47 | 16:14 | 58:01 | 766:28 | 60:01 | 7:30 | 99.0253 | 98.9917 | 792:56 | 99:07 | 98.1346 | 98.0702
4 | KARWAR | 10 | 10 | 35:44 | 267:36 | 34:11 | 43:50 | 78:01 | 1066:52 | 113:45 | 11:22 | 98.9514 | 98.4711 | 1334:28 | 133:27 | 97.9228 | 97.4017
5 | BELAGAVI | 78 | 78 | 84:34 | 1129:47 | 435:16 | 168:16 | 603:32 | 3405:24 | 688:06 | 8:49 | 98.96 | 98.8143 | 4535:11 | 58:09 | 99.1499 | 98.8679
6 | VIJAYAPUR | 41 | 41 | 441:09 | 1222:06 | 216:24 | 214:51 | 431:15 | 3225:36 | 872:24 | 21:17 | 98.5863 | 97.14 | 4447:42 | 108:29 | 98.4682 | 97.8878
7 | BAGALKOT | 25 | 25 | 10:50 | 767:23 | 39:20 | 41:29 | 80:49 | 1399:57 | 91:39 | 3:40 | 99.5655 | 99.5073 | 2167:20 | 86:42 | 98.9097 | 98.312
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of November-2023
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of November-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Nov-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 42 | 42 | 69:04 | 202:43 | 711:08 | 91:57 | 803:05 | 6682:09 | 872:09 | 20:46 | 97.3443 | 97.1159 | 6884:52 | 163:56 | 97.2831 | 97.2007
2 | GADAG | 12 | 12 | 0:00 | 171:44 | 48:41 | 29:58 | 78:39 | 878:33 | 78:39 | 6:33 | 99.0897 | 99.0897 | 1050:17 | 87:31 | 98.7498 | 98.5054
3 | HAVERI | 8 | 8 | 4:52 | 31:20 | 19:29 | 24:54 | 44:23 | 810:51 | 49:15 | 6:09 | 99.2295 | 99.145 | 842:11 | 105:16 | 98.2692 | 98.2023
4 | KARWAR | 10 | 10 | 5:30 | 273:06 | 21:58 | 54:44 | 76:42 | 1143:34 | 82:12 | 8:13 | 98.9347 | 98.8583 | 1416:40 | 141:40 | 98.0472 | 97.5808
5 | BELAGAVI | 78 | 78 | 493:39 | 1623:26 | 434:27 | 170:34 | 605:01 | 4010:25 | 1098:40 | 14:05 | 98.9227 | 98.0437 | 5633:51 | 72:14 | 99.122 | 98.7666
6 | VIJAYAPUR | 41 | 41 | 14:10 | 1236:16 | 200:30 | 88:46 | 289:16 | 3514:52 | 303:26 | 7:24 | 99.0201 | 98.9721 | 4751:08 | 115:53 | 98.5361 | 98.0212
7 | BAGALKOT | 24 | 24 | 3:38 | 771:01 | 37:38 | 52:02 | 89:40 | 1489:37 | 93:18 | 3:53 | 99.4811 | 99.4601 | 2260:38 | 94:12 | 98.9401 | 98.3915
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of December-2023
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of December-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Dec-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 41 | 40 | 2:48 | 205:31 | 578:04 | 59:14 | 637:18 | 7319:27 | 640:06 | 15:37 | 97.9108 | 97.9016 | 7524:58 | 183:32 | 97.2951 | 97.2192
2 | GADAG | 12 | 12 | 9:54 | 181:38 | 113:15 | 12:25 | 125:40 | 1004:13 | 135:34 | 11:18 | 98.5924 | 98.4816 | 1185:51 | 98:49 | 98.732 | 98.5027
3 | HAVERI | 8 | 8 | 2:55 | 34:15 | 104:37 | 23:07 | 127:44 | 938:35 | 130:39 | 16:20 | 97.8539 | 97.8049 | 972:50 | 121:36 | 98.2224 | 98.1575
4 | KARWAR | 10 | 10 | 2:00 | 275:06 | 42:23 | 38:29 | 80:52 | 1224:26 | 82:52 | 8:17 | 98.9131 | 98.8862 | 1499:32 | 149:57 | 98.1448 | 97.728
5 | BELAGAVI | 78 | 74 | 25:09 | 1648:35 | 55:20 | 54:05 | 109:25 | 4119:50 | 134:34 | 1:44 | 99.8115 | 99.7681 | 5768:25 | 73:57 | 99.1997 | 98.8795
6 | VIJAYAPUR | 41 | 41 | 409:38 | 1645:54 | 217:35 | 186:20 | 403:55 | 3918:47 | 813:33 | 19:51 | 98.6759 | 97.333 | 5564:41 | 135:43 | 98.5518 | 97.9436
7 | BAGALKOT | 25 | 25 | 96:30 | 867:31 | 112:14 | 39:34 | 151:48 | 1641:25 | 248:18 | 9:56 | 99.1839 | 98.6651 | 2508:56 | 100:21 | 99.0052 | 98.4794
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of January-2024
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of January-2024 |  |  |  | Reliability for cumulative period from Apr-23 to Jan-24
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 41 | 38 | 0:57 | 206:28 | 510:20 | 60:39 | 570:59 | 7890:26 | 571:56 | 13:57 | 98.1282 | 98.1251 | 8096:54 | 197:29 | 97.3795 | 97.3109
2 | GADAG | 12 | 12 | 7:30 | 189:08 | 46:10 | 12:05 | 58:15 | 1062:28 | 65:45 | 5:29 | 99.3476 | 99.2636 | 1251:36 | 104:18 | 98.7944 | 98.5798
3 | HAVERI | 8 | 8 | 21:16 | 55:31 | 99:19 | 30:35 | 129:54 | 1068:29 | 151:10 | 18:54 | 97.8175 | 97.4602 | 1124:00 | 140:30 | 98.1814 | 98.0869
4 | KARWAR | 10 | 10 | 3:30 | 278:36 | 79:33 | 52:53 | 132:26 | 1356:52 | 135:56 | 13:36 | 98.22 | 98.1729 | 1635:28 | 163:33 | 98.1524 | 97.7731
5 | BELAGAVI | 78 | 76 | 21:04 | 1669:39 | 42:20 | 82:04 | 124:24 | 4244:14 | 145:28 | 1:52 | 99.7856 | 99.7493 | 5913:53 | 75:49 | 99.2591 | 98.9676
6 | VIJAYAPUR | 41 | 41 | 3:36 | 1649:30 | 313:10 | 62:36 | 375:46 | 4294:33 | 379:22 | 9:15 | 98.7681 | 98.7563 | 5944:03 | 144:59 | 98.5737 | 98.0259
7 | BAGALKOT | 25 | 25 | 36:47 | 904:18 | 60:13 | 19:14 | 79:27 | 1720:52 | 116:14 | 4:39 | 99.5728 | 99.3751 | 2625:10 | 105:00 | 99.0627 | 98.5702
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of February-2024
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of February-2024 |  |  |  | Reliability for cumulative period from Apr-23 to Feb-24
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 41 | 39 | 0:57 | 207:25 | 601:49 | 84:59 | 686:48 | 8577:14 | 687:45 | 16:46 | 97.5932 | 97.5899 | 8784:39 | 214:16 | 97.398 | 97.3351
2 | GADAG | 12 | 12 | 43:24 | 232:32 | 93:53 | 14:27 | 108:20 | 1170:48 | 151:44 | 12:39 | 98.7029 | 98.1833 | 1403:20 | 116:57 | 98.7865 | 98.5455
3 | HAVERI | 8 | 8 | 3:04 | 58:35 | 78:16 | 13:00 | 91:16 | 1159:45 | 94:20 | 11:48 | 98.3609 | 98.3058 | 1218:20 | 152:18 | 98.1969 | 98.1058
4 | KARWAR | 10 | 10 | 37:16 | 315:52 | 21:15 | 26:34 | 47:49 | 1404:41 | 85:05 | 8:30 | 99.313 | 98.7775 | 1720:33 | 172:03 | 98.2529 | 97.86
5 | BELAGAVI | 78 | 78 | 258:43 | 1928:22 | 469:36 | 167:37 | 637:13 | 4881:27 | 895:56 | 11:29 | 98.8262 | 98.3497 | 6809:49 | 87:18 | 99.2216 | 98.9141
6 | VIJAYAPUR | 41 | 41 | 228:41 | 1878:11 | 299:45 | 66:16 | 366:01 | 4660:34 | 594:42 | 14:30 | 98.7174 | 97.916 | 6538:45 | 159:29 | 98.5862 | 98.0164
7 | BAGALKOT | 25 | 22 | 0:24 | 904:42 | 50:24 | 26:26 | 76:50 | 1797:42 | 77:14 | 3:05 | 99.5584 | 99.5561 | 2702:24 | 108:06 | 99.1056 | 98.6555
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of March-2024
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of March-2024 |  |  |  | Reliability for cumulative period from Apr-23 to Mar-24
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 41 | 41 | 18:36 | 226:01 | 678:18 | 114:25 | 792:43 | 9369:57 | 811:19 | 19:47 | 97.4013 | 97.3403 | 9595:58 | 234:03 | 97.3983 | 97.3355
2 | GADAG | 12 | 12 | 0:00 | 232:32 | 29:43 | 29:43 | 59:26 | 1230:14 | 59:26 | 4:57 | 99.3343 | 99.3343 | 1462:46 | 121:54 | 98.8329 | 98.6123
3 | HAVERI | 8 | 8 | 0:00 | 58:35 | 22:25 | 14:59 | 37:24 | 1197:09 | 37:24 | 4:40 | 99.3716 | 99.3716 | 1255:44 | 156:58 | 98.2964 | 98.213
4 | KARWAR | 10 | 10 | 4:14 | 320:06 | 20:59 | 46:19 | 67:18 | 1471:59 | 71:32 | 7:09 | 99.0954 | 99.0385 | 1792:05 | 179:12 | 98.3242 | 97.9598
5 | BELAGAVI | 78 | 73 | 54:27 | 1982:49 | 161:34 | 132:19 | 293:53 | 5175:20 | 348:20 | 4:28 | 99.4936 | 99.3998 | 7158:09 | 91:46 | 99.2446 | 98.9552
6 | VIJAYAPUR | 43 | 43 | 4:40 | 1882:51 | 176:41 | 97:56 | 274:37 | 4935:11 | 279:17 | 6:30 | 99.1416 | 99.127 | 6818:02 | 158:34 | 98.6934 | 98.1949
7 | BAGALKOT | 25 | 25 | 148:19 | 1053:01 | 54:44 | 47:06 | 101:50 | 1899:32 | 250:09 | 10:00 | 99.4525 | 98.6551 | 2952:33 | 118:06 | 99.135 | 98.6555
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]

## URBAN
Annex-II | [13 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of April-2023
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Apr-23
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 84 | 84 | 20:55 | 20:55 | 210:13 | 177:10 | 387:23 | 387:23 | 408:18 | 4:52 | 99.3595 | 99.3249 | 408:18 | 4:52 | 99.3595 | 99.3249
2 | DHARWAD (RURAL) | 13 | 13 | 0:00 | 0:00 | 109:32 | 58:03 | 167:35 | 167:35 | 167:35 | 12:53 | 98.2096 | 98.2096 | 167:35 | 12:53 | 98.2096 | 98.2096
3 | KUNDAGOL | 1 | 1 | 19:45 | 19:45 | 5:40 | 1:42 | 7:22 | 7:22 | 27:07 | 27:07 | 98.9769 | 96.2338 | 27:07 | 27:07 | 98.9769 | 96.2338
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 2:39 | 14:26 | 17:05 | 17:05 | 17:05 | 17:05 | 97.6273 | 97.6273 | 17:05 | 17:05 | 97.6273 | 97.6273
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 11:40 | 7:36 | 19:16 | 19:16 | 19:16 | 19:16 | 97.3241 | 97.3241 | 19:16 | 19:16 | 97.3241 | 97.3241
6 | KALGHATAGI | 2 | 2 | 0:00 | 0:00 | 10:50 | 14:25 | 25:15 | 25:15 | 25:15 | 12:38 | 98.2465 | 98.2465 | 25:15 | 12:38 | 98.2465 | 98.2465
7 | ALNAVAR | 2 | 2 | 0:00 | 0:00 | 5:40 | 4:15 | 9:55 | 9:55 | 9:55 | 4:58 | 99.3113 | 99.3113 | 9:55 | 4:58 | 99.3113 | 99.3113
8 | NARAGUND | 2 | 2 | 13:00 | 13:00 | 18:10 | 16:25 | 34:35 | 34:35 | 47:35 | 23:48 | 97.5984 | 96.6956 | 47:35 | 23:48 | 97.5984 | 96.6956
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 5:50 | 4:05 | 9:55 | 9:55 | 9:55 | 9:55 | 98.6227 | 98.6227 | 9:55 | 9:55 | 98.6227 | 98.6227
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 18:54 | 11:48 | 30:42 | 30:42 | 30:42 | 10:14 | 98.5787 | 98.5787 | 30:42 | 10:14 | 98.5787 | 98.5787
11 | NAREGAL | 1 | 1 | 4:00 | 4:00 | 3:10 | 2:35 | 5:45 | 5:45 | 9:45 | 9:45 | 99.2014 | 98.6458 | 9:45 | 9:45 | 99.2014 | 98.6458
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 6:20 | 11:30 | 17:50 | 17:50 | 17:50 | 8:55 | 98.7616 | 98.7616 | 17:50 | 8:55 | 98.7616 | 98.7616
13 | RON | 3 | 3 | 0:00 | 0:00 | 14:20 | 25:34 | 39:54 | 39:54 | 39:54 | 13:18 | 98.1528 | 98.1528 | 39:54 | 13:18 | 98.1528 | 98.1528
14 | MUNDARAGI | 1 | 1 | 1:55 | 1:55 | 6:10 | 12:55 | 19:05 | 19:05 | 21:00 | 21:00 | 97.3495 | 97.0833 | 21:00 | 21:00 | 97.3495 | 97.0833
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 36:51 | 17:33 | 54:24 | 54:24 | 54:24 | 54:24 | 92.4444 | 92.4444 | 54:24 | 54:24 | 92.4444 | 92.4444
16 | SAVANUR | 2 | 2 | 3:25 | 3:25 | 19:50 | 3:35 | 23:25 | 23:25 | 26:50 | 13:25 | 98.3738 | 98.1366 | 26:50 | 13:25 | 98.3738 | 98.1366
17 | SHIGGAON | 3 | 3 | 11:10 | 11:10 | 9:15 | 7:40 | 16:55 | 16:55 | 28:05 | 9:22 | 99.2168 | 98.6998 | 28:05 | 9:22 | 99.2168 | 98.6998
18 | BANKAPUR | 1 | 1 | 7:50 | 7:50 | 7:25 | 8:00 | 15:25 | 15:25 | 23:15 | 23:15 | 97.8588 | 96.7708 | 23:15 | 23:15 | 97.8588 | 96.7708
19 | HANGAL | 2 | 2 | 13:30 | 13:30 | 6:45 | 5:35 | 12:20 | 12:20 | 25:50 | 12:55 | 99.1435 | 98.206 | 25:50 | 12:55 | 99.1435 | 98.206
20 | RANEBENNUR | 10 | 10 | 7:54 | 7:54 | 74:40 | 19:18 | 93:58 | 93:58 | 101:52 | 10:11 | 98.6949 | 98.5852 | 101:52 | 10:11 | 98.6949 | 98.5852
21 | TUMINAKATTI | 1 | 1 | 2:45 | 2:45 | 8:30 | 3:15 | 11:45 | 11:45 | 14:30 | 14:30 | 98.3681 | 97.9861 | 14:30 | 14:30 | 98.3681 | 97.9861
22 | RATTIHALLI | 1 | 1 | 1:50 | 1:50 | 11:40 | 6:30 | 18:10 | 18:10 | 20:00 | 20:00 | 97.4769 | 97.2222 | 20:00 | 20:00 | 97.4769 | 97.2222
23 | HIREKERUR | 1 | 1 | 2:20 | 2:20 | 4:50 | 5:40 | 10:30 | 10:30 | 12:50 | 12:50 | 98.5417 | 98.2176 | 12:50 | 12:50 | 98.5417 | 98.2176
24 | BYADAGI | 5 | 5 | 24:50 | 24:50 | 22:45 | 23:55 | 46:40 | 46:40 | 71:30 | 14:18 | 98.7037 | 98.0139 | 71:30 | 14:18 | 98.7037 | 98.0139
25 | SIRSI | 5 | 5 | 5:25 | 5:25 | 51:10 | 13:40 | 64:50 | 64:50 | 70:15 | 14:03 | 98.1991 | 98.0486 | 70:15 | 14:03 | 98.1991 | 98.0486
26 | YELLAPUR | 1 | 1 | 1:40 | 1:40 | 3:30 | 1:45 | 5:15 | 5:15 | 6:55 | 6:55 | 99.2708 | 99.0394 | 6:55 | 6:55 | 99.2708 | 99.0394
27 | MUNDAGOD | 1 | 1 | 2:20 | 2:20 | 2:55 | 3:40 | 6:35 | 6:35 | 8:55 | 8:55 | 99.0856 | 98.7616 | 8:55 | 8:55 | 99.0856 | 98.7616
28 | SIDDAPUR | 2 | 2 | 3:30 | 3:30 | 4:50 | 5:20 | 10:10 | 10:10 | 13:40 | 6:50 | 99.294 | 99.0509 | 13:40 | 6:50 | 99.294 | 99.0509
29 | DANDELI | 7 | 7 | 1:36 | 1:36 | 105:45 | 6:34 | 112:19 | 112:19 | 113:55 | 16:16 | 97.7715 | 97.7397 | 113:55 | 16:16 | 97.7715 | 97.7397
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 14:40 | 5:40 | 20:20 | 20:20 | 20:20 | 10:10 | 98.588 | 98.588 | 20:20 | 10:10 | 98.588 | 98.588
31 | ANKOLA | 2 | 2 | 6:38 | 6:38 | 9:43 | 0:22 | 10:05 | 10:05 | 16:43 | 8:22 | 99.2998 | 98.8391 | 16:43 | 8:22 | 99.2998 | 98.8391
32 | KUMTA | 3 | 3 | 7:36 | 7:36 | 7:29 | 7:13 | 14:42 | 14:42 | 22:18 | 7:26 | 99.3194 | 98.9676 | 22:18 | 7:26 | 99.3194 | 98.9676
33 | GOKARNA | 1 | 1 | 39:41 | 39:41 | 3:30 | 3:15 | 6:45 | 6:45 | 46:26 | 46:26 | 99.0625 | 93.5509 | 46:26 | 46:26 | 99.0625 | 93.5509
34 | HONNAVAR | 3 | 3 | 25:36 | 25:36 | 12:53 | 7:39 | 20:32 | 20:32 | 46:08 | 15:23 | 99.0494 | 97.8642 | 46:08 | 15:23 | 99.0494 | 97.8642
35 | BHATKAL | 3 | 3 | 3:36 | 3:36 | 9:32 | 5:29 | 15:01 | 15:01 | 18:37 | 6:12 | 99.3048 | 99.1381 | 18:37 | 6:12 | 99.3048 | 99.1381
36 | KHANAPUR | 2 | 2 | 0:50 | 0:50 | 123:20 | 14:45 | 138:05 | 138:05 | 138:55 | 69:28 | 90.4109 | 90.353 | 138:55 | 69:28 | 90.4109 | 90.353
37 | BAILHONGAL | 3 | 3 | 8:36 | 8:36 | 19:00 | 24:10 | 43:10 | 43:10 | 51:46 | 17:15 | 98.0015 | 97.6034 | 51:46 | 17:15 | 98.0015 | 97.6034
38 | KITTUR | 1 | 1 | 3:00 | 3:00 | 2:25 | 4:45 | 7:10 | 7:10 | 10:10 | 10:10 | 99.0046 | 98.588 | 10:10 | 10:10 | 99.0046 | 98.588
39 | M K HUBLI | 1 | 1 | 1:50 | 1:50 | 7:55 | 7:45 | 15:40 | 15:40 | 17:30 | 17:30 | 97.8241 | 97.5694 | 17:30 | 17:30 | 97.8241 | 97.5694
40 | SOUNDATTI | 3 | 3 | 3:30 | 3:30 | 15:16 | 8:42 | 23:58 | 23:58 | 27:28 | 9:09 | 98.8904 | 98.7284 | 27:28 | 9:09 | 98.8904 | 98.7284
41 | MUNAVALLI | 1 | 1 | 3:05 | 3:05 | 37:55 | 8:35 | 46:30 | 46:30 | 49:35 | 49:35 | 93.5417 | 93.1134 | 49:35 | 49:35 | 93.5417 | 93.1134
42 | YARAGATTI | 1 | 1 | 4:12 | 4:12 | 32:18 | 7:26 | 39:44 | 39:44 | 43:56 | 43:56 | 94.4815 | 93.8981 | 43:56 | 43:56 | 94.4815 | 93.8981
43 | RAMDURG | 2 | 2 | 4:18 | 4:18 | 29:05 | 10:05 | 39:10 | 39:10 | 43:28 | 21:44 | 97.2801 | 96.9815 | 43:28 | 21:44 | 97.2801 | 96.9815
44 | GOKAK | 10 | 10 | 34:58 | 34:58 | 9:57 | 35:24 | 45:21 | 45:21 | 80:19 | 8:02 | 99.3701 | 98.8845 | 80:19 | 8:02 | 99.3701 | 98.8845
45 | MUDALAGI | 2 | 2 | 0:10 | 0:10 | 17:55 | 4:10 | 22:05 | 22:05 | 22:15 | 11:08 | 98.4664 | 98.4549 | 22:15 | 11:08 | 98.4664 | 98.4549
46 | KONNUR | 1 | 1 | 1:05 | 1:05 | 23:16 | 1:40 | 24:56 | 24:56 | 26:01 | 26:01 | 96.537 | 96.3866 | 26:01 | 26:01 | 96.537 | 96.3866
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 26:00 | 10:00 | 36:00 | 36:00 | 36:00 | 36:00 | 95 | 95 | 36:00 | 36:00 | 95 | 95
48 | KUDACHI | 1 | 1 | 1:20 | 1:20 | 25:10 | 3:40 | 28:50 | 28:50 | 30:10 | 30:10 | 95.9954 | 95.8102 | 30:10 | 30:10 | 95.9954 | 95.8102
49 | ATHANI | 7 | 7 | 37:00 | 37:00 | 208:58 | 6:02 | 215:00 | 215:00 | 252:00 | 36:00 | 95.7341 | 95 | 252:00 | 36:00 | 95.7341 | 95
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 67:18 | 37:20 | 104:38 | 104:38 | 104:38 | 26:10 | 96.3669 | 96.3669 | 104:38 | 26:10 | 96.3669 | 96.3669
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 56:55 | 13:10 | 70:05 | 70:05 | 70:05 | 14:01 | 98.0532 | 98.0532 | 70:05 | 14:01 | 98.0532 | 98.0532
52 | SADALAGA | 1 | 1 | 0:00 | 0:00 | 13:10 | 6:25 | 19:35 | 19:35 | 19:35 | 19:35 | 97.2801 | 97.2801 | 19:35 | 19:35 | 97.2801 | 97.2801
53 | MUDDEBIHAL | 2 | 2 | 24:05 | 24:05 | 34:50 | 16:50 | 51:40 | 51:40 | 75:45 | 37:52 | 96.412 | 94.7396 | 75:45 | 37:52 | 96.412 | 94.7396
54 | TALIKOTI | 1 | 1 | 3:45 | 3:45 | 18:15 | 45:00 | 63:15 | 63:15 | 67:00 | 67:00 | 91.2153 | 90.6944 | 67:00 | 67:00 | 91.2153 | 90.6944
55 | B.BAGEWADI | 1 | 1 | 0:10 | 0:10 | 3:01 | 6:45 | 9:46 | 9:46 | 9:56 | 9:56 | 98.6435 | 98.6204 | 9:56 | 9:56 | 98.6435 | 98.6204
56 | INDI | 3 | 3 | 0:28 | 0:28 | 57:05 | 8:36 | 65:41 | 65:41 | 66:09 | 22:03 | 96.9591 | 96.9375 | 66:09 | 22:03 | 96.9591 | 96.9375
57 | SINDAGI | 2 | 2 | 4:50 | 4:50 | 42:55 | 23:35 | 66:30 | 66:30 | 71:20 | 35:40 | 95.3819 | 95.0463 | 71:20 | 35:40 | 95.3819 | 95.0463
58 | GULEDGUDDA | 2 | 2 | 1:55 | 1:55 | 57:10 | 15:45 | 72:55 | 72:55 | 74:50 | 37:25 | 94.9363 | 94.8032 | 74:50 | 37:25 | 94.9363 | 94.8032
59 | ILKAL | 7 | 7 | 18:17 | 18:17 | 85:53 | 182:28 | 268:21 | 268:21 | 286:38 | 40:57 | 94.6756 | 94.3128 | 286:38 | 40:57 | 94.6756 | 94.3128
60 | KERUR | 1 | 1 | 3:52 | 3:52 | 10:38 | 13:55 | 24:33 | 24:33 | 28:25 | 28:25 | 96.5903 | 96.0532 | 28:25 | 28:25 | 96.5903 | 96.0532
61 | HUNGUND | 4 | 4 | 23:56 | 23:56 | 31:56 | 50:12 | 82:08 | 82:08 | 106:04 | 26:31 | 97.1481 | 96.3171 | 106:04 | 26:31 | 97.1481 | 96.3171
62 | BADAMI | 2 | 2 | 4:22 | 4:22 | 13:00 | 42:07 | 55:07 | 55:07 | 59:29 | 29:45 | 96.1725 | 95.8692 | 59:29 | 29:45 | 96.1725 | 95.8692
63 | JAMKHANDI | 6 | 6 | 5:25 | 5:25 | 54:00 | 13:30 | 67:30 | 67:30 | 72:55 | 12:09 | 98.4375 | 98.3121 | 72:55 | 12:09 | 98.4375 | 98.3121
64 | MAHALINGAPUR | 2 | 2 | 1:10 | 1:10 | 33:50 | 9:13 | 43:03 | 43:03 | 44:13 | 22:07 | 97.0104 | 96.9294 | 44:13 | 22:07 | 97.0104 | 96.9294
65 | RABAKAVI | 2 | 2 | 4:20 | 4:20 | 18:40 | 3:50 | 22:30 | 22:30 | 26:50 | 13:25 | 98.4375 | 98.1366 | 26:50 | 13:25 | 98.4375 | 98.1366
66 | BANAHATTI | 2 | 2 | 1:40 | 1:40 | 13:20 | 0:45 | 14:05 | 14:05 | 15:45 | 7:52 | 99.022 | 98.9062 | 15:45 | 7:52 | 99.022 | 98.9062
67 | TERDAL | 2 | 2 | 2:00 | 2:00 | 24:10 | 4:35 | 28:45 | 28:45 | 30:45 | 15:22 | 98.0035 | 97.8646 | 30:45 | 15:22 | 98.0035 | 97.8646
68 | MUDHOL | 4 | 4 | 0:00 | 0:00 | 39:23 | 29:59 | 69:22 | 69:22 | 69:22 | 17:20 | 97.5914 | 97.5914 | 69:22 | 17:20 | 97.5914 | 97.5914
69 | BILAGI | 1 | 1 | 2:45 | 2:45 | 13:45 | 6:50 | 20:35 | 20:35 | 23:20 | 23:20 | 97.1412 | 96.7593 | 23:20 | 23:20 | 97.1412 | 96.7593
70 | LOKAPUR | 2 | 2 | 1:20 | 1:20 | 102:25 | 14:55 | 117:20 | 117:20 | 118:40 | 59:20 | 91.8519 | 91.7593 | 118:40 | 59:20 | 91.8519 | 91.7593
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of May-2023
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2023 |  |  |  | Reliability for cumulative period from Apr-23 to May-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 86 | 82 | 93:48 | 114:43 | 214:53 | 436:15 | 651:08 | 1038:31 | 744:56 | 8:40 | 98.9823 | 98.8358 | 1153:14 | 13:25 | 99.1752 | 99.084
2 | DHARWAD (RURAL) | 13 | 13 | 2:52 | 2:52 | 188:59 | 108:22 | 297:21 | 464:56 | 300:13 | 23:06 | 96.9257 | 96.896 | 467:48 | 35:59 | 97.5571 | 97.542
3 | KUNDAGOL | 1 | 1 | 34:10 | 53:55 | 6:27 | 9:17 | 15:44 | 23:06 | 49:54 | 49:54 | 97.8853 | 93.293 | 77:01 | 77:01 | 98.4221 | 94.7393
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 3:34 | 12:41 | 16:15 | 33:20 | 16:15 | 16:15 | 97.8159 | 97.8159 | 33:20 | 33:20 | 97.7231 | 97.7231
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 8:40 | 10:35 | 19:15 | 38:31 | 19:15 | 19:15 | 97.4126 | 97.4126 | 38:31 | 38:31 | 97.3691 | 97.3691
6 | KALGHATAGI | 2 | 2 | 7:50 | 7:50 | 7:00 | 16:35 | 23:35 | 48:50 | 31:25 | 15:42 | 98.4151 | 97.8887 | 56:40 | 28:20 | 98.3322 | 98.0647
7 | ALNAVAR | 2 | 2 | 9:05 | 9:05 | 31:25 | 7:20 | 38:45 | 48:40 | 47:50 | 23:55 | 97.3958 | 96.7854 | 57:45 | 28:52 | 98.3379 | 98.0277
8 | NARAGUND | 2 | 2 | 2:40 | 15:40 | 15:10 | 31:20 | 46:30 | 81:05 | 49:10 | 24:35 | 96.875 | 96.6958 | 96:45 | 48:22 | 97.2308 | 96.6957
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 8:45 | 14:00 | 22:45 | 32:40 | 22:45 | 22:45 | 96.9422 | 96.9422 | 32:40 | 32:40 | 97.7687 | 97.7687
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 51:26 | 31:03 | 82:29 | 113:11 | 82:29 | 27:30 | 96.3045 | 96.3045 | 113:11 | 37:44 | 97.423 | 97.423
11 | NAREGAL | 1 | 1 | 0:20 | 4:20 | 1:30 | 2:20 | 3:50 | 9:35 | 4:10 | 4:10 | 99.4848 | 99.44 | 13:55 | 13:55 | 99.3454 | 99.0494
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 8:45 | 9:00 | 17:45 | 35:35 | 17:45 | 8:52 | 98.8071 | 98.8071 | 35:35 | 17:48 | 98.7847 | 98.7847
13 | RON | 3 | 3 | 0:00 | 0:00 | 15:55 | 11:07 | 27:02 | 66:56 | 27:02 | 9:01 | 98.7888 | 98.7888 | 66:56 | 22:19 | 98.476 | 98.476
14 | MUNDARAGI | 1 | 1 | 0:00 | 1:55 | 6:05 | 17:23 | 23:28 | 42:33 | 23:28 | 23:28 | 96.8459 | 96.8459 | 44:28 | 44:28 | 97.0936 | 96.9627
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 31:08 | 19:55 | 51:03 | 105:27 | 51:03 | 51:03 | 93.1384 | 93.1384 | 105:27 | 105:27 | 92.7971 | 92.7971
16 | SAVANUR | 2 | 2 | 2:40 | 6:05 | 53:25 | 36:00 | 89:25 | 112:50 | 92:05 | 46:02 | 93.9908 | 93.8116 | 118:55 | 59:28 | 96.1464 | 95.9386
17 | SHIGGAON | 3 | 3 | 24:30 | 35:40 | 21:35 | 27:50 | 49:25 | 66:20 | 73:55 | 24:38 | 97.786 | 96.6883 | 102:00 | 34:00 | 98.4897 | 97.6776
18 | BANKAPUR | 1 | 1 | 14:35 | 22:25 | 11:30 | 10:15 | 21:45 | 37:10 | 36:20 | 36:20 | 97.0766 | 95.1165 | 59:35 | 59:35 | 97.4613 | 95.9301
19 | HANGAL | 2 | 2 | 17:40 | 31:10 | 34:05 | 78:45 | 112:50 | 125:10 | 130:30 | 65:15 | 92.4171 | 91.2298 | 156:20 | 78:10 | 95.7252 | 94.6607
20 | RANEBENNUR | 10 | 10 | 5:40 | 13:34 | 84:44 | 83:08 | 167:52 | 261:50 | 173:32 | 17:21 | 97.7437 | 97.6676 | 275:24 | 27:32 | 98.2115 | 98.1189
21 | TUMINAKATTI | 1 | 1 | 1:15 | 4:00 | 13:20 | 4:45 | 18:05 | 29:50 | 19:20 | 19:20 | 97.5694 | 97.4014 | 33:50 | 33:50 | 97.9622 | 97.689
22 | RATTIHALLI | 1 | 1 | 1:10 | 3:00 | 27:25 | 14:20 | 41:45 | 59:55 | 42:55 | 42:55 | 94.3884 | 94.2316 | 62:55 | 62:55 | 95.9073 | 95.7024
23 | HIREKERUR | 1 | 1 | 1:20 | 3:40 | 8:15 | 15:00 | 23:15 | 33:45 | 24:35 | 24:35 | 96.875 | 96.6958 | 37:25 | 37:25 | 97.6947 | 97.4442
24 | BYADAGI | 5 | 5 | 42:29 | 67:19 | 45:50 | 70:13 | 116:03 | 162:43 | 158:32 | 31:42 | 96.8804 | 95.7384 | 230:02 | 46:00 | 97.7771 | 96.8575
25 | SIRSI | 5 | 5 | 35:00 | 40:25 | 49:15 | 35:05 | 84:20 | 149:10 | 119:20 | 23:52 | 97.733 | 96.7921 | 189:35 | 37:55 | 97.9622 | 97.4101
26 | YELLAPUR | 1 | 1 | 6:05 | 7:45 | 3:55 | 13:25 | 17:20 | 22:35 | 23:25 | 23:25 | 97.6703 | 96.8526 | 30:20 | 30:20 | 98.4574 | 97.9281
27 | MUNDAGOD | 1 | 1 | 0:00 | 2:20 | 4:40 | 4:50 | 9:30 | 16:05 | 9:30 | 9:30 | 98.7231 | 98.7231 | 18:25 | 18:25 | 98.9014 | 98.742
28 | SIDDAPUR | 2 | 2 | 1:30 | 5:00 | 8:15 | 11:01 | 19:16 | 29:26 | 20:46 | 10:23 | 98.7052 | 98.6044 | 34:26 | 17:13 | 98.9948 | 98.824
29 | DANDELI | 7 | 7 | 10:10 | 11:46 | 47:11 | 90:20 | 137:31 | 249:50 | 147:41 | 21:06 | 97.3595 | 97.1643 | 261:36 | 37:22 | 97.5621 | 97.4473
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 14:40 | 5:40 | 20:20 | 40:40 | 20:20 | 10:10 | 98.6335 | 98.6335 | 40:40 | 20:20 | 98.6111 | 98.6111
31 | ANKOLA | 2 | 2 | 30:56 | 37:34 | 15:38 | 14:28 | 30:06 | 40:11 | 61:02 | 30:31 | 97.9772 | 95.8983 | 77:45 | 38:52 | 98.6276 | 97.3446
32 | KUMTA | 3 | 3 | 1:33 | 9:09 | 22:49 | 12:00 | 34:49 | 49:31 | 36:22 | 12:07 | 98.4401 | 98.3707 | 58:40 | 19:33 | 98.8726 | 98.6642
33 | GOKARNA | 1 | 1 | 13:45 | 53:26 | 3:50 | 0:55 | 4:45 | 11:30 | 18:30 | 18:30 | 99.3616 | 97.5134 | 64:56 | 64:56 | 99.2145 | 95.5647
34 | HONNAVAR | 3 | 3 | 5:09 | 30:45 | 25:02 | 17:45 | 42:47 | 63:19 | 47:56 | 15:59 | 98.0832 | 97.8524 | 94:04 | 31:21 | 98.5584 | 97.8582
35 | BHATKAL | 3 | 3 | 7:03 | 10:39 | 31:02 | 0:00 | 31:02 | 46:03 | 38:05 | 12:42 | 98.6096 | 98.2938 | 56:42 | 18:54 | 98.9515 | 98.709
36 | KHANAPUR | 2 | 2 | 1:00 | 1:50 | 10:35 | 10:35 | 21:10 | 159:15 | 22:10 | 11:05 | 98.5775 | 98.5103 | 161:05 | 80:32 | 94.5611 | 94.4985
37 | BAILHONGAL | 3 | 3 | 0:00 | 8:36 | 18:00 | 14:00 | 32:00 | 75:10 | 32:00 | 10:40 | 98.5663 | 98.5663 | 83:46 | 27:55 | 98.2886 | 98.0927
38 | KITTUR | 1 | 1 | 0:55 | 3:55 | 3:20 | 6:00 | 9:20 | 16:30 | 10:15 | 10:15 | 98.7455 | 98.6223 | 20:25 | 20:25 | 98.873 | 98.6054
39 | M K HUBLI | 1 | 1 | 0:00 | 1:50 | 11:50 | 9:15 | 21:05 | 36:45 | 21:05 | 21:05 | 97.1662 | 97.1662 | 38:35 | 38:35 | 97.4898 | 97.3645
40 | SOUNDATTI | 3 | 3 | 19:51 | 23:21 | 31:02 | 28:39 | 59:41 | 83:39 | 79:32 | 26:31 | 97.326 | 96.4367 | 107:00 | 35:40 | 98.0954 | 97.5638
41 | MUNAVALLI | 1 | 1 | 12:20 | 15:25 | 32:40 | 4:35 | 37:15 | 83:45 | 49:35 | 49:35 | 94.9933 | 93.3356 | 99:10 | 99:10 | 94.2794 | 93.2263
42 | YARAGATTI | 1 | 1 | 4:28 | 8:40 | 28:47 | 9:37 | 38:24 | 78:08 | 42:52 | 42:52 | 94.8387 | 94.2384 | 86:48 | 86:48 | 94.663 | 94.071
43 | RAMDURG | 2 | 2 | 9:54 | 14:12 | 42:34 | 4:45 | 47:19 | 86:29 | 57:13 | 28:36 | 96.8201 | 96.1548 | 100:41 | 50:20 | 97.0463 | 96.5614
44 | GOKAK | 10 | 10 | 26:17 | 61:15 | 41:18 | 52:12 | 93:30 | 138:51 | 119:47 | 11:59 | 98.7433 | 98.39 | 200:06 | 20:01 | 99.0516 | 98.6332
45 | MUDALAGI | 2 | 2 | 1:40 | 1:50 | 18:25 | 24:40 | 43:05 | 65:10 | 44:45 | 22:22 | 97.1046 | 96.9926 | 67:00 | 33:30 | 97.7744 | 97.7117
46 | KONNUR | 1 | 1 | 0:10 | 1:15 | 21:10 | 2:55 | 24:05 | 49:01 | 24:15 | 24:15 | 96.763 | 96.7406 | 50:16 | 50:16 | 96.6519 | 96.5665
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 27:10 | 13:55 | 41:05 | 77:05 | 41:05 | 41:05 | 94.478 | 94.478 | 77:05 | 77:05 | 94.7347 | 94.7347
48 | KUDACHI | 1 | 1 | 1:15 | 2:35 | 7:35 | 24:50 | 32:25 | 61:15 | 33:40 | 33:40 | 95.6429 | 95.4749 | 63:50 | 63:50 | 95.8163 | 95.6398
49 | ATHANI | 7 | 7 | 63:15 | 100:15 | 174:55 | 133:11 | 308:06 | 523:06 | 371:21 | 53:03 | 94.0841 | 92.8696 | 623:21 | 89:03 | 94.8956 | 93.9173
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 25:50 | 20:26 | 46:16 | 150:54 | 46:16 | 11:34 | 98.4453 | 98.4453 | 150:54 | 37:44 | 97.4232 | 97.4232
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 45:45 | 53:00 | 98:45 | 168:50 | 98:45 | 19:45 | 97.3454 | 97.3454 | 168:50 | 33:46 | 97.6935 | 97.6935
52 | SADALAGA | 1 | 1 | 5:20 | 5:20 | 17:55 | 3:40 | 21:35 | 41:10 | 26:55 | 26:55 | 97.099 | 96.3822 | 46:30 | 46:30 | 97.1881 | 96.8238
53 | MUDDEBIHAL | 2 | 2 | 0:30 | 24:35 | 22:41 | 16:00 | 38:41 | 90:21 | 39:11 | 19:36 | 97.4003 | 97.3667 | 114:56 | 57:28 | 96.9143 | 96.0747
54 | TALIKOTI | 1 | 1 | 4:15 | 8:00 | 16:50 | 18:05 | 34:55 | 98:10 | 39:10 | 39:10 | 95.3069 | 94.7357 | 106:10 | 106:10 | 93.2946 | 92.7482
55 | B.BAGEWADI | 1 | 1 | 2:28 | 2:38 | 3:02 | 3:58 | 7:00 | 16:46 | 9:28 | 9:28 | 99.0591 | 98.7276 | 19:24 | 19:24 | 98.8547 | 98.6749
56 | INDI | 3 | 3 | 1:06 | 1:34 | 6:41 | 12:46 | 19:27 | 85:08 | 20:33 | 6:51 | 99.1286 | 99.0793 | 86:42 | 28:54 | 98.0616 | 98.026
57 | SINDAGI | 2 | 2 | 2:00 | 6:50 | 55:15 | 24:55 | 80:10 | 146:40 | 82:10 | 41:05 | 94.6125 | 94.478 | 153:30 | 76:45 | 94.9909 | 94.7575
58 | GULEDGUDDA | 2 | 2 | 0:00 | 1:55 | 9:30 | 15:00 | 24:30 | 97:25 | 24:30 | 12:15 | 98.3535 | 98.3535 | 99:20 | 49:40 | 96.6729 | 96.6075
59 | ILKAL | 7 | 7 | 10:27 | 28:44 | 49:15 | 126:14 | 175:29 | 443:50 | 185:56 | 26:34 | 96.6305 | 96.4299 | 472:34 | 67:31 | 95.6691 | 95.3887
60 | KERUR | 1 | 1 | 0:40 | 4:32 | 12:58 | 18:02 | 31:00 | 55:33 | 31:40 | 31:40 | 95.8333 | 95.7437 | 60:05 | 60:05 | 96.2056 | 95.8959
61 | HUNGUND | 4 | 4 | 10:12 | 34:08 | 23:17 | 31:30 | 54:47 | 136:55 | 64:59 | 16:15 | 98.1592 | 97.8164 | 171:03 | 42:46 | 97.6619 | 97.0791
62 | BADAMI | 2 | 2 | 2:16 | 6:38 | 19:04 | 18:06 | 37:10 | 92:17 | 39:26 | 19:43 | 97.5022 | 97.3499 | 98:55 | 49:28 | 96.8482 | 96.6217
63 | JAMKHANDI | 6 | 6 | 8:25 | 13:50 | 86:50 | 62:25 | 149:15 | 216:45 | 157:40 | 26:17 | 96.6566 | 96.468 | 230:35 | 38:26 | 97.5324 | 97.375
64 | MAHALINGAPUR | 2 | 2 | 1:18 | 2:28 | 29:59 | 6:04 | 36:03 | 79:06 | 37:21 | 18:40 | 97.5773 | 97.4899 | 81:34 | 40:47 | 97.2985 | 97.2143
65 | RABAKAVI | 2 | 2 | 2:20 | 6:40 | 25:35 | 4:20 | 29:55 | 52:25 | 32:15 | 16:08 | 97.9895 | 97.8327 | 59:05 | 29:33 | 98.2098 | 97.9821
66 | BANAHATTI | 2 | 2 | 2:42 | 4:22 | 32:57 | 4:15 | 37:12 | 51:17 | 39:54 | 19:57 | 97.5 | 97.3185 | 55:39 | 27:49 | 98.2485 | 98.0994
67 | TERDAL | 2 | 2 | 0:50 | 2:50 | 51:05 | 10:35 | 61:40 | 90:25 | 62:30 | 31:15 | 95.8557 | 95.7997 | 93:15 | 46:38 | 96.912 | 96.8152
68 | MUDHOL | 4 | 4 | 16:27 | 16:27 | 46:01 | 29:54 | 75:55 | 145:17 | 92:22 | 23:06 | 97.449 | 96.8963 | 161:44 | 40:26 | 97.5191 | 97.2382
69 | BILAGI | 1 | 1 | 3:45 | 6:30 | 18:00 | 4:50 | 22:50 | 43:25 | 26:35 | 26:35 | 96.931 | 96.427 | 49:55 | 49:55 | 97.0344 | 96.5904
70 | LOKAPUR | 2 | 2 | 0:00 | 1:20 | 40:20 | 33:10 | 73:30 | 190:50 | 73:30 | 36:45 | 95.0605 | 95.0605 | 192:10 | 96:05 | 93.4825 | 93.4369
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of June-2023
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2023 |  |  |  | Reliability for cumulative period from Apr-23 to June-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 84 | 84 | 134:01 | 248:44 | 629:05 | 258:52 | 887:57 | 1926:28 | 1021:58 | 12:10 | 98.5318 | 98.3102 | 2175:12 | 25:54 | 98.9499 | 98.8143
2 | DHARWAD (RURAL) | 14 | 14 | 7:44 | 10:36 | 102:29 | 73:41 | 176:10 | 641:06 | 183:54 | 13:08 | 98.2523 | 98.1756 | 651:42 | 46:33 | 97.9033 | 97.8686
3 | KUNDAGOL | 1 | 1 | 28:37 | 82:32 | 3:54 | 1:38 | 5:32 | 28:38 | 34:09 | 34:09 | 99.2315 | 95.2569 | 111:10 | 111:10 | 98.6889 | 94.91
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 14:57 | 8:02 | 22:59 | 56:19 | 22:59 | 22:59 | 96.8079 | 96.8079 | 56:19 | 56:19 | 97.4214 | 97.4214
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 6:10 | 16:42 | 22:52 | 61:23 | 22:52 | 22:52 | 96.8241 | 96.8241 | 61:23 | 61:23 | 97.1894 | 97.1894
6 | KALGHATAGI | 2 | 2 | 0:00 | 7:50 | 29:00 | 6:35 | 35:35 | 84:25 | 35:35 | 17:48 | 97.5289 | 97.5289 | 92:15 | 46:07 | 98.0674 | 97.888
7 | ALNAVAR | 2 | 2 | 0:00 | 9:05 | 2:40 | 5:05 | 7:45 | 56:25 | 7:45 | 3:52 | 99.4618 | 99.4618 | 65:30 | 32:45 | 98.7084 | 98.5005
8 | NARAGUND | 2 | 2 | 4:40 | 20:20 | 39:50 | 42:00 | 81:50 | 162:55 | 86:30 | 43:15 | 94.3171 | 93.9931 | 183:15 | 91:38 | 96.2702 | 95.8047
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 10:35 | 4:05 | 14:40 | 47:20 | 14:40 | 14:40 | 97.963 | 97.963 | 47:20 | 47:20 | 97.8327 | 97.8327
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 29:09 | 20:39 | 49:48 | 162:59 | 49:48 | 16:36 | 97.6944 | 97.6944 | 162:59 | 54:20 | 97.5125 | 97.5125
11 | NAREGAL | 1 | 1 | 1:15 | 5:35 | 11:25 | 2:10 | 13:35 | 23:10 | 14:50 | 14:50 | 98.1134 | 97.9398 | 28:45 | 28:45 | 98.9393 | 98.6836
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 33:15 | 7:15 | 40:30 | 76:05 | 40:30 | 20:15 | 97.1875 | 97.1875 | 76:05 | 38:02 | 98.2582 | 98.2582
13 | RON | 3 | 3 | 0:00 | 0:00 | 62:35 | 10:28 | 73:03 | 139:59 | 73:03 | 24:21 | 96.6181 | 96.6181 | 139:59 | 46:40 | 97.8635 | 97.8635
14 | MUNDARAGI | 1 | 1 | 9:28 | 11:23 | 10:10 | 12:05 | 22:15 | 64:48 | 31:43 | 31:43 | 96.9097 | 95.5949 | 76:11 | 76:11 | 97.033 | 96.5118
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 28:38 | 29:22 | 58:00 | 163:27 | 58:00 | 58:00 | 91.9444 | 91.9444 | 163:27 | 163:27 | 92.516 | 92.516
16 | SAVANUR | 2 | 2 | 1:15 | 7:20 | 25:20 | 8:55 | 34:15 | 147:05 | 35:30 | 17:45 | 97.6215 | 97.5347 | 154:25 | 77:13 | 96.6327 | 96.4648
17 | SHIGGAON | 3 | 3 | 10:30 | 46:10 | 6:05 | 14:40 | 20:45 | 87:05 | 31:15 | 10:25 | 99.0394 | 98.5532 | 133:15 | 44:25 | 98.6709 | 97.9663
18 | BANKAPUR | 1 | 1 | 21:30 | 43:55 | 12:40 | 19:20 | 32:00 | 69:10 | 53:30 | 53:30 | 95.5556 | 92.5694 | 113:05 | 113:05 | 96.833 | 94.8222
19 | HANGAL | 2 | 2 | 35:40 | 66:50 | 13:00 | 11:50 | 24:50 | 150:00 | 60:30 | 30:15 | 98.2755 | 95.7986 | 216:50 | 108:25 | 96.5659 | 95.0359
20 | RANEBENNUR | 10 | 10 | 7:19 | 20:53 | 144:38 | 48:30 | 193:08 | 454:58 | 200:27 | 20:03 | 97.3176 | 97.216 | 475:51 | 47:35 | 97.9168 | 97.8212
21 | TUMINAKATTI | 1 | 1 | 0:30 | 4:30 | 20:55 | 0:30 | 21:25 | 51:15 | 21:55 | 21:55 | 97.0255 | 96.956 | 55:45 | 55:45 | 97.6534 | 97.4473
22 | RATTIHALLI | 1 | 1 | 0:50 | 3:50 | 14:30 | 7:45 | 22:15 | 82:10 | 23:05 | 23:05 | 96.9097 | 96.794 | 86:00 | 86:00 | 96.2378 | 96.0623
23 | HIREKERUR | 1 | 1 | 0:50 | 4:30 | 20:25 | 11:25 | 31:50 | 65:35 | 32:40 | 32:40 | 95.5787 | 95.463 | 70:05 | 70:05 | 96.9971 | 96.7911
24 | BYADAGI | 5 | 5 | 19:42 | 87:01 | 85:25 | 71:50 | 157:15 | 319:58 | 176:57 | 35:23 | 95.6319 | 95.0847 | 406:59 | 81:24 | 97.0699 | 96.273
25 | SIRSI | 5 | 5 | 3:45 | 44:10 | 32:45 | 15:10 | 47:55 | 197:05 | 51:40 | 10:20 | 98.669 | 98.5648 | 241:15 | 48:15 | 98.1952 | 97.7908
26 | YELLAPUR | 1 | 1 | 3:45 | 11:30 | 2:00 | 13:30 | 15:30 | 38:05 | 19:15 | 19:15 | 97.8472 | 97.3264 | 49:35 | 49:35 | 98.2563 | 97.7297
27 | MUNDAGOD | 1 | 1 | 0:22 | 2:42 | 13:55 | 4:20 | 18:15 | 34:20 | 18:37 | 18:37 | 97.4653 | 97.4144 | 37:02 | 37:02 | 98.428 | 98.3043
28 | SIDDAPUR | 2 | 2 | 1:30 | 6:30 | 20:10 | 7:05 | 27:15 | 56:41 | 28:45 | 14:22 | 98.1076 | 98.0035 | 63:11 | 31:36 | 98.7023 | 98.5535
29 | DANDELI | 7 | 7 | 31:47 | 43:33 | 138:37 | 36:40 | 175:17 | 425:07 | 207:04 | 29:35 | 96.5222 | 95.8915 | 468:40 | 66:57 | 97.2193 | 96.9344
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 5:30 | 10:40 | 16:10 | 56:50 | 16:10 | 8:05 | 98.8773 | 98.8773 | 56:50 | 28:25 | 98.6989 | 98.6989
31 | ANKOLA | 2 | 2 | 5:38 | 43:12 | 12:13 | 17:31 | 29:44 | 69:55 | 35:22 | 17:41 | 97.9352 | 97.544 | 113:07 | 56:34 | 98.3993 | 97.4103
32 | KUMTA | 3 | 3 | 1:12 | 10:21 | 38:27 | 25:21 | 63:48 | 113:19 | 65:00 | 21:40 | 97.0463 | 96.9907 | 123:40 | 41:13 | 98.2705 | 98.1125
33 | GOKARNA | 1 | 1 | 26:40 | 80:06 | 6:35 | 1:40 | 8:15 | 19:45 | 34:55 | 34:55 | 98.8542 | 95.1505 | 99:51 | 99:51 | 99.0957 | 95.4281
34 | HONNAVAR | 3 | 3 | 14:27 | 45:12 | 39:39 | 15:18 | 54:57 | 118:16 | 69:24 | 23:08 | 97.456 | 96.787 | 163:28 | 54:29 | 98.195 | 97.5051
35 | BHATKAL | 3 | 3 | 20:33 | 31:12 | 21:24 | 13:35 | 34:59 | 81:02 | 55:32 | 18:31 | 98.3804 | 97.429 | 112:14 | 37:25 | 98.7632 | 98.287
36 | KHANAPUR | 2 | 2 | 11:10 | 13:00 | 21:50 | 5:35 | 27:25 | 186:40 | 38:35 | 19:18 | 98.0961 | 97.3206 | 199:40 | 99:50 | 95.7265 | 95.4289
37 | BAILHONGAL | 3 | 3 | 0:00 | 8:36 | 73:10 | 13:00 | 86:10 | 161:20 | 86:10 | 28:43 | 96.0108 | 96.0108 | 169:56 | 56:39 | 97.5376 | 97.4064
38 | KITTUR | 1 | 1 | 0:45 | 4:40 | 10:50 | 3:10 | 14:00 | 30:30 | 14:45 | 14:45 | 98.0556 | 97.9514 | 35:10 | 35:10 | 98.6035 | 98.3898
39 | M K HUBLI | 1 | 1 | 0:00 | 1:50 | 15:35 | 10:15 | 25:50 | 62:35 | 25:50 | 25:50 | 96.412 | 96.412 | 64:25 | 64:25 | 97.1345 | 97.0505
40 | SOUNDATTI | 3 | 3 | 0:20 | 23:41 | 16:15 | 7:57 | 24:12 | 107:51 | 24:32 | 8:11 | 98.8796 | 98.8642 | 131:32 | 43:51 | 98.3539 | 97.9925
41 | MUNAVALLI | 1 | 1 | 4:10 | 19:35 | 48:05 | 5:05 | 53:10 | 136:55 | 57:20 | 57:20 | 92.6157 | 92.037 | 156:30 | 156:30 | 93.7309 | 92.8342
42 | YARAGATTI | 1 | 1 | 7:50 | 16:30 | 27:20 | 6:27 | 33:47 | 111:55 | 41:37 | 41:37 | 95.3079 | 94.2199 | 128:25 | 128:25 | 94.8756 | 94.1201
43 | RAMDURG | 2 | 2 | 11:25 | 25:37 | 22:26 | 6:40 | 29:06 | 115:35 | 40:31 | 20:16 | 97.9792 | 97.1863 | 141:12 | 70:36 | 97.3539 | 96.7674
44 | GOKAK | 10 | 10 | 2:44 | 63:59 | 31:49 | 36:49 | 68:38 | 207:29 | 71:22 | 7:08 | 99.0468 | 99.0088 | 271:28 | 27:09 | 99.05 | 98.757
45 | MUDALAGI | 2 | 2 | 0:10 | 2:00 | 24:00 | 5:35 | 29:35 | 94:45 | 29:45 | 14:52 | 97.9456 | 97.934 | 96:45 | 48:22 | 97.8308 | 97.785
46 | KONNUR | 1 | 1 | 0:10 | 1:25 | 26:55 | 3:05 | 30:00 | 79:01 | 30:10 | 30:10 | 95.8333 | 95.8102 | 80:26 | 80:26 | 96.382 | 96.3172
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 35:15 | 7:20 | 42:35 | 119:40 | 42:35 | 42:35 | 94.0856 | 94.0856 | 119:40 | 119:40 | 94.5208 | 94.5208
48 | KUDACHI | 1 | 1 | 0:00 | 2:35 | 34:50 | 4:25 | 39:15 | 100:30 | 39:15 | 39:15 | 94.5486 | 94.5486 | 103:05 | 103:05 | 95.3984 | 95.2801
49 | ATHANI | 7 | 7 | 18:12 | 118:27 | 180:27 | 148:24 | 328:51 | 851:57 | 347:03 | 49:35 | 93.4752 | 93.1141 | 970:24 | 138:38 | 94.4273 | 93.6525
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 89:28 | 10:18 | 99:46 | 250:40 | 99:46 | 24:56 | 96.5359 | 96.5359 | 250:40 | 62:40 | 97.1306 | 97.1306
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 78:10 | 18:25 | 96:35 | 265:25 | 96:35 | 19:19 | 97.3171 | 97.3171 | 265:25 | 53:05 | 97.5694 | 97.5694
52 | SADALAGA | 1 | 1 | 0:25 | 5:45 | 22:35 | 2:50 | 25:25 | 66:35 | 25:50 | 25:50 | 96.4699 | 96.412 | 72:20 | 72:20 | 96.9513 | 96.688
53 | MUDDEBIHAL | 2 | 2 | 16:15 | 40:50 | 50:15 | 21:25 | 71:40 | 162:01 | 87:55 | 43:58 | 95.0231 | 93.8947 | 202:51 | 101:26 | 96.2908 | 95.356
54 | TALIKOTI | 1 | 1 | 25:20 | 33:20 | 12:10 | 13:00 | 25:10 | 123:20 | 50:30 | 50:30 | 96.5046 | 92.9861 | 156:40 | 156:40 | 94.3529 | 92.8266
55 | B.BAGEWADI | 1 | 1 | 0:59 | 3:37 | 39:05 | 8:49 | 47:54 | 64:40 | 48:53 | 48:53 | 93.3472 | 93.2106 | 68:17 | 68:17 | 97.0391 | 96.8735
56 | INDI | 3 | 3 | 10:49 | 12:23 | 25:32 | 15:37 | 41:09 | 126:17 | 51:58 | 17:19 | 98.0949 | 97.5941 | 138:40 | 46:13 | 98.0726 | 97.8836
57 | SINDAGI | 2 | 2 | 0:00 | 6:50 | 42:55 | 28:25 | 71:20 | 218:00 | 71:20 | 35:40 | 95.0463 | 95.0463 | 224:50 | 112:25 | 95.0092 | 94.8527
58 | GULEDGUDDA | 2 | 2 | 17:40 | 19:35 | 11:27 | 15:30 | 26:57 | 124:22 | 44:37 | 22:19 | 98.1285 | 96.9016 | 143:57 | 71:58 | 97.1528 | 96.7044
59 | ILKAL | 7 | 7 | 2:06 | 30:50 | 101:38 | 156:39 | 258:17 | 702:07 | 260:23 | 37:12 | 94.8753 | 94.8337 | 732:57 | 104:42 | 95.4074 | 95.2057
60 | KERUR | 1 | 1 | 9:30 | 14:02 | 10:55 | 12:36 | 23:31 | 79:04 | 33:01 | 33:01 | 96.7338 | 95.4144 | 93:06 | 93:06 | 96.3797 | 95.7372
61 | HUNGUND | 4 | 4 | 4:05 | 38:13 | 53:58 | 55:04 | 109:02 | 245:57 | 113:07 | 28:17 | 96.2141 | 96.0723 | 284:10 | 71:02 | 97.1846 | 96.7472
62 | BADAMI | 2 | 2 | 4:48 | 11:26 | 23:55 | 19:45 | 43:40 | 135:57 | 48:28 | 24:14 | 96.9676 | 96.6343 | 147:23 | 73:42 | 96.8876 | 96.6258
63 | JAMKHANDI | 6 | 6 | 54:20 | 68:10 | 97:00 | 14:15 | 111:15 | 328:00 | 165:35 | 27:36 | 97.4248 | 96.1671 | 396:10 | 66:02 | 97.4969 | 96.9768
64 | MAHALINGAPUR | 2 | 2 | 1:38 | 4:06 | 105:22 | 16:17 | 121:39 | 200:45 | 123:17 | 61:38 | 91.5521 | 91.4387 | 204:51 | 102:26 | 95.4041 | 95.3102
65 | RABAKAVI | 2 | 2 | 1:30 | 8:10 | 23:40 | 4:00 | 27:40 | 80:05 | 29:10 | 14:35 | 98.0787 | 97.9745 | 88:15 | 44:08 | 98.1666 | 97.9796
66 | BANAHATTI | 2 | 2 | 4:36 | 8:58 | 36:57 | 3:25 | 40:22 | 91:39 | 44:58 | 22:29 | 97.1968 | 96.8773 | 100:37 | 50:18 | 97.9018 | 97.6965
67 | TERDAL | 2 | 2 | 3:35 | 6:25 | 83:55 | 4:05 | 88:00 | 178:25 | 91:35 | 45:47 | 93.8889 | 93.64 | 184:50 | 92:25 | 95.9154 | 95.7685
68 | MUDHOL | 4 | 4 | 19:37 | 36:04 | 61:54 | 9:50 | 71:44 | 217:01 | 91:21 | 22:50 | 97.5093 | 96.8281 | 253:05 | 63:16 | 97.5158 | 97.103
69 | BILAGI | 1 | 1 | 13:50 | 20:20 | 12:30 | 2:10 | 14:40 | 58:05 | 28:30 | 28:30 | 97.963 | 96.0417 | 78:25 | 78:25 | 97.3405 | 96.4095
70 | LOKAPUR | 2 | 2 | 0:20 | 1:40 | 72:15 | 20:25 | 92:40 | 283:30 | 93:00 | 46:30 | 93.5648 | 93.5417 | 285:10 | 142:35 | 93.5096 | 93.4715
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of July-2023
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2023 |  |  |  | Reliability for cumulative period from Apr-23 to July-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 85 | 83 | 90:55 | 339:39 | 443:04 | 401:52 | 844:56 | 2771:24 | 935:51 | 11:01 | 98.6639 | 98.5202 | 3111:03 | 36:36 | 98.8865 | 98.75
2 | DHARWAD (RURAL) | 14 | 13 | 2:16 | 12:52 | 137:46 | 76:00 | 213:46 | 854:52 | 216:02 | 15:26 | 97.9477 | 97.9259 | 867:44 | 61:59 | 97.9146 | 97.8832
3 | KUNDAGOL | 1 | 1 | 28:37 | 111:09 | 3:54 | 1:38 | 5:32 | 34:10 | 34:09 | 34:09 | 99.2563 | 95.4099 | 145:19 | 145:19 | 98.8331 | 95.037
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 4:56 | 12:47 | 17:43 | 74:02 | 17:43 | 17:43 | 97.6187 | 97.6187 | 74:02 | 74:02 | 97.4715 | 97.4715
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 4:25 | 8:05 | 12:30 | 73:53 | 12:30 | 12:30 | 98.3199 | 98.3199 | 73:53 | 73:53 | 97.4767 | 97.4767
6 | KALGHATAGI | 2 | 2 | 0:00 | 7:50 | 11:55 | 32:10 | 44:05 | 128:30 | 44:05 | 22:02 | 97.0374 | 97.0374 | 136:20 | 68:10 | 97.8057 | 97.6719
7 | ALNAVAR | 2 | 2 | 3:30 | 12:35 | 8:30 | 19:00 | 27:30 | 83:55 | 31:00 | 15:30 | 98.1519 | 97.9167 | 96:30 | 48:15 | 98.567 | 98.3521
8 | NARAGUND | 2 | 2 | 7:20 | 27:40 | 15:20 | 19:45 | 35:05 | 198:00 | 42:25 | 21:12 | 97.6422 | 97.1494 | 225:40 | 112:50 | 96.6189 | 96.1464
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 14:00 | 5:15 | 19:15 | 66:35 | 19:15 | 19:15 | 97.4126 | 97.4126 | 66:35 | 66:35 | 97.726 | 97.726
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 36:26 | 20:04 | 56:30 | 219:29 | 56:30 | 18:50 | 97.4686 | 97.4686 | 219:29 | 73:10 | 97.5013 | 97.5013
11 | NAREGAL | 1 | 1 | 2:50 | 8:25 | 2:15 | 2:35 | 4:50 | 28:00 | 7:40 | 7:40 | 99.3504 | 98.9695 | 36:25 | 36:25 | 99.0437 | 98.7563
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 15:45 | 10:45 | 26:30 | 102:35 | 26:30 | 13:15 | 98.2191 | 98.2191 | 102:35 | 51:18 | 98.2482 | 98.2482
13 | RON | 3 | 3 | 0:00 | 0:00 | 22:20 | 4:50 | 27:10 | 167:09 | 27:10 | 9:03 | 98.7829 | 98.7829 | 167:09 | 55:43 | 98.0971 | 98.0971
14 | MUNDARAGI | 1 | 1 | 2:14 | 13:37 | 5:30 | 12:37 | 18:07 | 82:55 | 20:21 | 20:21 | 97.565 | 97.2648 | 96:32 | 96:32 | 97.1681 | 96.7031
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 32:05 | 63:46 | 95:51 | 259:18 | 95:51 | 95:51 | 87.1169 | 87.1169 | 259:18 | 259:18 | 91.1441 | 91.1441
16 | SAVANUR | 2 | 2 | 0:00 | 7:20 | 15:15 | 18:40 | 33:55 | 181:00 | 33:55 | 16:58 | 97.7207 | 97.7207 | 188:20 | 94:10 | 96.9092 | 96.7839
17 | SHIGGAON | 3 | 3 | 9:20 | 55:30 | 20:55 | 12:15 | 33:10 | 120:15 | 42:30 | 14:10 | 98.514 | 98.0959 | 175:45 | 58:35 | 98.631 | 97.9992
18 | BANKAPUR | 1 | 1 | 5:25 | 49:20 | 26:10 | 17:35 | 43:45 | 112:55 | 49:10 | 49:10 | 94.1196 | 93.3916 | 162:15 | 162:15 | 96.1436 | 94.4587
19 | HANGAL | 2 | 2 | 24:35 | 91:25 | 17:40 | 20:30 | 38:10 | 188:10 | 62:45 | 31:22 | 97.435 | 95.7829 | 279:35 | 139:48 | 96.7868 | 95.2257
20 | RANEBENNUR | 10 | 9 | 1:25 | 22:18 | 60:09 | 112:49 | 172:58 | 627:56 | 174:23 | 17:26 | 97.6752 | 97.6561 | 650:14 | 65:01 | 97.8554 | 97.7793
21 | TUMINAKATTI | 1 | 1 | 0:00 | 4:30 | 14:15 | 0:20 | 14:35 | 65:50 | 14:35 | 14:35 | 98.0399 | 98.0399 | 70:20 | 70:20 | 97.7516 | 97.5979
22 | RATTIHALLI | 1 | 1 | 0:00 | 3:50 | 6:50 | 8:50 | 15:40 | 97:50 | 15:40 | 15:40 | 97.8943 | 97.8943 | 101:40 | 101:40 | 96.6587 | 96.5278
23 | HIREKERUR | 1 | 1 | 0:00 | 4:30 | 22:20 | 8:40 | 31:00 | 96:35 | 31:00 | 31:00 | 95.8333 | 95.8333 | 101:05 | 101:05 | 96.7014 | 96.5477
24 | BYADAGI | 5 | 5 | 3:25 | 90:26 | 110:43 | 262:10 | 372:53 | 692:51 | 376:18 | 75:16 | 89.9763 | 89.8844 | 783:17 | 156:39 | 95.2674 | 94.6497
25 | SIRSI | 6 | 6 | 6:56 | 51:06 | 213:20 | 24:29 | 237:49 | 434:54 | 244:45 | 40:48 | 94.6726 | 94.5172 | 486:00 | 81:00 | 97.5245 | 97.2336
26 | YELLAPUR | 1 | 1 | 3:20 | 14:50 | 7:58 | 13:30 | 21:28 | 59:33 | 24:48 | 24:48 | 97.1147 | 96.6667 | 74:23 | 74:23 | 97.9662 | 97.4596
27 | MUNDAGOD | 1 | 1 | 0:26 | 3:08 | 8:07 | 4:20 | 12:27 | 46:47 | 12:53 | 12:53 | 98.3266 | 98.2684 | 49:55 | 49:55 | 98.4022 | 98.2952
28 | SIDDAPUR | 2 | 2 | 1:55 | 8:25 | 12:32 | 7:05 | 19:37 | 76:18 | 21:32 | 10:46 | 98.6817 | 98.5529 | 84:43 | 42:22 | 98.6971 | 98.5533
29 | DANDELI | 8 | 8 | 24:26 | 67:59 | 67:48 | 114:52 | 182:40 | 607:47 | 207:06 | 25:53 | 96.931 | 96.5205 | 675:46 | 84:28 | 97.4053 | 97.1151
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 19:25 | 13:30 | 32:55 | 89:45 | 32:55 | 16:27 | 97.7879 | 97.7879 | 89:45 | 44:52 | 98.4674 | 98.4674
31 | ANKOLA | 2 | 2 | 77:54 | 121:06 | 13:46 | 15:46 | 29:32 | 99:27 | 107:26 | 53:43 | 98.0152 | 92.78 | 220:33 | 110:16 | 98.3017 | 96.2338
32 | KUMTA | 3 | 3 | 1:24 | 11:45 | 56:20 | 95:09 | 151:29 | 264:48 | 152:53 | 50:58 | 93.2131 | 93.1504 | 276:33 | 92:11 | 96.9854 | 96.8517
33 | GOKARNA | 1 | 1 | 62:42 | 142:48 | 5:00 | 3:40 | 8:40 | 28:25 | 71:22 | 71:22 | 98.8351 | 90.4077 | 171:13 | 171:13 | 99.0295 | 94.1524
34 | HONNAVAR | 3 | 3 | 1:24 | 46:36 | 59:29 | 33:31 | 93:00 | 211:16 | 94:24 | 31:28 | 95.8333 | 95.7706 | 257:52 | 85:57 | 97.5949 | 97.0644
35 | BHATKAL | 3 | 3 | 11:15 | 42:27 | 34:21 | 23:24 | 57:45 | 138:47 | 69:00 | 23:00 | 97.4126 | 96.9086 | 181:14 | 60:25 | 98.42 | 97.9368
36 | KHANAPUR | 2 | 2 | 6:45 | 19:45 | 18:00 | 12:55 | 30:55 | 217:35 | 37:40 | 18:50 | 97.9223 | 97.4686 | 237:20 | 118:40 | 96.2844 | 95.9472
37 | BAILHONGAL | 3 | 3 | 0:00 | 8:36 | 27:20 | 13:25 | 40:45 | 202:05 | 40:45 | 13:35 | 98.1743 | 98.1743 | 210:41 | 70:14 | 97.6994 | 97.6015
38 | KITTUR | 1 | 1 | 1:10 | 5:50 | 4:20 | 1:10 | 5:30 | 36:00 | 6:40 | 6:40 | 99.2608 | 99.1039 | 41:50 | 41:50 | 98.7705 | 98.5713
39 | M K HUBLI | 1 | 1 | 0:00 | 1:50 | 22:50 | 10:30 | 33:20 | 95:55 | 33:20 | 33:20 | 95.5197 | 95.5197 | 97:45 | 97:45 | 96.7242 | 96.6615
40 | SOUNDATTI | 3 | 2 | 0:30 | 24:11 | 12:56 | 4:19 | 17:15 | 125:06 | 17:45 | 5:55 | 99.2272 | 99.2047 | 149:17 | 49:46 | 98.5758 | 98.3005
41 | MUNAVALLI | 1 | 1 | 4:45 | 24:20 | 49:35 | 14:05 | 63:40 | 200:35 | 68:25 | 68:25 | 91.4427 | 90.8042 | 224:55 | 224:55 | 93.1495 | 92.3184
42 | YARAGATTI | 1 | 1 | 15:12 | 31:42 | 34:21 | 9:14 | 43:35 | 155:30 | 58:47 | 58:47 | 94.142 | 92.099 | 187:12 | 187:12 | 94.6892 | 93.6066
43 | RAMDURG | 2 | 2 | 27:22 | 52:59 | 25:42 | 4:20 | 30:02 | 145:37 | 57:24 | 28:42 | 97.9816 | 96.1425 | 198:36 | 99:18 | 97.5134 | 96.6086
44 | GOKAK | 10 | 10 | 8:23 | 72:22 | 6:25 | 16:49 | 23:14 | 230:43 | 31:37 | 3:10 | 99.6877 | 99.575 | 303:05 | 30:18 | 99.212 | 98.9649
45 | MUDALAGI | 2 | 2 | 0:00 | 2:00 | 25:05 | 7:00 | 32:05 | 126:50 | 32:05 | 16:02 | 97.8439 | 97.8439 | 128:50 | 64:25 | 97.8341 | 97.8
46 | KONNUR | 1 | 1 | 0:00 | 1:25 | 14:20 | 4:50 | 19:10 | 98:11 | 19:10 | 19:10 | 97.4238 | 97.4238 | 99:36 | 99:36 | 96.6467 | 96.5984
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 26:00 | 4:55 | 30:55 | 150:35 | 30:55 | 30:55 | 95.8445 | 95.8445 | 150:35 | 150:35 | 94.8571 | 94.8571
48 | KUDACHI | 1 | 1 | 0:00 | 2:35 | 42:05 | 7:10 | 49:15 | 149:45 | 49:15 | 49:15 | 93.3804 | 93.3804 | 152:20 | 152:20 | 94.8856 | 94.7974
49 | ATHANI | 7 | 7 | 37:00 | 155:27 | 187:46 | 63:50 | 251:36 | 1103:33 | 288:36 | 41:14 | 95.169 | 94.4585 | 1259:00 | 179:51 | 94.6158 | 93.8573
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 14:45 | 7:30 | 22:15 | 272:55 | 22:15 | 5:34 | 99.2524 | 99.2524 | 272:55 | 68:14 | 97.6698 | 97.6698
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 51:10 | 23:05 | 74:15 | 339:40 | 74:15 | 14:51 | 98.004 | 98.004 | 339:40 | 67:56 | 97.6799 | 97.6799
52 | SADALAGA | 1 | 1 | 0:00 | 5:45 | 24:51 | 6:10 | 31:01 | 97:36 | 31:01 | 31:01 | 95.8311 | 95.8311 | 103:21 | 103:21 | 96.6667 | 96.4703
53 | MUDDEBIHAL | 2 | 2 | 5:05 | 45:55 | 60:05 | 12:55 | 73:00 | 235:01 | 78:05 | 39:02 | 95.0941 | 94.7525 | 280:56 | 140:28 | 95.9867 | 95.2026
54 | TALIKOTI | 1 | 1 | 3:20 | 36:40 | 13:00 | 12:50 | 25:50 | 149:10 | 29:10 | 29:10 | 96.5278 | 96.0797 | 185:50 | 185:50 | 94.9055 | 93.6532
55 | B.BAGEWADI | 1 | 1 | 1:56 | 5:33 | 14:25 | 3:03 | 17:28 | 82:08 | 19:24 | 19:24 | 97.6523 | 97.3925 | 87:41 | 87:41 | 97.1949 | 97.0054
56 | INDI | 3 | 3 | 7:50 | 20:13 | 9:34 | 19:24 | 28:58 | 155:15 | 36:48 | 12:16 | 98.7022 | 98.3513 | 175:28 | 58:29 | 98.2326 | 98.0024
57 | SINDAGI | 2 | 2 | 0:15 | 7:05 | 59:30 | 26:35 | 86:05 | 304:05 | 86:20 | 43:10 | 94.2148 | 94.198 | 311:10 | 155:35 | 94.8073 | 94.6864
58 | GULEDGUDDA | 2 | 2 | 2:01 | 21:36 | 21:26 | 13:59 | 35:25 | 159:47 | 37:26 | 18:43 | 97.6198 | 97.4843 | 181:23 | 90:42 | 97.2715 | 96.9026
59 | ILKAL | 7 | 7 | 16:14 | 47:04 | 89:45 | 123:02 | 212:47 | 914:54 | 229:01 | 32:43 | 95.9143 | 95.6026 | 961:58 | 137:25 | 95.5362 | 95.3066
60 | KERUR | 1 | 1 | 1:40 | 15:42 | 15:51 | 10:59 | 26:50 | 105:54 | 28:30 | 28:30 | 96.3934 | 96.1694 | 121:36 | 121:36 | 96.3832 | 95.847
61 | HUNGUND | 4 | 4 | 12:20 | 50:33 | 34:10 | 61:07 | 95:17 | 341:14 | 107:37 | 26:54 | 96.7983 | 96.3838 | 391:47 | 97:57 | 97.0865 | 96.6549
62 | BADAMI | 2 | 2 | 1:54 | 13:20 | 8:03 | 21:09 | 29:12 | 165:09 | 31:06 | 15:33 | 98.0376 | 97.9099 | 178:29 | 89:14 | 97.1798 | 96.9521
63 | JAMKHANDI | 6 | 6 | 54:20 | 122:30 | 97:00 | 14:15 | 111:15 | 439:15 | 165:35 | 27:36 | 97.5078 | 96.2907 | 561:45 | 93:38 | 97.4997 | 96.8024
64 | MAHALINGAPUR | 2 | 2 | 1:38 | 5:44 | 105:22 | 16:17 | 121:39 | 322:24 | 123:17 | 61:38 | 91.8246 | 91.7148 | 328:08 | 164:04 | 94.4945 | 94.3966
65 | RABAKAVI | 2 | 2 | 1:30 | 9:40 | 23:40 | 4:00 | 27:40 | 107:45 | 29:10 | 14:35 | 98.1407 | 98.0399 | 117:25 | 58:43 | 98.16 | 97.9949
66 | BANAHATTI | 2 | 2 | 4:36 | 13:34 | 36:57 | 3:25 | 40:22 | 132:01 | 44:58 | 22:29 | 97.2872 | 96.978 | 145:35 | 72:47 | 97.7456 | 97.5139
67 | TERDAL | 2 | 2 | 3:35 | 10:00 | 83:55 | 4:05 | 88:00 | 266:25 | 91:35 | 45:47 | 94.086 | 93.8452 | 276:25 | 138:12 | 95.4505 | 95.2798
68 | MUDHOL | 4 | 4 | 17:20 | 53:24 | 46:43 | 15:55 | 62:38 | 279:39 | 79:58 | 20:00 | 97.8954 | 97.3129 | 333:03 | 83:16 | 97.6123 | 97.1563
69 | BILAGI | 1 | 1 | 0:55 | 21:15 | 14:45 | 4:35 | 19:20 | 77:25 | 20:15 | 20:15 | 97.4014 | 97.2782 | 98:40 | 98:40 | 97.356 | 96.6302
70 | LOKAPUR | 2 | 2 | 0:46 | 2:26 | 48:11 | 34:02 | 82:13 | 365:43 | 82:59 | 41:30 | 94.4747 | 94.4232 | 368:09 | 184:04 | 93.7548 | 93.7133
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of Aug-2023
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Aug-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Aug-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 83 | 83 | 75:43 | 415:22 | 297:57 | 197:15 | 495:12 | 3266:36 | 570:55 | 6:53 | 99.1981 | 99.0755 | 3681:58 | 44:22 | 98.9282 | 98.7919
2 | DHARWAD (RURAL) | 13 | 13 | 1:11 | 14:03 | 195:31 | 151:12 | 346:43 | 1201:35 | 347:54 | 26:46 | 96.4153 | 96.403 | 1215:38 | 93:31 | 97.4829 | 97.4534
3 | KUNDAGOL | 1 | 1 | 9:01 | 120:10 | 8:14 | 1:46 | 10:00 | 44:10 | 19:01 | 19:01 | 98.6559 | 97.444 | 164:20 | 164:20 | 98.7972 | 95.5247
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 7:05 | 7:57 | 15:02 | 89:04 | 15:02 | 15:02 | 97.9794 | 97.9794 | 89:04 | 89:04 | 97.5744 | 97.5744
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 6:30 | 5:20 | 11:50 | 85:43 | 11:50 | 11:50 | 98.4095 | 98.4095 | 85:43 | 85:43 | 97.6657 | 97.6657
6 | KALGHATAGI | 2 | 2 | 0:00 | 7:50 | 34:40 | 11:00 | 45:40 | 174:10 | 45:40 | 22:50 | 96.931 | 96.931 | 182:00 | 91:00 | 97.6284 | 97.5218
7 | ALNAVAR | 2 | 2 | 9:05 | 21:40 | 11:25 | 5:45 | 17:10 | 101:05 | 26:15 | 13:08 | 98.8463 | 98.2359 | 122:45 | 61:22 | 98.6236 | 98.3286
8 | NARAGUND | 2 | 2 | 20:40 | 48:20 | 13:20 | 15:25 | 28:45 | 226:45 | 49:25 | 24:42 | 98.0679 | 96.679 | 275:05 | 137:33 | 96.9124 | 96.2543
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 2:49 | 66:47 | 69:36 | 136:11 | 69:36 | 69:36 | 90.6452 | 90.6452 | 136:11 | 136:11 | 96.2913 | 96.2913
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 36:26 | 13:02 | 49:28 | 268:57 | 49:28 | 16:29 | 97.7838 | 97.7838 | 268:57 | 89:39 | 97.5586 | 97.5586
11 | NAREGAL | 1 | 1 | 1:05 | 9:30 | 3:10 | 1:40 | 4:50 | 32:50 | 5:55 | 5:55 | 99.3504 | 99.2047 | 42:20 | 42:20 | 99.1058 | 98.8471
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 13:20 | 6:15 | 19:35 | 122:10 | 19:35 | 9:48 | 98.6839 | 98.6839 | 122:10 | 61:05 | 98.3365 | 98.3365
13 | RON | 3 | 3 | 0:00 | 0:00 | 30:24 | 8:08 | 38:32 | 205:41 | 38:32 | 12:51 | 98.2736 | 98.2736 | 205:41 | 68:34 | 98.1329 | 98.1329
14 | MUNDARAGI | 1 | 1 | 2:40 | 16:17 | 11:15 | 12:05 | 23:20 | 106:15 | 26:00 | 26:00 | 96.8638 | 96.5054 | 122:32 | 122:32 | 97.1065 | 96.663
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 31:04 | 22:30 | 53:34 | 312:52 | 53:34 | 53:34 | 92.8002 | 92.8002 | 312:52 | 312:52 | 91.4797 | 91.4797
16 | SAVANUR | 2 | 2 | 0:50 | 8:10 | 10:45 | 3:20 | 14:05 | 195:05 | 14:55 | 7:28 | 99.0535 | 98.9975 | 203:15 | 101:38 | 97.3436 | 97.2324
17 | SHIGGAON | 3 | 3 | 4:25 | 59:55 | 10:00 | 7:45 | 17:45 | 138:00 | 22:10 | 7:23 | 99.2047 | 99.0069 | 197:55 | 65:58 | 98.7473 | 98.2034
18 | BANKAPUR | 1 | 1 | 9:50 | 59:10 | 14:30 | 4:20 | 18:50 | 131:45 | 28:40 | 28:40 | 97.4686 | 96.147 | 190:55 | 190:55 | 96.412 | 94.8007
19 | HANGAL | 2 | 2 | 12:45 | 104:10 | 15:45 | 5:55 | 21:40 | 209:50 | 34:25 | 17:12 | 98.5439 | 97.6871 | 314:00 | 157:00 | 97.1428 | 95.7244
20 | RANEBENNUR | 10 | 10 | 12:48 | 35:06 | 230:44 | 137:08 | 367:52 | 995:48 | 380:40 | 38:04 | 95.0556 | 94.8835 | 1030:54 | 103:05 | 97.2881 | 97.1925
21 | TUMINAKATTI | 1 | 1 | 5:35 | 10:05 | 11:25 | 0:15 | 11:40 | 77:30 | 17:15 | 17:15 | 98.4319 | 97.6815 | 87:35 | 87:35 | 97.8894 | 97.6148
22 | RATTIHALLI | 1 | 1 | 5:55 | 9:45 | 9:35 | 9:00 | 18:35 | 116:25 | 24:30 | 24:30 | 97.5022 | 96.707 | 126:10 | 126:10 | 96.8296 | 96.5641
23 | HIREKERUR | 1 | 1 | 6:15 | 10:45 | 16:35 | 10:30 | 27:05 | 123:40 | 33:20 | 33:20 | 96.3598 | 95.5197 | 134:25 | 134:25 | 96.6322 | 96.3394
24 | BYADAGI | 5 | 5 | 27:41 | 118:07 | 111:35 | 72:30 | 184:05 | 876:56 | 211:46 | 42:21 | 95.0515 | 94.3073 | 995:03 | 199:01 | 95.2237 | 94.5803
25 | SIRSI | 6 | 6 | 29:11 | 80:17 | 60:39 | 9:49 | 70:28 | 505:22 | 99:39 | 16:36 | 98.4214 | 97.7677 | 585:39 | 97:36 | 97.7062 | 97.3418
26 | YELLAPUR | 1 | 1 | 6:55 | 21:45 | 12:10 | 7:15 | 19:25 | 78:58 | 26:20 | 26:20 | 97.3902 | 96.4606 | 100:43 | 100:43 | 97.8495 | 97.2572
27 | MUNDAGOD | 1 | 1 | 0:00 | 3:08 | 11:05 | 4:20 | 15:25 | 62:12 | 15:25 | 15:25 | 97.9279 | 97.9279 | 65:20 | 65:20 | 98.3061 | 98.2208
28 | SIDDAPUR | 2 | 2 | 1:35 | 10:00 | 10:05 | 4:35 | 14:40 | 90:58 | 16:15 | 8:08 | 99.0143 | 98.9079 | 100:58 | 50:29 | 98.7613 | 98.6252
29 | DANDELI | 8 | 8 | 21:36 | 89:35 | 43:02 | 55:03 | 98:05 | 705:52 | 119:41 | 14:58 | 98.3521 | 97.9892 | 795:27 | 99:26 | 97.5971 | 97.2922
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 12:15 | 3:45 | 16:00 | 105:45 | 16:00 | 8:00 | 98.9247 | 98.9247 | 105:45 | 52:52 | 98.56 | 98.56
31 | ANKOLA | 2 | 2 | 4:12 | 125:18 | 18:27 | 18:27 | 36:54 | 136:21 | 41:06 | 20:33 | 97.5202 | 97.2379 | 261:39 | 130:50 | 98.1434 | 96.4372
32 | KUMTA | 3 | 3 | 0:18 | 12:03 | 26:21 | 8:37 | 34:58 | 299:46 | 35:16 | 11:45 | 98.4334 | 98.42 | 311:49 | 103:56 | 97.2788 | 97.1694
33 | GOKARNA | 1 | 1 | 12:32 | 155:20 | 0:45 | 0:35 | 1:20 | 29:45 | 13:52 | 13:52 | 99.8208 | 98.1362 | 185:05 | 185:05 | 99.1898 | 94.9596
34 | HONNAVAR | 3 | 3 | 0:33 | 47:09 | 26:00 | 9:42 | 35:42 | 246:58 | 36:15 | 12:05 | 98.4005 | 98.3759 | 294:07 | 98:02 | 97.7581 | 97.3301
35 | BHATKAL | 3 | 3 | 8:33 | 51:00 | 17:52 | 2:33 | 20:25 | 159:12 | 28:58 | 9:39 | 99.0853 | 98.7022 | 210:12 | 70:04 | 98.5548 | 98.0919
36 | KHANAPUR | 2 | 2 | 16:35 | 36:20 | 45:25 | 9:15 | 54:40 | 272:15 | 71:15 | 35:38 | 96.3262 | 95.2117 | 308:35 | 154:18 | 96.2929 | 95.7982
37 | BAILHONGAL | 3 | 3 | 0:00 | 8:36 | 44:15 | 10:10 | 54:25 | 256:30 | 54:25 | 18:08 | 97.562 | 97.562 | 265:06 | 88:22 | 97.6716 | 97.5935
38 | KITTUR | 3 | 3 | 0:45 | 6:35 | 16:35 | 170:05 | 186:40 | 222:40 | 187:25 | 62:28 | 91.6368 | 91.6032 | 229:15 | 76:25 | 97.9787 | 97.9189
39 | M K HUBLI | 1 | 1 | 0:00 | 1:50 | 24:55 | 10:40 | 35:35 | 131:30 | 35:35 | 35:35 | 95.2173 | 95.2173 | 133:20 | 133:20 | 96.4188 | 96.3689
40 | SOUNDATTI | 3 | 3 | 7:05 | 31:16 | 6:57 | 24:45 | 31:42 | 156:48 | 38:47 | 12:56 | 98.5797 | 98.2624 | 188:04 | 62:41 | 98.5766 | 98.2928
41 | MUNAVALLI | 1 | 1 | 12:05 | 36:25 | 39:10 | 11:40 | 50:50 | 251:25 | 62:55 | 62:55 | 93.1676 | 91.5435 | 287:50 | 287:50 | 93.1531 | 92.1614
42 | YARAGATTI | 1 | 1 | 2:23 | 34:05 | 35:04 | 21:20 | 56:24 | 211:54 | 58:47 | 58:47 | 92.4194 | 92.099 | 245:59 | 245:59 | 94.2293 | 93.3011
43 | RAMDURG | 2 | 2 | 1:00 | 53:59 | 16:25 | 4:15 | 20:40 | 166:17 | 21:40 | 10:50 | 98.6111 | 98.5439 | 220:16 | 110:08 | 97.7358 | 97.0007
44 | GOKAK | 10 | 10 | 1:32 | 73:54 | 23:58 | 10:03 | 34:01 | 264:44 | 35:33 | 3:33 | 99.5428 | 99.5222 | 338:38 | 33:52 | 99.279 | 99.0778
45 | MUDALAGI | 2 | 2 | 2:20 | 4:20 | 32:10 | 4:30 | 36:40 | 163:30 | 39:00 | 19:30 | 97.5358 | 97.379 | 167:50 | 83:55 | 97.7737 | 97.7147
46 | KONNUR | 1 | 1 | 0:58 | 2:23 | 19:35 | 3:40 | 23:15 | 121:26 | 24:13 | 24:13 | 96.875 | 96.7451 | 123:49 | 123:49 | 96.693 | 96.6281
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 27:20 | 5:25 | 32:45 | 183:20 | 32:45 | 32:45 | 95.5981 | 95.5981 | 183:20 | 183:20 | 95.0073 | 95.0073
48 | KUDACHI | 1 | 1 | 0:00 | 2:35 | 23:10 | 2:10 | 25:20 | 175:05 | 25:20 | 25:20 | 96.595 | 96.595 | 177:40 | 177:40 | 95.2319 | 95.1616
49 | ATHANI | 7 | 7 | 42:06 | 197:33 | 160:30 | 61:21 | 221:51 | 1325:24 | 263:57 | 37:42 | 95.7402 | 94.9318 | 1522:57 | 217:34 | 94.8436 | 94.075
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 156:28 | 5:42 | 162:10 | 435:05 | 162:10 | 40:32 | 94.5509 | 94.5509 | 435:05 | 108:46 | 97.0378 | 97.0378
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 55:00 | 12:20 | 67:20 | 407:00 | 67:20 | 13:28 | 98.19 | 98.19 | 407:00 | 81:24 | 97.7832 | 97.7832
52 | SADALAGA | 1 | 1 | 7:30 | 13:15 | 9:45 | 5:00 | 14:45 | 112:21 | 22:15 | 22:15 | 98.0175 | 97.0094 | 125:36 | 125:36 | 96.9404 | 96.5795
53 | MUDDEBIHAL | 2 | 2 | 50:40 | 96:35 | 40:25 | 3:50 | 44:15 | 279:16 | 94:55 | 47:28 | 97.0262 | 93.6212 | 375:51 | 187:56 | 96.1973 | 94.8822
54 | TALIKOTI | 1 | 1 | 16:55 | 53:35 | 6:15 | 19:25 | 25:40 | 174:50 | 42:35 | 42:35 | 96.5502 | 94.2764 | 228:25 | 228:25 | 95.2387 | 93.7795
55 | B.BAGEWADI | 1 | 1 | 5:19 | 10:52 | 6:56 | 6:37 | 13:33 | 95:41 | 18:52 | 18:52 | 98.1788 | 97.4642 | 106:33 | 106:33 | 97.3942 | 97.0983
56 | INDI | 3 | 3 | 0:50 | 21:03 | 13:51 | 5:09 | 19:00 | 174:15 | 19:50 | 6:37 | 99.1487 | 99.1114 | 195:18 | 65:06 | 98.4182 | 98.2271
57 | SINDAGI | 2 | 2 | 0:00 | 7:05 | 35:00 | 8:30 | 43:30 | 347:35 | 43:30 | 21:45 | 97.0766 | 97.0766 | 354:40 | 177:20 | 95.2671 | 95.1707
58 | GULEDGUDDA | 2 | 2 | 1:14 | 22:50 | 12:00 | 20:30 | 32:30 | 192:17 | 33:44 | 16:52 | 97.8159 | 97.733 | 215:07 | 107:34 | 97.3818 | 97.0709
59 | ILKAL | 7 | 7 | 0:00 | 47:04 | 53:43 | 45:05 | 98:48 | 1013:42 | 98:48 | 14:07 | 98.1029 | 98.1029 | 1060:46 | 151:32 | 96.0563 | 95.8731
60 | KERUR | 1 | 1 | 0:00 | 15:42 | 8:35 | 4:45 | 13:20 | 119:14 | 13:20 | 13:20 | 98.2079 | 98.2079 | 134:56 | 134:56 | 96.7529 | 96.3253
61 | HUNGUND | 4 | 4 | 2:08 | 52:41 | 30:45 | 31:29 | 62:14 | 403:28 | 64:22 | 16:06 | 97.9088 | 97.8371 | 456:09 | 114:02 | 97.2531 | 96.8944
62 | BADAMI | 2 | 2 | 2:10 | 15:30 | 12:15 | 10:12 | 22:27 | 187:36 | 24:37 | 12:18 | 98.4913 | 98.3457 | 203:06 | 101:33 | 97.4455 | 97.2345
63 | JAMKHANDI | 6 | 6 | 43:15 | 165:45 | 51:15 | 5:30 | 56:45 | 496:00 | 100:00 | 16:40 | 98.7287 | 97.7599 | 661:45 | 110:17 | 97.7487 | 96.9964
64 | MAHALINGAPUR | 2 | 2 | 4:13 | 9:57 | 29:35 | 6:42 | 36:17 | 358:41 | 40:30 | 20:15 | 97.5616 | 97.2782 | 368:38 | 184:19 | 95.116 | 94.9805
65 | RABAKAVI | 2 | 2 | 8:25 | 18:05 | 7:55 | 0:55 | 8:50 | 116:35 | 17:15 | 8:38 | 99.4064 | 98.8407 | 134:40 | 67:20 | 98.4125 | 98.1663
66 | BANAHATTI | 2 | 2 | 13:23 | 26:57 | 24:40 | 1:35 | 26:15 | 158:16 | 39:38 | 19:49 | 98.2359 | 97.3365 | 185:13 | 92:36 | 97.845 | 97.478
67 | TERDAL | 2 | 2 | 11:40 | 21:40 | 29:50 | 4:40 | 34:30 | 300:55 | 46:10 | 23:05 | 97.6815 | 96.8974 | 322:35 | 161:18 | 95.9026 | 95.6075
68 | MUDHOL | 4 | 4 | 19:44 | 73:08 | 49:47 | 9:25 | 59:12 | 338:51 | 78:56 | 19:44 | 98.0108 | 97.3477 | 411:59 | 103:00 | 97.693 | 97.1951
69 | BILAGI | 1 | 1 | 13:08 | 34:23 | 8:00 | 0:30 | 8:30 | 85:55 | 21:38 | 21:38 | 98.8575 | 97.0923 | 120:18 | 120:18 | 97.6602 | 96.7239
70 | LOKAPUR | 2 | 2 | 0:30 | 2:56 | 70:34 | 11:10 | 81:44 | 447:27 | 82:14 | 41:07 | 94.5072 | 94.4736 | 450:23 | 225:11 | 93.9073 | 93.8673
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of SEPTEMBER-2023
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Sept-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Sept-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 82 | 82 | 21:51 | 437:13 | 307:04 | 252:24 | 559:28 | 3826:04 | 581:19 | 7:05 | 99.0524 | 99.0154 | 4263:17 | 51:59 | 98.9376 | 98.8162
2 | DHARWAD (RURAL) | 14 | 13 | 0:58 | 15:01 | 132:17 | 33:51 | 166:08 | 1367:43 | 167:06 | 11:56 | 98.3519 | 98.3423 | 1382:44 | 98:46 | 97.7756 | 97.7512
3 | KUNDAGOL | 1 | 1 | 2:49 | 122:59 | 3:20 | 2:02 | 5:22 | 49:32 | 8:11 | 8:11 | 99.2546 | 98.8634 | 172:31 | 172:31 | 98.8722 | 96.072
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 2:43 | 3:58 | 6:41 | 95:45 | 6:41 | 6:41 | 99.0718 | 99.0718 | 95:45 | 95:45 | 97.8199 | 97.8199
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 9:10 | 1:15 | 10:25 | 96:08 | 10:25 | 10:25 | 98.5532 | 98.5532 | 96:08 | 96:08 | 97.8112 | 97.8112
6 | KALGHATAGI | 2 | 2 | 0:00 | 7:50 | 12:05 | 5:15 | 17:20 | 191:30 | 17:20 | 8:40 | 98.7963 | 98.7963 | 199:20 | 99:40 | 97.8199 | 97.7307
7 | ALNAVAR | 2 | 2 | 2:20 | 24:00 | 7:35 | 10:10 | 17:45 | 118:50 | 20:05 | 10:02 | 98.7674 | 98.6053 | 142:50 | 71:25 | 98.6472 | 98.3739
8 | NARAGUND | 2 | 2 | 0:00 | 48:20 | 23:45 | 27:50 | 51:35 | 278:20 | 51:35 | 25:48 | 96.4178 | 96.4178 | 326:40 | 163:20 | 96.8314 | 96.2811
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 17:18 | 17:49 | 35:07 | 171:18 | 35:07 | 35:07 | 95.1227 | 95.1227 | 171:18 | 171:18 | 96.0997 | 96.0997
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 58:20 | 23:12 | 81:32 | 350:29 | 81:32 | 27:11 | 96.2253 | 96.2253 | 350:29 | 116:50 | 97.34 | 97.34
11 | NAREGAL | 1 | 1 | 0:55 | 10:25 | 10:15 | 0:55 | 11:10 | 44:00 | 12:05 | 12:05 | 98.4491 | 98.3218 | 54:25 | 54:25 | 98.9982 | 98.761
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 27:45 | 9:00 | 36:45 | 158:55 | 36:45 | 18:22 | 97.4479 | 97.4479 | 158:55 | 79:28 | 98.1908 | 98.1908
13 | RON | 3 | 3 | 0:00 | 0:00 | 44:00 | 7:08 | 51:08 | 256:49 | 51:08 | 17:03 | 97.6327 | 97.6327 | 256:49 | 85:36 | 98.0509 | 98.0509
14 | MUNDARAGI | 1 | 1 | 8:15 | 24:32 | 14:00 | 5:00 | 19:00 | 125:15 | 27:15 | 27:15 | 97.3611 | 96.2153 | 149:47 | 149:47 | 97.1482 | 96.5896
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 24:55 | 9:43 | 34:38 | 347:30 | 34:38 | 34:38 | 95.1898 | 95.1898 | 347:30 | 347:30 | 92.0879 | 92.0879
16 | SAVANUR | 2 | 2 | 1:10 | 9:20 | 37:10 | 2:20 | 39:30 | 234:35 | 40:40 | 20:20 | 97.2569 | 97.1759 | 243:55 | 121:58 | 97.3294 | 97.2232
17 | SHIGGAON | 3 | 3 | 28:05 | 88:00 | 9:45 | 9:35 | 19:20 | 157:20 | 47:25 | 15:48 | 99.1049 | 97.8048 | 245:20 | 81:47 | 98.8059 | 98.138
18 | BANKAPUR | 1 | 1 | 8:20 | 67:30 | 7:35 | 3:20 | 10:55 | 142:40 | 19:15 | 19:15 | 98.4838 | 97.3264 | 210:10 | 210:10 | 96.7517 | 95.2148
19 | HANGAL | 2 | 2 | 31:20 | 135:30 | 18:05 | 11:45 | 29:50 | 239:40 | 61:10 | 30:35 | 97.9282 | 95.7523 | 375:10 | 187:35 | 97.2716 | 95.729
20 | RANEBENNUR | 10 | 10 | 2:50 | 37:56 | 135:12 | 22:58 | 158:10 | 1153:58 | 161:00 | 16:06 | 97.8032 | 97.7639 | 1191:54 | 119:11 | 97.3726 | 97.2862
21 | TUMINAKATTI | 1 | 1 | 0:30 | 10:35 | 18:25 | 0:25 | 18:50 | 96:20 | 19:20 | 19:20 | 97.3843 | 97.3148 | 106:55 | 106:55 | 97.8066 | 97.5656
22 | RATTIHALLI | 1 | 1 | 0:45 | 10:30 | 17:25 | 6:15 | 23:40 | 140:05 | 24:25 | 24:25 | 96.713 | 96.6088 | 150:35 | 150:35 | 96.8105 | 96.5714
23 | HIREKERUR | 1 | 1 | 0:10 | 10:55 | 10:20 | 7:40 | 18:00 | 141:40 | 18:10 | 18:10 | 97.5 | 97.4769 | 152:35 | 152:35 | 96.7744 | 96.5259
24 | BYADAGI | 5 | 5 | 21:25 | 139:32 | 59:55 | 18:55 | 78:50 | 955:46 | 100:15 | 20:03 | 97.8102 | 97.2153 | 1095:18 | 219:04 | 95.6477 | 95.0123
25 | SIRSI | 6 | 6 | 22:37 | 102:54 | 52:44 | 13:44 | 66:28 | 571:50 | 89:05 | 14:51 | 98.4614 | 97.9379 | 674:44 | 112:27 | 97.83 | 97.4395
26 | YELLAPUR | 1 | 1 | 3:15 | 25:00 | 2:35 | 8:05 | 10:40 | 89:38 | 13:55 | 13:55 | 98.5185 | 98.0671 | 114:38 | 114:38 | 97.9592 | 97.39
27 | MUNDAGOD | 1 | 1 | 0:10 | 3:18 | 20:05 | 1:20 | 21:25 | 83:37 | 21:35 | 21:35 | 97.0255 | 97.0023 | 86:55 | 86:55 | 98.0962 | 98.021
28 | SIDDAPUR | 2 | 2 | 1:10 | 11:10 | 23:01 | 6:48 | 29:49 | 120:47 | 30:59 | 15:30 | 97.9294 | 97.8484 | 131:57 | 65:58 | 98.625 | 98.4978
29 | DANDELI | 8 | 8 | 361:48 | 451:23 | 237:41 | 22:01 | 259:42 | 965:34 | 621:30 | 77:41 | 95.4913 | 89.2101 | 1416:57 | 177:07 | 97.2519 | 95.9672
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 10:25 | 3:45 | 14:10 | 119:55 | 14:10 | 7:05 | 99.0162 | 99.0162 | 119:55 | 59:58 | 98.6348 | 98.6348
31 | ANKOLA | 2 | 2 | 16:10 | 141:28 | 8:31 | 8:31 | 17:02 | 153:23 | 33:12 | 16:36 | 98.8171 | 97.6944 | 294:51 | 147:26 | 98.2538 | 96.6433
32 | KUMTA | 3 | 3 | 0:51 | 12:54 | 31:49 | 30:22 | 62:11 | 361:57 | 63:02 | 21:01 | 97.1211 | 97.0818 | 374:51 | 124:57 | 97.253 | 97.1551
33 | GOKARNA | 1 | 1 | 53:27 | 208:47 | 1:35 | 0:20 | 1:55 | 31:40 | 55:22 | 55:22 | 99.7338 | 92.3102 | 240:27 | 240:27 | 99.279 | 94.5253
34 | HONNAVAR | 3 | 3 | 1:21 | 48:30 | 39:05 | 13:13 | 52:18 | 299:16 | 53:39 | 17:53 | 97.5787 | 97.5162 | 347:46 | 115:55 | 97.7287 | 97.3606
35 | BHATKAL | 3 | 3 | 13:54 | 64:54 | 24:56 | 5:38 | 30:34 | 189:46 | 44:28 | 14:49 | 98.5849 | 97.9414 | 254:40 | 84:53 | 98.5598 | 98.0672
36 | KHANAPUR | 2 | 2 | 4:00 | 40:20 | 9:30 | 6:25 | 15:55 | 288:10 | 19:55 | 9:58 | 98.8947 | 98.6169 | 328:30 | 164:15 | 96.7194 | 96.2602
37 | BAILHONGAL | 3 | 3 | 0:00 | 8:36 | 49:50 | 24:20 | 74:10 | 330:40 | 74:10 | 24:43 | 96.5664 | 96.5664 | 339:16 | 113:05 | 97.4904 | 97.4251
38 | KITTUR | 3 | 3 | 6:10 | 12:45 | 14:55 | 98:10 | 113:05 | 335:45 | 119:15 | 39:45 | 94.7647 | 94.4792 | 348:30 | 116:10 | 97.4518 | 97.355
39 | M K HUBLI | 1 | 1 | 0:00 | 1:50 | 22:05 | 8:00 | 30:05 | 161:35 | 30:05 | 30:05 | 95.8218 | 95.8218 | 163:25 | 163:25 | 96.321 | 96.2792
40 | SOUNDATTI | 3 | 3 | 3:02 | 34:18 | 7:46 | 6:04 | 13:50 | 170:38 | 16:52 | 5:37 | 99.3596 | 99.2191 | 204:56 | 68:19 | 98.705 | 98.4446
41 | MUNAVALLI | 1 | 1 | 10:55 | 47:20 | 16:45 | 3:20 | 20:05 | 271:30 | 31:00 | 31:00 | 97.2106 | 95.6944 | 318:50 | 318:50 | 93.8183 | 92.7406
42 | YARAGATTI | 1 | 1 | 0:00 | 34:05 | 29:59 | 3:03 | 33:02 | 244:56 | 33:02 | 33:02 | 95.412 | 95.412 | 279:01 | 279:01 | 94.4232 | 93.6472
43 | RAMDURG | 2 | 2 | 5:24 | 59:23 | 15:35 | 5:05 | 20:40 | 186:57 | 26:04 | 13:02 | 98.5648 | 98.1898 | 246:20 | 123:10 | 97.8717 | 97.1957
44 | GOKAK | 10 | 10 | 12:40 | 86:34 | 41:57 | 8:57 | 50:54 | 315:38 | 63:34 | 6:21 | 99.2931 | 99.1171 | 402:12 | 40:13 | 99.2813 | 99.0842
45 | MUDALAGI | 2 | 2 | 0:00 | 4:20 | 16:05 | 1:45 | 17:50 | 181:20 | 17:50 | 8:55 | 98.7616 | 98.7616 | 185:40 | 92:50 | 97.9356 | 97.8863
46 | KONNUR | 1 | 1 | 0:00 | 2:23 | 9:40 | 1:30 | 11:10 | 132:36 | 11:10 | 11:10 | 98.4491 | 98.4491 | 134:59 | 134:59 | 96.9809 | 96.9266
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 27:20 | 5:57 | 33:17 | 216:37 | 33:17 | 33:17 | 95.3773 | 95.3773 | 216:37 | 216:37 | 95.0679 | 95.0679
48 | KUDACHI | 1 | 1 | 0:00 | 2:35 | 36:50 | 2:00 | 38:50 | 213:55 | 38:50 | 38:50 | 94.6065 | 94.6065 | 216:30 | 216:30 | 95.1294 | 95.0706
49 | ATHANI | 7 | 7 | 43:12 | 240:45 | 164:47 | 75:45 | 240:32 | 1565:56 | 283:44 | 40:32 | 95.2275 | 94.3704 | 1806:41 | 258:06 | 94.9065 | 94.1235
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 66:02 | 10:59 | 77:01 | 512:06 | 77:01 | 19:15 | 97.3258 | 97.3258 | 512:06 | 128:01 | 97.085 | 97.085
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 86:30 | 20:25 | 106:55 | 513:55 | 106:55 | 21:23 | 97.0301 | 97.0301 | 513:55 | 102:47 | 97.6598 | 97.6598
52 | SADALAGA | 1 | 1 | 0:00 | 13:15 | 19:20 | 1:45 | 21:05 | 133:26 | 21:05 | 21:05 | 97.0718 | 97.0718 | 146:41 | 146:41 | 96.9619 | 96.6602
53 | MUDDEBIHAL | 2 | 2 | 0:00 | 96:35 | 22:37 | 7:45 | 30:22 | 309:38 | 30:22 | 15:11 | 97.8912 | 97.8912 | 406:13 | 203:06 | 96.475 | 95.3755
54 | TALIKOTI | 1 | 1 | 20:05 | 73:40 | 12:05 | 15:25 | 27:30 | 202:20 | 47:35 | 47:35 | 96.1806 | 93.3912 | 276:00 | 276:00 | 95.3931 | 93.7158
55 | B.BAGEWADI | 2 | 2 | 1:07 | 11:59 | 16:48 | 2:33 | 19:21 | 115:02 | 20:28 | 10:14 | 98.6562 | 98.5787 | 127:01 | 63:31 | 98.6904 | 98.554
56 | INDI | 3 | 3 | 33:05 | 54:08 | 21:57 | 14:40 | 36:37 | 210:52 | 69:42 | 23:14 | 98.3048 | 96.7731 | 265:00 | 88:20 | 98.3996 | 97.9888
57 | SINDAGI | 2 | 2 | 20:50 | 27:55 | 36:15 | 0:00 | 36:15 | 383:50 | 57:05 | 28:32 | 97.4826 | 96.0359 | 411:45 | 205:52 | 95.6303 | 95.3125
58 | GULEDGUDDA | 2 | 2 | 26:16 | 49:06 | 11:08 | 10:24 | 21:32 | 213:49 | 47:48 | 23:54 | 98.5046 | 96.6806 | 262:55 | 131:28 | 97.5658 | 97.0069
59 | ILKAL | 7 | 7 | 0:00 | 47:04 | 118:37 | 79:33 | 198:10 | 1211:52 | 198:10 | 28:19 | 96.0681 | 96.0681 | 1258:56 | 179:51 | 96.0582 | 95.9051
60 | KERUR | 1 | 1 | 0:00 | 15:42 | 13:54 | 6:13 | 20:07 | 139:21 | 20:07 | 20:07 | 97.206 | 97.206 | 155:03 | 155:03 | 96.8272 | 96.4697
61 | HUNGUND | 4 | 4 | 1:20 | 54:01 | 67:30 | 57:43 | 125:13 | 528:41 | 126:33 | 31:38 | 95.6522 | 95.6059 | 582:42 | 145:40 | 96.9906 | 96.6832
62 | BADAMI | 2 | 2 | 0:56 | 16:26 | 12:41 | 14:05 | 26:46 | 214:22 | 27:42 | 13:51 | 98.1412 | 98.0764 | 230:48 | 115:24 | 97.5596 | 97.3725
63 | JAMKHANDI | 6 | 6 | 7:30 | 173:15 | 42:10 | 22:15 | 64:25 | 560:25 | 71:55 | 11:59 | 98.5089 | 98.3353 | 733:40 | 122:17 | 97.8733 | 97.2159
64 | MAHALINGAPUR | 2 | 2 | 1:50 | 11:47 | 36:13 | 8:30 | 44:43 | 403:24 | 46:33 | 23:16 | 96.8947 | 96.7674 | 415:11 | 207:36 | 95.4076 | 95.2734
65 | RABAKAVI | 2 | 2 | 3:45 | 21:50 | 9:05 | 3:35 | 12:40 | 129:15 | 16:25 | 8:12 | 99.1204 | 98.86 | 151:05 | 75:32 | 98.5286 | 98.28
66 | BANAHATTI | 2 | 2 | 1:10 | 28:07 | 9:55 | 1:05 | 11:00 | 169:16 | 12:10 | 6:05 | 99.2361 | 99.1551 | 197:23 | 98:41 | 98.073 | 97.7529
67 | TERDAL | 2 | 2 | 2:00 | 23:40 | 25:00 | 5:45 | 30:45 | 331:40 | 32:45 | 16:22 | 97.8646 | 97.7257 | 355:20 | 177:40 | 96.2242 | 95.9548
68 | MUDHOL | 4 | 4 | 6:37 | 79:45 | 93:45 | 21:30 | 115:15 | 454:06 | 121:52 | 30:28 | 95.9983 | 95.7685 | 533:51 | 133:28 | 97.4152 | 96.9612
69 | BILAGI | 1 | 1 | 0:30 | 34:53 | 18:05 | 1:37 | 19:42 | 105:37 | 20:12 | 20:12 | 97.2639 | 97.1944 | 140:30 | 140:30 | 97.5952 | 96.801
70 | LOKAPUR | 2 | 2 | 0:00 | 2:56 | 29:14 | 16:10 | 45:24 | 492:51 | 45:24 | 22:42 | 96.8472 | 96.8472 | 495:47 | 247:53 | 94.3892 | 94.3558
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of OCTOBER-2023
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of October-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Oct-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 83 | 82 | 13:50 | 451:03 | 220:28 | 236:49 | 457:17 | 4283:21 | 471:07 | 5:41 | 99.2595 | 99.2371 | 4734:24 | 57:02 | 98.9952 | 98.8894
2 | DHARWAD (RURAL) | 14 | 14 | 5:13 | 20:14 | 169:16 | 23:05 | 192:21 | 1560:04 | 197:34 | 14:07 | 98.1533 | 98.1032 | 1580:18 | 112:53 | 97.8303 | 97.8022
3 | KUNDAGOL | 1 | 1 | 5:18 | 128:17 | 6:34 | 2:42 | 9:16 | 58:48 | 14:34 | 14:34 | 98.7545 | 98.0421 | 187:05 | 187:05 | 98.8551 | 96.3574
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 4:18 | 4:35 | 8:53 | 104:38 | 8:53 | 8:53 | 98.806 | 98.806 | 104:38 | 104:38 | 97.9627 | 97.9627
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 3:30 | 3:24 | 6:54 | 103:02 | 6:54 | 6:54 | 99.0726 | 99.0726 | 103:02 | 103:02 | 97.9939 | 97.9939
6 | KALGHATAGI | 2 | 2 | 0:00 | 7:50 | 35:20 | 26:25 | 61:45 | 253:15 | 61:45 | 30:53 | 95.8501 | 95.8501 | 261:05 | 130:32 | 97.5346 | 97.4583
7 | ALNAVAR | 2 | 2 | 0:00 | 24:00 | 3:30 | 9:55 | 13:25 | 132:15 | 13:25 | 6:42 | 99.0983 | 99.0983 | 156:15 | 78:08 | 98.7125 | 98.4789
8 | NARAGUND | 2 | 2 | 1:20 | 49:40 | 12:40 | 7:45 | 20:25 | 298:45 | 21:45 | 10:52 | 98.6279 | 98.5383 | 348:25 | 174:13 | 97.0916 | 96.6081
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 7:50 | 4:25 | 12:15 | 183:33 | 12:15 | 12:15 | 98.3535 | 98.3535 | 183:33 | 183:33 | 96.4262 | 96.4262
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 31:10 | 7:32 | 38:42 | 389:11 | 38:42 | 12:54 | 98.2661 | 98.2661 | 389:11 | 129:44 | 97.4741 | 97.4741
11 | NAREGAL | 1 | 1 | 0:00 | 10:25 | 12:15 | 1:50 | 14:05 | 58:05 | 14:05 | 14:05 | 98.1071 | 98.1071 | 68:30 | 68:30 | 98.8691 | 98.6663
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 7:25 | 16:30 | 23:55 | 182:50 | 23:55 | 11:58 | 98.3927 | 98.3927 | 182:50 | 91:25 | 98.2201 | 98.2201
13 | RON | 3 | 3 | 0:00 | 0:00 | 25:50 | 4:09 | 29:59 | 286:48 | 29:59 | 10:00 | 98.6567 | 98.6567 | 286:48 | 95:36 | 98.1386 | 98.1386
14 | MUNDARAGI | 1 | 1 | 1:05 | 25:37 | 22:50 | 6:30 | 29:20 | 154:35 | 30:25 | 30:25 | 96.0573 | 95.9117 | 180:12 | 180:12 | 96.9902 | 96.4914
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 56:40 | 9:57 | 66:37 | 414:07 | 66:37 | 66:37 | 91.0461 | 91.0461 | 414:07 | 414:07 | 91.937 | 91.937
16 | SAVANUR | 2 | 2 | 0:00 | 9:20 | 11:30 | 4:45 | 16:15 | 250:50 | 16:15 | 8:08 | 98.9079 | 98.9079 | 260:10 | 130:05 | 97.5581 | 97.4672
17 | SHIGGAON | 3 | 3 | 9:45 | 97:45 | 7:45 | 10:50 | 18:35 | 175:55 | 28:20 | 9:27 | 99.1674 | 98.7306 | 273:40 | 91:13 | 98.8583 | 98.2239
18 | BANKAPUR | 1 | 1 | 1:40 | 69:10 | 12:10 | 4:35 | 16:45 | 159:25 | 18:25 | 18:25 | 97.7487 | 97.5246 | 228:35 | 228:35 | 96.8961 | 95.5494
19 | HANGAL | 2 | 2 | 26:05 | 161:35 | 10:40 | 27:30 | 38:10 | 277:50 | 64:15 | 32:07 | 97.435 | 95.6821 | 439:25 | 219:42 | 97.2952 | 95.7222
20 | RANEBENNUR | 10 | 10 | 23:00 | 60:56 | 70:47 | 16:25 | 87:12 | 1241:10 | 110:12 | 11:01 | 98.828 | 98.5188 | 1302:06 | 130:13 | 97.5834 | 97.4648
21 | TUMINAKATTI | 1 | 1 | 1:35 | 12:10 | 13:30 | 1:00 | 14:30 | 110:50 | 16:05 | 16:05 | 98.0511 | 97.8383 | 123:00 | 123:00 | 97.842 | 97.6051
22 | RATTIHALLI | 1 | 1 | 1:10 | 11:40 | 12:35 | 3:20 | 15:55 | 156:00 | 17:05 | 17:05 | 97.8607 | 97.7039 | 167:40 | 167:40 | 96.9626 | 96.7355
23 | HIREKERUR | 1 | 1 | 1:00 | 11:55 | 12:20 | 2:45 | 15:05 | 156:45 | 16:05 | 16:05 | 97.9727 | 97.8383 | 168:40 | 168:40 | 96.948 | 96.716
24 | BYADAGI | 5 | 5 | 5:05 | 144:37 | 42:26 | 76:03 | 118:29 | 1074:15 | 123:34 | 24:43 | 96.815 | 96.6783 | 1218:52 | 243:46 | 95.8168 | 95.2536
25 | SIRSI | 6 | 6 | 1:15 | 104:09 | 33:55 | 12:33 | 46:28 | 618:18 | 47:43 | 7:57 | 98.9591 | 98.9311 | 722:27 | 120:24 | 97.9936 | 97.6556
26 | YELLAPUR | 1 | 1 | 5:20 | 30:20 | 2:35 | 8:40 | 11:15 | 100:53 | 16:35 | 16:35 | 98.4879 | 97.7711 | 131:13 | 131:13 | 98.0358 | 97.4452
27 | MUNDAGOD | 1 | 1 | 0:10 | 3:28 | 20:05 | 1:20 | 21:25 | 105:02 | 21:35 | 21:35 | 97.1214 | 97.099 | 108:30 | 108:30 | 97.955 | 97.8875
28 | SIDDAPUR | 2 | 2 | 6:10 | 17:20 | 28:20 | 7:05 | 35:25 | 156:12 | 41:35 | 20:48 | 97.6198 | 97.2054 | 173:32 | 86:46 | 98.4794 | 98.3106
29 | DANDELI | 8 | 8 | 8:05 | 459:28 | 40:33 | 9:28 | 50:01 | 1015:35 | 58:06 | 7:16 | 99.1597 | 99.0239 | 1475:03 | 184:23 | 97.5283 | 96.41
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 5:55 | 12:30 | 18:25 | 138:20 | 18:25 | 9:12 | 98.7623 | 98.7623 | 138:20 | 69:10 | 98.6533 | 98.6533
31 | ANKOLA | 2 | 2 | 8:40 | 150:08 | 7:18 | 6:53 | 14:11 | 167:34 | 22:51 | 11:26 | 99.0468 | 98.4644 | 317:42 | 158:51 | 98.3687 | 96.9071
32 | KUMTA | 3 | 3 | 7:09 | 20:03 | 18:55 | 12:23 | 31:18 | 393:15 | 38:27 | 12:49 | 98.5977 | 98.2773 | 413:18 | 137:46 | 97.4478 | 97.3176
33 | GOKARNA | 1 | 1 | 36:41 | 245:28 | 2:20 | 1:00 | 3:20 | 35:00 | 40:01 | 40:01 | 99.552 | 94.6214 | 280:28 | 280:28 | 99.3185 | 94.5392
34 | HONNAVAR | 3 | 3 | 7:09 | 55:39 | 24:17 | 8:09 | 32:26 | 331:42 | 39:35 | 13:12 | 98.5469 | 98.2266 | 387:21 | 129:07 | 97.8472 | 97.486
35 | BHATKAL | 3 | 3 | 5:24 | 70:18 | 22:49 | 10:07 | 32:56 | 222:42 | 38:20 | 12:47 | 98.5245 | 98.2826 | 293:00 | 97:40 | 98.5546 | 98.0984
36 | KHANAPUR | 2 | 2 | 1:45 | 42:05 | 12:35 | 5:15 | 17:50 | 306:00 | 19:35 | 9:48 | 98.8015 | 98.6839 | 348:05 | 174:02 | 97.021 | 96.6113
37 | BAILHONGAL | 3 | 3 | 0:00 | 8:36 | 19:10 | 11:40 | 30:50 | 361:30 | 30:50 | 10:17 | 98.6186 | 98.6186 | 370:06 | 123:22 | 97.6538 | 97.598
38 | KITTUR | 3 | 3 | 8:05 | 20:50 | 51:30 | 10:15 | 61:45 | 397:30 | 69:50 | 23:17 | 97.2334 | 96.8713 | 418:20 | 139:27 | 97.4202 | 97.285
39 | M K HUBLI | 1 | 1 | 0:00 | 1:50 | 13:40 | 4:55 | 18:35 | 180:10 | 18:35 | 18:35 | 97.5022 | 97.5022 | 182:00 | 182:00 | 96.4921 | 96.4564
40 | SOUNDATTI | 3 | 3 | 1:15 | 35:33 | 6:19 | 5:29 | 11:48 | 182:26 | 13:03 | 4:21 | 99.4713 | 99.4153 | 217:59 | 72:40 | 98.816 | 98.5853
41 | MUNAVALLI | 1 | 1 | 2:15 | 49:35 | 45:55 | 1:15 | 47:10 | 318:40 | 49:25 | 49:25 | 93.6604 | 93.358 | 368:15 | 368:15 | 93.7954 | 92.83
42 | YARAGATTI | 1 | 1 | 0:00 | 34:05 | 27:04 | 8:26 | 35:30 | 280:26 | 35:30 | 35:30 | 95.2285 | 95.2285 | 314:31 | 314:31 | 94.5398 | 93.8762
43 | RAMDURG | 2 | 2 | 2:34 | 61:57 | 26:20 | 1:55 | 28:15 | 215:12 | 30:49 | 15:25 | 98.1015 | 97.929 | 277:09 | 138:34 | 97.905 | 97.3019
44 | GOKAK | 10 | 10 | 25:03 | 111:37 | 37:04 | 42:52 | 79:56 | 395:34 | 104:59 | 10:30 | 98.9256 | 98.5889 | 507:11 | 50:43 | 99.2298 | 99.0125
45 | MUDALAGI | 2 | 2 | 1:00 | 5:20 | 18:05 | 6:10 | 24:15 | 205:35 | 25:15 | 12:38 | 98.3703 | 98.3031 | 210:55 | 105:28 | 97.9986 | 97.9467
46 | KONNUR | 1 | 1 | 1:38 | 4:01 | 7:25 | 0:25 | 7:50 | 140:26 | 9:28 | 9:28 | 98.9471 | 98.7276 | 144:27 | 144:27 | 97.2657 | 97.1875
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 32:28 | 3:07 | 35:35 | 252:12 | 35:35 | 35:35 | 95.2173 | 95.2173 | 252:12 | 252:12 | 95.0896 | 95.0896
48 | KUDACHI | 1 | 1 | 0:00 | 2:35 | 18:50 | 3:20 | 22:10 | 236:05 | 22:10 | 22:10 | 97.0206 | 97.0206 | 238:40 | 238:40 | 95.4034 | 95.3531
49 | ATHANI | 7 | 7 | 36:09 | 276:54 | 98:16 | 60:46 | 159:02 | 1724:58 | 195:11 | 27:53 | 96.9464 | 96.2522 | 2001:52 | 285:59 | 95.202 | 94.4318
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 19:43 | 8:20 | 28:03 | 540:09 | 28:03 | 7:01 | 99.0575 | 99.0575 | 540:09 | 135:02 | 97.3708 | 97.3708
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 42:35 | 55:45 | 98:20 | 612:15 | 98:20 | 19:40 | 97.3566 | 97.3566 | 612:15 | 122:27 | 97.6158 | 97.6158
52 | SADALAGA | 1 | 1 | 7:40 | 20:55 | 22:20 | 1:25 | 23:45 | 157:11 | 31:25 | 31:25 | 96.8078 | 95.7773 | 178:06 | 178:06 | 96.9396 | 96.5323
53 | MUDDEBIHAL | 2 | 2 | 4:45 | 101:20 | 35:35 | 5:27 | 41:02 | 350:40 | 45:47 | 22:54 | 97.2424 | 96.9232 | 452:00 | 226:00 | 96.5862 | 95.5997
54 | TALIKOTI | 1 | 1 | 3:05 | 76:45 | 27:50 | 6:40 | 34:30 | 236:50 | 37:35 | 37:35 | 95.3629 | 94.9485 | 313:35 | 313:35 | 95.3888 | 93.8944
55 | B.BAGEWADI | 2 | 2 | 3:45 | 15:44 | 14:46 | 3:15 | 18:01 | 133:03 | 21:46 | 10:53 | 98.7892 | 98.5372 | 148:47 | 74:24 | 98.7047 | 98.5516
56 | INDI | 3 | 3 | 4:22 | 58:30 | 16:04 | 1:39 | 17:43 | 228:35 | 22:05 | 7:22 | 99.2062 | 99.0106 | 287:05 | 95:42 | 98.5165 | 98.1368
57 | SINDAGI | 2 | 2 | 3:50 | 31:45 | 30:25 | 52:25 | 82:50 | 466:40 | 86:40 | 43:20 | 94.4332 | 94.1756 | 498:25 | 249:12 | 95.4569 | 95.1478
58 | GULEDGUDDA | 2 | 2 | 13:03 | 62:09 | 9:05 | 4:53 | 13:58 | 227:47 | 27:01 | 13:30 | 99.0614 | 98.1844 | 289:56 | 144:58 | 97.7825 | 97.1774
59 | ILKAL | 7 | 7 | 13:32 | 60:36 | 28:50 | 43:22 | 72:12 | 1284:04 | 85:44 | 12:15 | 98.6137 | 98.3538 | 1344:40 | 192:06 | 96.4284 | 96.2598
60 | KERUR | 1 | 1 | 0:00 | 15:42 | 8:35 | 3:12 | 11:47 | 151:08 | 11:47 | 11:47 | 98.4162 | 98.4162 | 166:50 | 166:50 | 97.0574 | 96.7517
61 | HUNGUND | 4 | 4 | 7:06 | 61:07 | 33:44 | 35:29 | 69:13 | 597:54 | 76:19 | 19:05 | 97.6742 | 97.4356 | 659:01 | 164:45 | 97.0897 | 96.7922
62 | BADAMI | 2 | 2 | 0:18 | 16:44 | 10:51 | 11:23 | 22:14 | 236:36 | 22:32 | 11:16 | 98.5058 | 98.4857 | 253:20 | 126:40 | 97.6967 | 97.5337
63 | JAMKHANDI | 6 | 6 | 13:30 | 186:45 | 96:40 | 11:05 | 107:45 | 668:10 | 121:15 | 20:12 | 97.5862 | 97.2838 | 854:55 | 142:29 | 97.8318 | 97.2257
64 | MAHALINGAPUR | 2 | 2 | 1:14 | 13:01 | 24:44 | 3:25 | 28:09 | 431:33 | 29:23 | 14:42 | 98.1082 | 98.0253 | 444:34 | 222:17 | 95.7988 | 95.6721
65 | RABAKAVI | 2 | 2 | 1:25 | 23:15 | 7:35 | 4:40 | 12:15 | 141:30 | 13:40 | 6:50 | 99.1767 | 99.0815 | 164:45 | 82:22 | 98.6225 | 98.3961
66 | BANAHATTI | 2 | 2 | 2:34 | 30:41 | 29:05 | 0:35 | 29:40 | 198:56 | 32:14 | 16:07 | 98.0063 | 97.8338 | 229:37 | 114:48 | 98.0633 | 97.7646
67 | TERDAL | 2 | 2 | 1:05 | 24:45 | 47:15 | 5:10 | 52:25 | 384:05 | 53:30 | 26:45 | 96.4774 | 96.4046 | 408:50 | 204:25 | 96.2609 | 96.0199
68 | MUDHOL | 4 | 4 | 14:52 | 94:37 | 71:20 | 8:51 | 80:11 | 534:17 | 95:03 | 23:46 | 97.3057 | 96.8061 | 628:54 | 157:14 | 97.3993 | 96.9388
69 | BILAGI | 1 | 1 | 0:00 | 34:53 | 14:05 | 1:30 | 15:35 | 121:12 | 15:35 | 15:35 | 97.9055 | 97.9055 | 156:05 | 156:05 | 97.6402 | 96.961
70 | LOKAPUR | 2 | 2 | 0:00 | 2:56 | 40:00 | 14:55 | 54:55 | 547:46 | 54:55 | 27:28 | 96.3094 | 96.3094 | 550:42 | 275:21 | 94.6674 | 94.6388
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of NOVEMBER-2023
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of November-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Nov-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 83 | 83 | 44:06 | 495:09 | 221:40 | 196:53 | 418:33 | 4701:54 | 462:39 | 5:34 | 99.2996 | 99.2258 | 5197:03 | 62:37 | 99.0326 | 98.9308
2 | DHARWAD (RURAL) | 14 | 14 | 13:25 | 33:39 | 428:20 | 44:50 | 473:10 | 2033:14 | 486:35 | 34:45 | 95.3059 | 95.1728 | 2066:53 | 147:38 | 97.52 | 97.4789
3 | KUNDAGOL | 1 | 1 | 8:37 | 136:54 | 2:25 | 4:18 | 6:43 | 65:31 | 15:20 | 15:20 | 99.0671 | 97.8704 | 202:25 | 202:25 | 98.8812 | 96.5434
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 11:00 | 3:47 | 14:47 | 119:25 | 14:47 | 14:47 | 97.9468 | 97.9468 | 119:25 | 119:25 | 97.9608 | 97.9608
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 4:20 | 10:30 | 14:50 | 117:52 | 14:50 | 14:50 | 97.9398 | 97.9398 | 117:52 | 117:52 | 97.9872 | 97.9872
6 | KALGHATAGI | 2 | 2 | 0:00 | 7:50 | 28:30 | 5:55 | 34:25 | 287:40 | 34:25 | 17:12 | 97.61 | 97.61 | 295:30 | 147:45 | 97.5438 | 97.4769
7 | ALNAVAR | 2 | 2 | 0:00 | 24:00 | 20:50 | 9:55 | 30:45 | 163:00 | 30:45 | 15:22 | 97.8646 | 97.8646 | 187:00 | 93:30 | 98.6083 | 98.4033
8 | NARAGUND | 2 | 2 | 3:20 | 53:00 | 8:55 | 17:45 | 26:40 | 325:25 | 30:00 | 15:00 | 98.1481 | 97.9167 | 378:25 | 189:13 | 97.2215 | 96.769
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 4:45 | 2:15 | 7:00 | 190:33 | 7:00 | 7:00 | 99.0278 | 99.0278 | 190:33 | 190:33 | 96.7461 | 96.7461
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 31:10 | 7:32 | 38:42 | 427:53 | 38:42 | 12:54 | 98.2083 | 98.2083 | 427:53 | 142:38 | 97.5644 | 97.5644
11 | NAREGAL | 1 | 1 | 0:00 | 10:25 | 3:30 | 6:15 | 9:45 | 67:50 | 9:45 | 9:45 | 98.6458 | 98.6458 | 78:15 | 78:15 | 98.8416 | 98.6638
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 11:35 | 11:10 | 22:45 | 205:35 | 22:45 | 11:22 | 98.4201 | 98.4201 | 205:35 | 102:47 | 98.2447 | 98.2447
13 | RON | 3 | 3 | 0:00 | 0:00 | 21:10 | 7:22 | 28:32 | 315:20 | 28:32 | 9:31 | 98.679 | 98.679 | 315:20 | 105:07 | 98.2051 | 98.2051
14 | MUNDARAGI | 1 | 1 | 0:36 | 26:13 | 12:50 | 17:55 | 30:45 | 185:20 | 31:21 | 31:21 | 95.7292 | 95.6458 | 211:33 | 211:33 | 96.8352 | 96.3875
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 43:15 | 15:31 | 58:46 | 472:53 | 58:46 | 58:46 | 91.838 | 91.838 | 472:53 | 472:53 | 91.9248 | 91.9248
16 | SAVANUR | 2 | 2 | 1:00 | 10:20 | 25:55 | 7:55 | 33:50 | 284:40 | 34:50 | 17:25 | 97.6505 | 97.581 | 295:00 | 147:30 | 97.5694 | 97.4812
17 | SHIGGAON | 3 | 3 | 6:30 | 104:15 | 10:40 | 8:10 | 18:50 | 194:45 | 25:20 | 8:27 | 99.1281 | 98.8272 | 299:00 | 99:40 | 98.8915 | 98.298
18 | BANKAPUR | 1 | 1 | 14:10 | 83:20 | 15:55 | 8:45 | 24:40 | 184:05 | 38:50 | 38:50 | 96.5741 | 94.6065 | 267:25 | 267:25 | 96.8565 | 95.4335
19 | HANGAL | 2 | 2 | 7:50 | 169:25 | 16:15 | 7:20 | 23:35 | 301:25 | 31:25 | 15:43 | 98.3623 | 97.8183 | 470:50 | 235:25 | 97.4264 | 95.9799
20 | RANEBENNUR | 10 | 10 | 19:55 | 80:51 | 35:27 | 57:18 | 92:45 | 1333:55 | 112:40 | 11:16 | 98.7118 | 98.4352 | 1414:46 | 141:29 | 97.7221 | 97.5841
21 | TUMINAKATTI | 1 | 1 | 1:05 | 13:15 | 12:40 | 0:35 | 13:15 | 124:05 | 14:20 | 14:20 | 98.1597 | 98.0093 | 137:20 | 137:20 | 97.8811 | 97.6548
22 | RATTIHALLI | 1 | 1 | 1:25 | 13:05 | 6:25 | 4:30 | 10:55 | 166:55 | 12:20 | 12:20 | 98.4838 | 98.287 | 180:00 | 180:00 | 97.1496 | 96.9262
23 | HIREKERUR | 1 | 1 | 1:05 | 13:00 | 3:55 | 8:40 | 12:35 | 169:20 | 13:40 | 13:40 | 98.2523 | 98.1019 | 182:20 | 182:20 | 97.1084 | 96.8864
24 | BYADAGI | 5 | 5 | 4:10 | 148:47 | 46:40 | 38:55 | 85:35 | 1159:50 | 89:45 | 17:57 | 97.6227 | 97.5069 | 1308:37 | 261:43 | 96.0388 | 95.5307
25 | SIRSI | 6 | 6 | 1:15 | 105:24 | 33:55 | 12:33 | 46:28 | 664:46 | 47:43 | 7:57 | 98.9244 | 98.8954 | 770:10 | 128:22 | 98.108 | 97.808
26 | YELLAPUR | 1 | 1 | 5:20 | 35:40 | 2:35 | 8:40 | 11:15 | 112:08 | 16:35 | 16:35 | 98.4375 | 97.6968 | 147:48 | 147:48 | 98.0852 | 97.4761
27 | MUNDAGOD | 2 | 2 | 6:10 | 9:38 | 6:00 | 4:55 | 10:55 | 115:57 | 17:05 | 8:32 | 99.2419 | 98.8137 | 125:35 | 62:47 | 99.01 | 98.9277
28 | SIDDAPUR | 2 | 2 | 3:15 | 20:35 | 43:00 | 4:35 | 47:35 | 203:47 | 50:50 | 25:25 | 96.6956 | 96.4699 | 224:22 | 112:11 | 98.26 | 98.0843
29 | DANDELI | 8 | 8 | 22:42 | 482:10 | 19:28 | 51:39 | 71:07 | 1086:42 | 93:49 | 11:44 | 98.7653 | 98.3712 | 1568:52 | 196:06 | 97.6804 | 96.6512
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 16:25 | 6:35 | 23:00 | 161:20 | 23:00 | 11:30 | 98.4028 | 98.4028 | 161:20 | 80:40 | 98.6225 | 98.6225
31 | ANKOLA | 2 | 2 | 17:30 | 167:38 | 3:10 | 5:18 | 8:28 | 176:02 | 25:58 | 12:59 | 99.412 | 98.1968 | 343:40 | 171:50 | 98.497 | 97.0657
32 | KUMTA | 3 | 3 | 0:00 | 20:03 | 29:30 | 21:51 | 51:21 | 444:36 | 51:21 | 17:07 | 97.6227 | 97.6227 | 464:39 | 154:53 | 97.4693 | 97.3551
33 | GOKARNA | 1 | 1 | 17:16 | 262:44 | 1:40 | 2:00 | 3:40 | 38:40 | 20:56 | 20:56 | 99.4907 | 97.0926 | 301:24 | 301:24 | 99.3397 | 94.8531
34 | HONNAVAR | 3 | 3 | 0:00 | 55:39 | 14:56 | 5:13 | 20:09 | 351:51 | 20:09 | 6:43 | 99.0671 | 99.0671 | 407:30 | 135:50 | 97.9972 | 97.6804
35 | BHATKAL | 3 | 3 | 9:24 | 79:42 | 21:19 | 17:25 | 38:44 | 261:26 | 48:08 | 16:03 | 98.2068 | 97.7716 | 341:08 | 113:43 | 98.5119 | 98.0582
36 | KHANAPUR | 2 | 2 | 12:30 | 54:35 | 24:05 | 8:40 | 32:45 | 338:45 | 45:15 | 22:38 | 97.7257 | 96.8576 | 393:20 | 196:40 | 97.1077 | 96.6416
37 | BAILHONGAL | 3 | 3 | 0:00 | 8:36 | 40:30 | 11:30 | 52:00 | 413:30 | 52:00 | 17:20 | 97.5926 | 97.5926 | 422:06 | 140:42 | 97.6463 | 97.5973
38 | KITTUR | 3 | 3 | 0:00 | 20:50 | 6:10 | 4:45 | 10:55 | 408:25 | 10:55 | 3:38 | 99.4946 | 99.4946 | 429:15 | 143:05 | 97.6752 | 97.5566
39 | M K HUBLI | 1 | 1 | 0:00 | 1:50 | 22:20 | 9:10 | 31:30 | 211:40 | 31:30 | 31:30 | 95.625 | 95.625 | 213:30 | 213:30 | 96.3855 | 96.3542
40 | SOUNDATTI | 3 | 3 | 3:21 | 38:54 | 16:22 | 6:12 | 22:34 | 205:00 | 25:55 | 8:38 | 98.9552 | 98.8002 | 243:54 | 81:18 | 98.8331 | 98.6117
41 | MUNAVALLI | 1 | 1 | 1:15 | 50:50 | 21:10 | 2:00 | 23:10 | 341:50 | 24:25 | 24:25 | 96.7824 | 96.6088 | 392:40 | 392:40 | 94.1627 | 93.2946
42 | YARAGATTI | 1 | 1 | 0:47 | 34:52 | 29:31 | 12:49 | 42:20 | 322:46 | 43:07 | 43:07 | 94.1204 | 94.0116 | 357:38 | 357:38 | 94.4883 | 93.8929
43 | RAMDURG | 2 | 2 | 5:14 | 67:11 | 12:17 | 2:20 | 14:37 | 229:49 | 19:51 | 9:56 | 98.985 | 98.6215 | 297:00 | 148:30 | 98.0378 | 97.4641
44 | GOKAK | 10 | 10 | 2:03 | 113:40 | 32:08 | 9:30 | 41:38 | 437:12 | 43:41 | 4:22 | 99.4218 | 99.3933 | 550:52 | 55:05 | 99.2534 | 99.0593
45 | MUDALAGI | 2 | 2 | 13:35 | 18:55 | 13:15 | 13:00 | 26:15 | 231:50 | 39:50 | 19:55 | 98.1771 | 97.2338 | 250:45 | 125:23 | 98.0205 | 97.859
46 | KONNUR | 1 | 1 | 0:00 | 4:01 | 15:25 | 5:50 | 21:15 | 161:41 | 21:15 | 21:15 | 97.0486 | 97.0486 | 165:42 | 165:42 | 97.239 | 97.1704
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 17:50 | 5:55 | 23:45 | 275:57 | 23:45 | 23:45 | 96.7014 | 96.7014 | 275:57 | 275:57 | 95.2877 | 95.2877
48 | KUDACHI | 1 | 1 | 0:00 | 2:35 | 17:25 | 2:00 | 19:25 | 255:30 | 19:25 | 19:25 | 97.3032 | 97.3032 | 258:05 | 258:05 | 95.637 | 95.5928
49 | ATHANI | 7 | 7 | 4:42 | 281:36 | 59:40 | 42:33 | 102:13 | 1827:11 | 106:55 | 15:16 | 97.9719 | 97.8786 | 2108:47 | 301:15 | 95.5426 | 94.8556
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 23:27 | 5:05 | 28:32 | 568:41 | 28:32 | 7:08 | 99.0093 | 99.0093 | 568:41 | 142:10 | 97.5722 | 97.5722
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 22:00 | 16:50 | 38:50 | 651:05 | 38:50 | 7:46 | 98.9213 | 98.9213 | 651:05 | 130:13 | 97.7764 | 97.7764
52 | SADALAGA | 1 | 1 | 1:45 | 22:40 | 12:20 | 1:30 | 13:50 | 171:01 | 15:35 | 15:35 | 98.0787 | 97.8356 | 193:41 | 193:41 | 97.0796 | 96.6926
53 | MUDDEBIHAL | 2 | 2 | 0:00 | 101:20 | 65:02 | 14:55 | 79:57 | 430:37 | 79:57 | 39:58 | 94.4479 | 94.4479 | 531:57 | 265:59 | 96.3233 | 95.4581
54 | TALIKOTI | 1 | 1 | 0:35 | 77:20 | 58:25 | 9:05 | 67:30 | 304:20 | 68:05 | 68:05 | 90.625 | 90.544 | 381:40 | 381:40 | 94.8031 | 93.4825
55 | B.BAGEWADI | 2 | 2 | 5:25 | 21:09 | 4:37 | 2:01 | 6:38 | 139:41 | 12:03 | 6:02 | 99.5394 | 99.1632 | 160:50 | 80:25 | 98.8073 | 98.6268
56 | INDI | 3 | 3 | 3:40 | 62:10 | 22:17 | 7:05 | 29:22 | 257:57 | 33:02 | 11:01 | 98.6404 | 98.4707 | 320:07 | 106:42 | 98.5317 | 98.1778
57 | SINDAGI | 2 | 2 | 0:00 | 31:45 | 37:50 | 0:00 | 37:50 | 504:30 | 37:50 | 18:55 | 97.3727 | 97.3727 | 536:15 | 268:08 | 95.6925 | 95.4214
58 | GULEDGUDDA | 2 | 2 | 0:00 | 62:09 | 7:58 | 16:09 | 24:07 | 251:54 | 24:07 | 12:04 | 98.3252 | 98.3252 | 314:03 | 157:02 | 97.8492 | 97.3186
59 | ILKAL | 7 | 7 | 2:55 | 63:31 | 16:23 | 45:06 | 61:29 | 1345:33 | 64:24 | 9:12 | 98.7801 | 98.7222 | 1409:04 | 201:18 | 96.7175 | 96.5626
60 | KERUR | 1 | 1 | 0:00 | 15:42 | 6:34 | 4:00 | 10:34 | 161:42 | 10:34 | 10:34 | 98.5324 | 98.5324 | 177:24 | 177:24 | 97.2387 | 96.9706
61 | HUNGUND | 4 | 4 | 2:00 | 63:07 | 14:50 | 46:41 | 61:31 | 659:25 | 63:31 | 15:53 | 97.864 | 97.7946 | 722:32 | 180:38 | 97.1849 | 96.9154
62 | BADAMI | 2 | 2 | 1:20 | 18:04 | 13:01 | 15:39 | 28:40 | 265:16 | 30:00 | 15:00 | 98.0093 | 97.9167 | 283:20 | 141:40 | 97.7351 | 97.5808
63 | JAMKHANDI | 6 | 6 | 6:53 | 193:38 | 52:40 | 14:30 | 67:10 | 735:20 | 74:03 | 12:20 | 98.4452 | 98.2859 | 928:58 | 154:50 | 97.9072 | 97.3561
64 | MAHALINGAPUR | 2 | 2 | 0:00 | 13:01 | 18:14 | 5:39 | 23:53 | 455:26 | 23:53 | 11:56 | 98.3414 | 98.3414 | 468:27 | 234:14 | 96.1114 | 96.0003
65 | RABAKAVI | 2 | 2 | 12:05 | 35:20 | 10:00 | 2:40 | 12:40 | 154:10 | 24:45 | 12:22 | 99.1204 | 98.2812 | 189:30 | 94:45 | 98.6837 | 98.382
66 | BANAHATTI | 2 | 2 | 2:38 | 33:19 | 8:32 | 0:25 | 8:57 | 207:53 | 11:35 | 5:48 | 99.3785 | 99.1956 | 241:12 | 120:36 | 98.225 | 97.9406
67 | TERDAL | 2 | 2 | 0:50 | 25:35 | 26:40 | 3:35 | 30:15 | 414:20 | 31:05 | 15:33 | 97.8993 | 97.8414 | 439:55 | 219:58 | 96.4623 | 96.2439
68 | MUDHOL | 4 | 4 | 0:05 | 94:42 | 61:54 | 11:08 | 73:02 | 607:19 | 73:07 | 18:17 | 97.4641 | 97.4612 | 702:01 | 175:30 | 97.4073 | 97.003
69 | BILAGI | 1 | 1 | 1:20 | 36:13 | 7:30 | 3:30 | 11:00 | 132:12 | 12:20 | 12:20 | 98.4722 | 98.287 | 168:25 | 168:25 | 97.7425 | 97.124
70 | LOKAPUR | 2 | 2 | 0:00 | 2:56 | 31:25 | 5:40 | 37:05 | 584:51 | 37:05 | 18:32 | 97.4248 | 97.4248 | 587:47 | 293:54 | 95.0064 | 94.9814
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of DECEMBER-2023
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of December-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Dec-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 85 | 85 | 34:52 | 530:01 | 372:45 | 166:32 | 539:17 | 5241:11 | 574:09 | 6:45 | 99.1472 | 99.0921 | 5771:12 | 67:54 | 99.0657 | 98.9713
2 | DHARWAD (RURAL) | 13 | 13 | 0:05 | 33:44 | 126:44 | 11:51 | 138:35 | 2171:49 | 138:40 | 10:40 | 98.5672 | 98.5663 | 2205:33 | 169:39 | 97.4687 | 97.4294
3 | KUNDAGOL | 1 | 1 | 0:59 | 137:53 | 1:57 | 0:34 | 2:31 | 68:02 | 3:30 | 3:30 | 99.6617 | 99.5296 | 205:55 | 205:55 | 98.9692 | 96.8801
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 2:50 | 1:44 | 4:34 | 123:59 | 4:34 | 4:34 | 99.3862 | 99.3862 | 123:59 | 123:59 | 98.1215 | 98.1215
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 4:05 | 7:20 | 11:25 | 129:17 | 11:25 | 11:25 | 98.4655 | 98.4655 | 129:17 | 129:17 | 98.0412 | 98.0412
6 | KALGHATAGI | 2 | 2 | 0:00 | 7:50 | 7:05 | 1:40 | 8:45 | 296:25 | 8:45 | 4:22 | 99.412 | 99.412 | 304:15 | 152:08 | 97.7544 | 97.6951
7 | ALNAVAR | 2 | 1 | 0:00 | 24:00 | 3:50 | 1:05 | 4:55 | 167:55 | 4:55 | 2:28 | 99.6696 | 99.6696 | 191:55 | 95:57 | 98.7279 | 98.5461
8 | NARAGUND | 2 | 2 | 2:20 | 55:20 | 14:10 | 20:05 | 34:15 | 359:40 | 36:35 | 18:18 | 97.6983 | 97.5414 | 415:00 | 207:30 | 97.2753 | 96.8561
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 3:45 | 1:45 | 5:30 | 196:03 | 5:30 | 5:30 | 99.2608 | 99.2608 | 196:03 | 196:03 | 97.0295 | 97.0295
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 31:10 | 7:32 | 38:42 | 466:35 | 38:42 | 12:54 | 98.2661 | 98.2661 | 466:35 | 155:32 | 97.6435 | 97.6435
11 | NAREGAL | 1 | 1 | 2:25 | 12:50 | 8:55 | 1:30 | 10:25 | 78:15 | 12:50 | 12:50 | 98.5999 | 98.2751 | 91:05 | 91:05 | 98.8144 | 98.6199
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 23:55 | 2:00 | 25:55 | 231:30 | 25:55 | 12:58 | 98.2583 | 98.2583 | 231:30 | 115:45 | 98.2462 | 98.2462
13 | RON | 3 | 3 | 0:00 | 0:00 | 40:30 | 2:48 | 43:18 | 358:38 | 43:18 | 14:26 | 98.06 | 98.06 | 358:38 | 119:33 | 98.1887 | 98.1887
14 | MUNDARAGI | 1 | 1 | 0:00 | 26:13 | 9:50 | 4:00 | 13:50 | 199:10 | 13:50 | 13:50 | 98.1407 | 98.1407 | 225:23 | 225:23 | 96.9823 | 96.5851
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 25:25 | 9:14 | 34:39 | 507:32 | 34:39 | 34:39 | 95.3427 | 95.3427 | 507:32 | 507:32 | 92.3101 | 92.3101
16 | SAVANUR | 2 | 2 | 1:00 | 11:20 | 14:50 | 2:05 | 16:55 | 301:35 | 17:55 | 8:58 | 98.8631 | 98.7959 | 312:55 | 156:28 | 97.7153 | 97.6294
17 | SHIGGAON | 3 | 3 | 18:50 | 123:05 | 21:10 | 4:35 | 25:45 | 220:30 | 44:35 | 14:52 | 98.8463 | 98.0025 | 343:35 | 114:32 | 98.8864 | 98.2647
18 | BANKAPUR | 1 | 1 | 3:15 | 86:35 | 6:20 | 5:55 | 12:15 | 196:20 | 15:30 | 15:30 | 98.3535 | 97.9167 | 282:55 | 282:55 | 97.0253 | 95.7134
19 | HANGAL | 2 | 2 | 1:30 | 170:55 | 32:05 | 7:05 | 39:10 | 340:35 | 40:40 | 20:20 | 97.3678 | 97.267 | 511:30 | 255:45 | 97.4198 | 96.125
20 | RANEBENNUR | 9 | 9 | 15:33 | 96:24 | 64:51 | 13:00 | 77:51 | 1411:46 | 93:24 | 10:23 | 98.8374 | 98.6051 | 1508:10 | 167:34 | 97.6233 | 97.461
21 | TUMINAKATTI | 1 | 1 | 3:25 | 16:40 | 12:30 | 0:50 | 13:20 | 137:25 | 16:45 | 16:45 | 98.2079 | 97.7487 | 154:05 | 154:05 | 97.9179 | 97.6654
22 | RATTIHALLI | 1 | 1 | 2:00 | 15:05 | 23:00 | 0:40 | 23:40 | 190:35 | 25:40 | 25:40 | 96.819 | 96.5502 | 205:40 | 205:40 | 97.1124 | 96.8838
23 | HIREKERUR | 1 | 1 | 1:00 | 14:00 | 12:20 | 2:45 | 15:05 | 184:25 | 16:05 | 16:05 | 97.9727 | 97.8383 | 198:25 | 198:25 | 97.2058 | 96.9937
24 | BYADAGI | 5 | 5 | 8:44 | 157:31 | 49:55 | 5:45 | 55:40 | 1215:30 | 64:24 | 12:53 | 98.5036 | 98.2688 | 1373:01 | 274:36 | 96.3167 | 95.8393
25 | SIRSI | 6 | 6 | 82:35 | 187:59 | 73:35 | 111:50 | 185:25 | 850:11 | 268:00 | 44:40 | 95.8464 | 93.9964 | 1038:10 | 173:02 | 97.8531 | 97.3784
26 | YELLAPUR | 1 | 1 | 20:30 | 56:10 | 2:45 | 0:00 | 2:45 | 114:53 | 23:15 | 23:15 | 99.6304 | 96.875 | 171:03 | 171:03 | 98.2593 | 97.4083
27 | MUNDAGOD | 1 | 1 | 0:00 | 9:38 | 9:15 | 1:50 | 11:05 | 127:02 | 11:05 | 11:05 | 98.5103 | 98.5103 | 136:40 | 136:40 | 98.0753 | 97.9293
28 | SIDDAPUR | 2 | 2 | 30:20 | 50:55 | 23:40 | 48:10 | 71:50 | 275:37 | 102:10 | 51:05 | 95.1725 | 93.134 | 326:32 | 163:16 | 97.912 | 97.5263
29 | DANDELI | 8 | 8 | 73:28 | 555:38 | 92:04 | 19:02 | 111:06 | 1197:48 | 184:34 | 23:04 | 98.1334 | 96.8991 | 1753:26 | 219:11 | 97.7314 | 96.6791
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 17:40 | 3:35 | 21:15 | 182:35 | 21:15 | 10:38 | 98.5719 | 98.5719 | 182:35 | 91:18 | 98.6168 | 98.6168
31 | ANKOLA | 2 | 2 | 9:00 | 176:38 | 3:10 | 5:18 | 8:28 | 184:30 | 17:28 | 8:44 | 99.431 | 98.8262 | 361:08 | 180:34 | 98.6023 | 97.2641
32 | KUMTA | 3 | 3 | 8:03 | 28:06 | 29:37 | 8:19 | 37:56 | 482:32 | 45:59 | 15:20 | 98.3005 | 97.9398 | 510:38 | 170:13 | 97.563 | 97.421
33 | GOKARNA | 1 | 1 | 15:16 | 278:00 | 4:15 | 0:05 | 4:20 | 43:00 | 19:36 | 19:36 | 99.4176 | 97.3656 | 321:00 | 321:00 | 99.3485 | 95.1364
34 | HONNAVAR | 3 | 3 | 8:03 | 63:42 | 18:35 | 4:15 | 22:50 | 374:41 | 30:53 | 10:18 | 98.977 | 98.6163 | 438:23 | 146:08 | 98.1077 | 97.7859
35 | BHATKAL | 3 | 3 | 0:30 | 80:12 | 18:46 | 4:03 | 22:49 | 284:15 | 23:19 | 7:46 | 98.9777 | 98.9553 | 364:27 | 121:29 | 98.5644 | 98.1593
36 | KHANAPUR | 2 | 2 | 0:50 | 55:25 | 9:40 | 3:45 | 13:25 | 352:10 | 14:15 | 7:08 | 99.0983 | 99.0423 | 407:35 | 203:48 | 97.3321 | 96.9122
37 | BAILHONGAL | 3 | 3 | 0:00 | 8:36 | 10:10 | 4:50 | 15:00 | 428:30 | 15:00 | 5:00 | 99.328 | 99.328 | 437:06 | 145:42 | 97.8359 | 97.7924
38 | KITTUR | 3 | 3 | 0:00 | 20:50 | 24:40 | 2:30 | 27:10 | 435:35 | 27:10 | 9:03 | 98.7829 | 98.7829 | 456:25 | 152:08 | 97.8001 | 97.6949
39 | M K HUBLI | 1 | 1 | 0:00 | 1:50 | 9:10 | 3:10 | 12:20 | 224:00 | 12:20 | 12:20 | 98.3423 | 98.3423 | 225:50 | 225:50 | 96.6061 | 96.5783
40 | SOUNDATTI | 3 | 3 | 14:23 | 53:17 | 3:36 | 1:12 | 4:48 | 209:48 | 19:11 | 6:24 | 99.7849 | 99.1405 | 263:05 | 87:42 | 98.9404 | 98.6713
41 | MUNAVALLI | 1 | 1 | 8:30 | 59:20 | 21:10 | 2:00 | 23:10 | 365:00 | 31:40 | 31:40 | 96.8862 | 95.7437 | 424:20 | 424:20 | 94.4697 | 93.5707
42 | YARAGATTI | 1 | 1 | 0:00 | 34:52 | 30:12 | 2:58 | 33:10 | 355:56 | 33:10 | 33:10 | 95.5421 | 95.5421 | 390:48 | 390:48 | 94.6071 | 94.0788
43 | RAMDURG | 2 | 2 | 5:14 | 72:25 | 12:17 | 2:20 | 14:37 | 244:26 | 19:51 | 9:56 | 99.0177 | 98.666 | 316:51 | 158:26 | 98.1482 | 97.5996
44 | GOKAK | 10 | 10 | 14:56 | 128:36 | 15:06 | 6:20 | 21:26 | 458:38 | 36:22 | 3:38 | 99.7119 | 99.5112 | 587:14 | 58:43 | 99.3051 | 99.1103
45 | MUDALAGI | 2 | 2 | 0:00 | 18:55 | 18:45 | 3:10 | 21:55 | 253:45 | 21:55 | 10:58 | 98.5271 | 98.5271 | 272:40 | 136:20 | 98.0777 | 97.9343
46 | KONNUR | 1 | 1 | 0:00 | 4:01 | 13:15 | 0:05 | 13:20 | 175:01 | 13:20 | 13:20 | 98.2079 | 98.2079 | 179:02 | 179:02 | 97.3482 | 97.2874
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 31:25 | 5:50 | 37:15 | 313:12 | 37:15 | 37:15 | 94.9933 | 94.9933 | 313:12 | 313:12 | 95.2545 | 95.2545
48 | KUDACHI | 1 | 1 | 0:00 | 2:35 | 25:20 | 0:25 | 25:45 | 281:15 | 25:45 | 25:45 | 96.539 | 96.539 | 283:50 | 283:50 | 95.7386 | 95.6995
49 | ATHANI | 7 | 7 | 32:06 | 313:42 | 96:07 | 17:43 | 113:50 | 1941:01 | 145:56 | 20:51 | 97.8143 | 97.1979 | 2254:43 | 322:06 | 95.7987 | 95.1197
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 16:40 | 1:20 | 18:00 | 586:41 | 18:00 | 4:30 | 99.3952 | 99.3952 | 586:41 | 146:40 | 97.7777 | 97.7777
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 64:20 | 5:55 | 70:15 | 721:20 | 70:15 | 14:03 | 98.1116 | 98.1116 | 721:20 | 144:16 | 97.8141 | 97.8141
52 | SADALAGA | 1 | 1 | 4:40 | 27:20 | 14:20 | 3:35 | 17:55 | 188:56 | 22:35 | 22:35 | 97.5918 | 96.9646 | 216:16 | 216:16 | 97.1374 | 96.7232
53 | MUDDEBIHAL | 2 | 2 | 18:20 | 119:40 | 47:20 | 3:00 | 50:20 | 480:57 | 68:40 | 34:20 | 96.6174 | 95.3853 | 600:37 | 300:19 | 96.3564 | 95.4499
54 | TALIKOTI | 1 | 1 | 8:15 | 85:35 | 10:30 | 7:00 | 17:30 | 321:50 | 25:45 | 25:45 | 97.6478 | 96.539 | 407:25 | 407:25 | 95.1237 | 93.827
55 | B.BAGEWADI | 2 | 2 | 1:02 | 22:11 | 3:44 | 0:40 | 4:24 | 144:05 | 5:26 | 2:43 | 99.7043 | 99.6349 | 166:16 | 83:08 | 98.9085 | 98.7404
56 | INDI | 3 | 3 | 17:56 | 80:06 | 25:17 | 1:31 | 26:48 | 284:45 | 44:44 | 14:55 | 98.7993 | 97.9958 | 364:51 | 121:37 | 98.5619 | 98.1573
57 | SINDAGI | 2 | 2 | 0:00 | 31:45 | 62:45 | 0:00 | 62:45 | 567:15 | 62:45 | 31:22 | 95.7829 | 95.7829 | 599:00 | 299:30 | 95.7027 | 95.4621
58 | GULEDGUDDA | 2 | 2 | 0:00 | 62:09 | 4:02 | 4:40 | 8:42 | 260:36 | 8:42 | 4:21 | 99.4153 | 99.4153 | 322:45 | 161:23 | 98.0258 | 97.5549
59 | ILKAL | 7 | 7 | 0:00 | 63:31 | 90:34 | 32:35 | 123:09 | 1468:42 | 123:09 | 17:36 | 97.6354 | 97.6354 | 1532:13 | 218:53 | 96.821 | 96.6835
60 | KERUR | 1 | 1 | 0:00 | 15:42 | 9:34 | 1:44 | 11:18 | 173:00 | 11:18 | 11:18 | 98.4812 | 98.4812 | 188:42 | 188:42 | 97.3788 | 97.1409
61 | HUNGUND | 4 | 4 | 0:00 | 63:07 | 43:55 | 15:06 | 59:01 | 718:26 | 59:01 | 14:45 | 98.0169 | 98.0169 | 781:33 | 195:23 | 97.2787 | 97.0396
62 | BADAMI | 2 | 2 | 0:28 | 18:32 | 26:44 | 6:30 | 33:14 | 298:30 | 33:42 | 16:51 | 97.7666 | 97.7352 | 317:02 | 158:31 | 97.7386 | 97.5982
63 | JAMKHANDI | 6 | 6 | 4:00 | 197:38 | 35:05 | 4:15 | 39:20 | 774:40 | 43:20 | 7:13 | 99.1189 | 99.0293 | 972:18 | 162:03 | 98.0438 | 97.5447
64 | MAHALINGAPUR | 2 | 2 | 0:14 | 13:15 | 17:22 | 5:39 | 23:01 | 478:27 | 23:15 | 11:38 | 98.4532 | 98.4375 | 491:42 | 245:51 | 96.3754 | 96.275
65 | RABAKAVI | 2 | 2 | 1:45 | 37:05 | 24:20 | 1:40 | 26:00 | 180:10 | 27:45 | 13:52 | 98.2527 | 98.1351 | 217:15 | 108:38 | 98.6351 | 98.3542
66 | BANAHATTI | 2 | 2 | 0:13 | 33:32 | 37:37 | 1:10 | 38:47 | 246:40 | 39:00 | 19:30 | 97.3936 | 97.379 | 280:12 | 140:06 | 98.1313 | 97.8773
67 | TERDAL | 2 | 2 | 16:25 | 42:00 | 58:25 | 2:35 | 61:00 | 475:20 | 77:25 | 38:42 | 95.9005 | 94.7973 | 517:20 | 258:40 | 96.399 | 96.0808
68 | MUDHOL | 4 | 4 | 0:12 | 94:54 | 49:42 | 8:25 | 58:07 | 665:26 | 58:19 | 14:35 | 98.0472 | 98.0404 | 760:20 | 190:05 | 97.4794 | 97.1199
69 | BILAGI | 1 | 1 | 0:15 | 36:28 | 11:35 | 1:40 | 13:15 | 145:27 | 13:30 | 13:30 | 98.2191 | 98.1855 | 181:55 | 181:55 | 97.7962 | 97.2437
70 | LOKAPUR | 2 | 2 | 0:00 | 2:56 | 44:20 | 7:55 | 52:15 | 637:06 | 52:15 | 26:08 | 96.4886 | 96.4886 | 640:02 | 320:01 | 95.1735 | 95.1513
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of JANUARY-2024
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of January-24 |  |  |  | Reliability for cumulative period from Apr-23 to Jan-24
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 85 | 85 | 25:05 | 555:06 | 230:48 | 160:21 | 391:09 | 5632:20 | 416:14 | 4:54 | 99.3815 | 99.3418 | 6187:26 | 72:48 | 99.0977 | 99.0088
2 | DHARWAD (RURAL) | 13 | 13 | 0:33 | 34:17 | 74:50 | 6:49 | 81:39 | 2253:28 | 82:12 | 6:19 | 99.1558 | 99.1501 | 2287:45 | 175:59 | 97.6397 | 97.6037
3 | KUNDAGOL | 1 | 1 | 2:40 | 140:33 | 2:59 | 0:22 | 3:21 | 71:23 | 6:01 | 6:01 | 99.5497 | 99.1913 | 211:56 | 211:56 | 99.028 | 97.1142
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 3:38 | 2:14 | 5:52 | 129:51 | 5:52 | 5:52 | 99.2115 | 99.2115 | 129:51 | 129:51 | 98.2319 | 98.2319
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 3:10 | 2:13 | 5:23 | 134:40 | 5:23 | 5:23 | 99.2764 | 99.2764 | 134:40 | 134:40 | 98.1663 | 98.1663
6 | KALGHATAGI | 2 | 2 | 0:00 | 7:50 | 23:35 | 11:50 | 35:25 | 331:50 | 35:25 | 17:42 | 97.6198 | 97.6198 | 339:40 | 169:50 | 97.7408 | 97.6875
7 | ALNAVAR | 2 | 2 | 0:00 | 24:00 | 1:20 | 2:25 | 3:45 | 171:40 | 3:45 | 1:52 | 99.748 | 99.748 | 195:40 | 97:50 | 98.8312 | 98.6678
8 | NARAGUND | 2 | 2 | 0:30 | 55:50 | 10:40 | 10:20 | 21:00 | 380:40 | 21:30 | 10:45 | 98.5887 | 98.5551 | 436:30 | 218:15 | 97.4083 | 97.0282
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 2:20 | 4:21 | 6:41 | 202:44 | 6:41 | 6:41 | 99.1017 | 99.1017 | 202:44 | 202:44 | 97.2395 | 97.2395
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 19:17 | 8:44 | 28:01 | 494:36 | 28:01 | 9:20 | 98.7448 | 98.7448 | 494:36 | 164:52 | 97.7551 | 97.7551
11 | NAREGAL | 1 | 1 | 0:00 | 12:50 | 6:50 | 1:40 | 8:30 | 86:45 | 8:30 | 8:30 | 98.8575 | 98.8575 | 99:35 | 99:35 | 98.8188 | 98.644
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 7:10 | 5:25 | 12:35 | 244:05 | 12:35 | 6:18 | 99.1543 | 99.1543 | 244:05 | 122:02 | 98.3382 | 98.3382
13 | RON | 3 | 3 | 0:00 | 0:00 | 13:40 | 0:50 | 14:30 | 373:08 | 14:30 | 4:50 | 99.3504 | 99.3504 | 373:08 | 124:23 | 98.3064 | 98.3064
14 | MUNDARAGI | 1 | 1 | 0:00 | 26:13 | 4:20 | 4:20 | 8:40 | 207:50 | 8:40 | 8:40 | 98.8351 | 98.8351 | 234:03 | 234:03 | 97.17 | 96.813
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 41:30 | 3:38 | 45:08 | 552:40 | 45:08 | 45:08 | 93.9337 | 93.9337 | 552:40 | 552:40 | 92.4746 | 92.4746
16 | SAVANUR | 2 | 2 | 6:20 | 17:40 | 3:50 | 2:45 | 6:35 | 308:10 | 12:55 | 6:28 | 99.5576 | 99.1319 | 325:50 | 162:55 | 97.9019 | 97.7816
17 | SHIGGAON | 3 | 3 | 7:20 | 130:25 | 12:05 | 6:35 | 18:40 | 239:10 | 26:00 | 8:40 | 99.1637 | 98.8351 | 369:35 | 123:12 | 98.9145 | 98.3225
18 | BANKAPUR | 1 | 1 | 11:15 | 97:50 | 8:05 | 2:45 | 10:50 | 207:10 | 22:05 | 22:05 | 98.5439 | 97.0318 | 305:00 | 305:00 | 97.1791 | 95.8469
19 | HANGAL | 2 | 2 | 4:15 | 175:10 | 23:10 | 5:00 | 28:10 | 368:45 | 32:25 | 16:12 | 98.1071 | 97.8215 | 543:55 | 271:57 | 97.4894 | 96.2969
20 | RANEBENNUR | 10 | 10 | 30:32 | 126:56 | 49:18 | 19:35 | 68:53 | 1480:39 | 99:25 | 9:56 | 99.0741 | 98.6638 | 1607:35 | 160:46 | 97.9839 | 97.811
21 | TUMINAKATTI | 1 | 1 | 2:25 | 19:05 | 24:55 | 0:15 | 25:10 | 162:35 | 27:35 | 27:35 | 96.6174 | 96.2926 | 181:40 | 181:40 | 97.7862 | 97.5263
22 | RATTIHALLI | 1 | 1 | 2:25 | 17:30 | 14:40 | 0:45 | 15:25 | 206:00 | 17:50 | 17:50 | 97.9279 | 97.603 | 223:30 | 223:30 | 97.195 | 96.9567
23 | HIREKERUR | 1 | 1 | 1:35 | 15:35 | 18:35 | 3:50 | 22:25 | 206:50 | 24:00 | 24:00 | 96.987 | 96.7742 | 222:25 | 222:25 | 97.1836 | 96.9715
24 | BYADAGI | 5 | 5 | 17:25 | 174:56 | 20:05 | 15:25 | 35:30 | 1251:00 | 52:55 | 10:35 | 99.0457 | 98.5775 | 1425:56 | 285:11 | 96.5931 | 96.1167
25 | SIRSI | 6 | 6 | 6:34 | 194:33 | 58:50 | 10:35 | 69:25 | 919:36 | 75:59 | 12:40 | 98.445 | 98.2979 | 1114:09 | 185:42 | 97.913 | 97.4715
26 | YELLAPUR | 1 | 1 | 5:30 | 61:40 | 5:20 | 5:45 | 11:05 | 125:58 | 16:35 | 16:35 | 98.5103 | 97.7711 | 187:38 | 187:38 | 98.2848 | 97.4451
27 | MUNDAGOD | 2 | 2 | 2:16 | 11:54 | 3:00 | 1:40 | 4:40 | 131:42 | 6:56 | 3:28 | 99.6864 | 99.5341 | 143:36 | 71:48 | 99.1033 | 99.0223
28 | SIDDAPUR | 2 | 2 | 4:20 | 55:15 | 4:10 | 2:35 | 6:45 | 282:22 | 11:05 | 5:32 | 99.5464 | 99.2552 | 337:37 | 168:48 | 98.0776 | 97.7014
29 | DANDELI | 8 | 8 | 9:52 | 565:30 | 9:50 | 9:45 | 19:35 | 1217:23 | 29:27 | 3:41 | 99.671 | 99.5052 | 1782:53 | 222:52 | 97.9279 | 96.9654
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 5:10 | 4:50 | 10:00 | 192:35 | 10:00 | 5:00 | 99.328 | 99.328 | 192:35 | 96:18 | 98.6888 | 98.6888
31 | ANKOLA | 2 | 2 | 19:30 | 196:08 | 4:13 | 8:12 | 12:25 | 196:55 | 31:55 | 15:58 | 99.1655 | 97.8551 | 393:03 | 196:32 | 98.6593 | 97.324
32 | KUMTA | 3 | 3 | 1:18 | 29:24 | 14:58 | 16:20 | 31:18 | 513:50 | 32:36 | 10:52 | 98.5977 | 98.5394 | 543:14 | 181:05 | 97.6678 | 97.5343
33 | GOKARNA | 1 | 1 | 3:09 | 281:09 | 2:05 | 0:10 | 2:15 | 45:15 | 5:24 | 5:24 | 99.6976 | 99.2742 | 326:24 | 326:24 | 99.3839 | 95.5556
34 | HONNAVAR | 3 | 3 | 1:18 | 65:00 | 15:32 | 11:45 | 27:17 | 401:58 | 28:35 | 9:32 | 98.7776 | 98.7194 | 466:58 | 155:39 | 98.1755 | 97.8805
35 | BHATKAL | 3 | 3 | 10:04 | 90:16 | 24:17 | 10:46 | 35:03 | 319:18 | 45:07 | 15:02 | 98.4297 | 97.9786 | 409:34 | 136:31 | 98.5507 | 98.141
36 | KHANAPUR | 2 | 2 | 4:40 | 60:05 | 26:10 | 35:05 | 61:15 | 413:25 | 65:55 | 32:58 | 95.8837 | 95.5701 | 473:30 | 236:45 | 97.1853 | 96.7763
37 | BAILHONGAL | 3 | 3 | 6:15 | 14:51 | 11:10 | 6:00 | 17:10 | 445:40 | 23:25 | 7:48 | 99.2309 | 98.9509 | 460:31 | 153:30 | 97.9772 | 97.9098
38 | KITTUR | 3 | 3 | 1:05 | 21:55 | 13:45 | 4:55 | 18:40 | 454:15 | 19:45 | 6:35 | 99.1637 | 99.1151 | 476:10 | 158:43 | 97.9382 | 97.8387
39 | M K HUBLI | 1 | 1 | 0:00 | 1:50 | 9:10 | 3:10 | 12:20 | 236:20 | 12:20 | 12:20 | 98.3423 | 98.3423 | 238:10 | 238:10 | 96.782 | 96.757
40 | SOUNDATTI | 3 | 3 | 0:55 | 54:12 | 5:18 | 10:51 | 16:09 | 225:57 | 17:04 | 5:41 | 99.2764 | 99.2354 | 280:09 | 93:23 | 98.9744 | 98.7284
41 | MUNAVALLI | 1 | 1 | 0:00 | 59:20 | 13:35 | 1:30 | 15:05 | 380:05 | 15:05 | 15:05 | 97.9727 | 97.9727 | 439:25 | 439:25 | 94.8246 | 94.0167
42 | YARAGATTI | 1 | 1 | 0:42 | 35:34 | 25:25 | 1:29 | 26:54 | 382:50 | 27:36 | 27:36 | 96.3844 | 96.2903 | 418:24 | 418:24 | 94.7871 | 94.3028
43 | RAMDURG | 2 | 2 | 0:10 | 72:35 | 10:25 | 2:20 | 12:45 | 257:11 | 12:55 | 6:28 | 99.1431 | 99.1319 | 329:46 | 164:53 | 98.249 | 97.7549
44 | GOKAK | 10 | 10 | 17:12 | 145:48 | 4:54 | 5:28 | 10:22 | 469:00 | 27:34 | 2:45 | 99.8607 | 99.6295 | 614:48 | 61:29 | 99.3614 | 99.1629
45 | MUDALAGI | 2 | 2 | 4:15 | 23:10 | 28:50 | 4:35 | 33:25 | 287:10 | 37:40 | 18:50 | 97.7543 | 97.4686 | 310:20 | 155:10 | 98.0449 | 97.8872
46 | KONNUR | 1 | 1 | 1:18 | 5:19 | 2:30 | 1:25 | 3:55 | 178:56 | 5:13 | 5:13 | 99.4736 | 99.2988 | 184:15 | 184:15 | 97.5635 | 97.4911
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 25:05 | 1:10 | 26:15 | 339:27 | 26:15 | 26:15 | 96.4718 | 96.4718 | 339:27 | 339:27 | 95.3779 | 95.3779
48 | KUDACHI | 1 | 1 | 1:10 | 3:45 | 16:30 | 3:10 | 19:40 | 300:55 | 20:50 | 20:50 | 97.3566 | 97.1998 | 304:40 | 304:40 | 95.9026 | 95.8515
49 | ATHANI | 7 | 7 | 19:06 | 332:48 | 69:24 | 18:27 | 87:51 | 2028:52 | 106:57 | 15:17 | 98.3132 | 97.9464 | 2361:40 | 337:23 | 96.0534 | 95.406
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 18:40 | 1:05 | 19:45 | 606:26 | 19:45 | 4:56 | 99.3364 | 99.3364 | 606:26 | 151:36 | 97.9356 | 97.9356
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 47:05 | 11:50 | 58:55 | 780:15 | 58:55 | 11:47 | 98.4162 | 98.4162 | 780:15 | 156:03 | 97.8751 | 97.8751
52 | SADALAGA | 1 | 1 | 0:00 | 27:20 | 13:05 | 0:55 | 14:00 | 202:56 | 14:00 | 14:00 | 98.1183 | 98.1183 | 230:16 | 230:16 | 97.2367 | 96.8646
53 | MUDDEBIHAL | 2 | 2 | 18:20 | 138:00 | 47:20 | 3:00 | 50:20 | 531:17 | 68:40 | 34:20 | 96.6174 | 95.3853 | 669:17 | 334:38 | 96.3829 | 95.4433
54 | TALIKOTI | 1 | 1 | 8:15 | 93:50 | 10:30 | 7:00 | 17:30 | 339:20 | 25:45 | 25:45 | 97.6478 | 96.539 | 433:10 | 433:10 | 95.3794 | 94.1018
55 | B.BAGEWADI | 2 | 2 | 1:02 | 23:13 | 3:44 | 0:40 | 4:24 | 148:29 | 5:26 | 2:43 | 99.7043 | 99.6349 | 171:42 | 85:51 | 98.9891 | 98.831
56 | INDI | 3 | 3 | 0:00 | 80:06 | 8:10 | 4:45 | 12:55 | 297:40 | 12:55 | 4:18 | 99.4213 | 99.4213 | 377:46 | 125:55 | 98.6489 | 98.2854
57 | SINDAGI | 2 | 2 | 0:50 | 32:35 | 23:40 | 0:30 | 24:10 | 591:25 | 25:00 | 12:30 | 98.3759 | 98.3199 | 624:00 | 312:00 | 95.9735 | 95.7516
58 | GULEDGUDDA | 2 | 2 | 0:00 | 62:09 | 1:45 | 4:10 | 5:55 | 266:31 | 5:55 | 2:58 | 99.6024 | 99.6024 | 328:40 | 164:20 | 98.1855 | 97.7623
59 | ILKAL | 7 | 7 | 0:00 | 63:31 | 31:40 | 26:26 | 58:06 | 1526:48 | 58:06 | 8:18 | 98.8844 | 98.8844 | 1590:19 | 227:11 | 97.03 | 96.9065
60 | KERUR | 1 | 1 | 0:00 | 15:42 | 7:41 | 2:42 | 10:23 | 183:23 | 10:23 | 10:23 | 98.6044 | 98.6044 | 199:05 | 199:05 | 97.503 | 97.2892
61 | HUNGUND | 4 | 4 | 4:20 | 67:27 | 11:13 | 16:23 | 27:36 | 746:02 | 31:56 | 7:59 | 99.0726 | 98.927 | 813:29 | 203:22 | 97.4604 | 97.2308
62 | BADAMI | 2 | 2 | 0:00 | 18:32 | 17:16 | 7:45 | 25:01 | 323:31 | 25:01 | 12:30 | 98.3188 | 98.3188 | 342:03 | 171:02 | 97.7974 | 97.6712
63 | JAMKHANDI | 6 | 6 | 7:10 | 204:48 | 34:50 | 4:35 | 39:25 | 814:05 | 46:35 | 7:46 | 99.117 | 98.9565 | 1018:53 | 169:49 | 98.1525 | 97.6877
64 | MAHALINGAPUR | 2 | 2 | 1:38 | 14:53 | 22:15 | 4:15 | 26:30 | 504:57 | 28:08 | 14:04 | 98.2191 | 98.1093 | 519:50 | 259:55 | 96.5622 | 96.4608
65 | RABAKAVI | 2 | 2 | 1:30 | 38:35 | 9:15 | 1:40 | 10:55 | 191:05 | 12:25 | 6:13 | 99.2664 | 99.1655 | 229:40 | 114:50 | 98.6991 | 98.4364
66 | BANAHATTI | 2 | 2 | 1:20 | 34:52 | 7:31 | 2:10 | 9:41 | 256:21 | 11:01 | 5:30 | 99.3492 | 99.2596 | 291:13 | 145:36 | 98.2547 | 98.0173
67 | TERDAL | 2 | 2 | 0:55 | 42:55 | 9:50 | 1:25 | 11:15 | 486:35 | 12:10 | 6:05 | 99.244 | 99.1823 | 529:30 | 264:45 | 96.6872 | 96.395
68 | MUDHOL | 4 | 4 | 4:16 | 99:10 | 38:36 | 6:54 | 45:30 | 710:56 | 49:46 | 12:26 | 98.4711 | 98.3277 | 810:06 | 202:32 | 97.5799 | 97.2423
69 | BILAGI | 1 | 1 | 1:45 | 38:13 | 11:45 | 1:30 | 13:15 | 158:42 | 15:00 | 15:00 | 98.2191 | 97.9839 | 196:55 | 196:55 | 97.8391 | 97.3187
70 | LOKAPUR | 2 | 2 | 0:00 | 2:56 | 47:50 | 1:50 | 49:40 | 686:46 | 49:40 | 24:50 | 96.6622 | 96.6622 | 689:42 | 344:51 | 95.3243 | 95.3043
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of FEBRUARY-2024
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of February-24 |  |  |  | Reliability for cumulative period from Apr-23 to Feb-24
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 84 | 83 | 103:21 | 658:27 | 361:20 | 127:06 | 488:26 | 6120:46 | 591:47 | 7:03 | 99.1646 | 98.9878 | 6779:13 | 80:42 | 99.0937 | 98.9962
2 | DHARWAD (RURAL) | 13 | 13 | 0:25 | 34:42 | 108:39 | 28:49 | 137:28 | 2390:56 | 137:53 | 10:36 | 98.4807 | 98.4761 | 2425:38 | 186:35 | 97.7125 | 97.6793
3 | KUNDAGOL | 1 | 1 | 10:41 | 151:14 | 4:41 | 2:16 | 6:57 | 78:20 | 17:38 | 17:38 | 99.0014 | 97.4665 | 229:34 | 229:34 | 99.0257 | 97.1447
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 9:28 | 1:52 | 11:20 | 141:11 | 11:20 | 11:20 | 98.3716 | 98.3716 | 141:11 | 141:11 | 98.244 | 98.244
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 10:55 | 3:58 | 14:53 | 149:33 | 14:53 | 14:53 | 97.8616 | 97.8616 | 149:33 | 149:33 | 98.1399 | 98.1399
6 | KALGHATAGI | 2 | 2 | 0:00 | 7:50 | 53:10 | 10:15 | 63:25 | 395:15 | 63:25 | 31:42 | 95.4442 | 95.4442 | 403:05 | 201:32 | 97.542 | 97.4933
7 | ALNAVAR | 2 | 2 | 5:40 | 29:40 | 20:30 | 1:10 | 21:40 | 193:20 | 27:20 | 13:40 | 98.4435 | 98.0364 | 223:00 | 111:30 | 98.7977 | 98.6132
8 | NARAGUND | 2 | 2 | 1:20 | 57:10 | 14:20 | 20:45 | 35:05 | 415:45 | 36:25 | 18:12 | 97.4796 | 97.3839 | 472:55 | 236:28 | 97.4145 | 97.059
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 1:31 | 4:33 | 6:04 | 208:48 | 6:04 | 6:04 | 99.1284 | 99.1284 | 208:48 | 208:48 | 97.403 | 97.403
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 50:15 | 13:37 | 63:52 | 558:28 | 63:52 | 21:17 | 96.9413 | 96.9413 | 558:28 | 186:09 | 97.6846 | 97.6846
11 | NAREGAL | 1 | 1 | 0:00 | 12:50 | 25:00 | 1:10 | 26:10 | 112:55 | 26:10 | 26:10 | 96.2404 | 96.2404 | 125:45 | 125:45 | 98.5956 | 98.4359
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 26:05 | 6:10 | 32:15 | 276:20 | 32:15 | 16:08 | 97.6832 | 97.6832 | 276:20 | 138:10 | 98.2815 | 98.2815
13 | RON | 3 | 3 | 0:00 | 0:00 | 40:40 | 2:04 | 42:44 | 415:52 | 42:44 | 14:15 | 97.9534 | 97.9534 | 415:52 | 138:37 | 98.2758 | 98.2758
14 | MUNDARAGI | 1 | 1 | 0:00 | 26:13 | 10:00 | 3:35 | 13:35 | 221:25 | 13:35 | 13:35 | 98.0484 | 98.0484 | 247:38 | 247:38 | 97.2461 | 96.92
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 18:15 | 1:10 | 19:25 | 572:05 | 19:25 | 19:25 | 97.2102 | 97.2102 | 572:05 | 572:05 | 92.8845 | 92.8845
16 | SAVANUR | 2 | 2 | 0:00 | 17:40 | 4:10 | 4:35 | 8:45 | 316:55 | 8:45 | 4:22 | 99.3714 | 99.3714 | 334:35 | 167:18 | 98.0291 | 97.9193
17 | SHIGGAON | 3 | 3 | 3:35 | 134:00 | 10:25 | 3:40 | 14:05 | 253:15 | 17:40 | 5:53 | 99.3255 | 99.1539 | 387:15 | 129:05 | 98.95 | 98.3945
18 | BANKAPUR | 1 | 1 | 2:20 | 100:10 | 9:45 | 6:20 | 16:05 | 223:15 | 18:25 | 18:25 | 97.6892 | 97.3539 | 323:25 | 323:25 | 97.2233 | 95.9774
19 | HANGAL | 2 | 2 | 9:20 | 184:30 | 26:05 | 3:25 | 29:30 | 398:15 | 38:50 | 19:25 | 97.8807 | 97.2102 | 582:45 | 291:22 | 97.5233 | 96.3759
20 | RANEBENNUR | 10 | 10 | 31:22 | 158:18 | 113:33 | 2:03 | 115:36 | 1596:15 | 146:58 | 14:42 | 98.3391 | 97.8884 | 1754:33 | 175:27 | 98.0146 | 97.8177
21 | TUMINAKATTI | 1 | 1 | 14:50 | 33:55 | 6:30 | 0:02 | 6:32 | 169:07 | 21:22 | 21:22 | 99.0613 | 96.9301 | 203:02 | 203:02 | 97.8966 | 97.4747
22 | RATTIHALLI | 1 | 1 | 14:50 | 32:20 | 20:50 | 0:04 | 20:54 | 226:54 | 35:44 | 35:44 | 96.9971 | 94.8659 | 259:14 | 259:14 | 97.1779 | 96.7757
23 | HIREKERUR | 1 | 1 | 5:35 | 21:10 | 18:25 | 0:21 | 18:46 | 225:36 | 24:21 | 24:21 | 97.3036 | 96.5014 | 246:46 | 246:46 | 97.194 | 96.9308
24 | BYADAGI | 5 | 5 | 15:51 | 190:47 | 38:10 | 0:44 | 38:54 | 1289:54 | 54:45 | 10:57 | 98.8822 | 98.4267 | 1480:41 | 296:08 | 96.7913 | 96.3167
25 | SIRSI | 6 | 6 | 4:54 | 199:27 | 66:55 | 20:05 | 87:00 | 1006:36 | 91:54 | 15:19 | 97.9167 | 97.7993 | 1206:03 | 201:00 | 97.9133 | 97.4999
26 | YELLAPUR | 1 | 1 | 8:15 | 69:55 | 0:50 | 1:00 | 1:50 | 127:48 | 10:05 | 10:05 | 99.7366 | 98.5512 | 197:43 | 197:43 | 98.4104 | 97.5408
27 | MUNDAGOD | 2 | 2 | 1:50 | 13:44 | 6:15 | 2:55 | 9:10 | 140:52 | 11:00 | 5:30 | 99.3415 | 99.2098 | 154:36 | 77:18 | 99.124 | 99.0386
28 | SIDDAPUR | 3 | 3 | 20:00 | 75:15 | 76:20 | 2:55 | 79:15 | 361:37 | 99:15 | 33:05 | 96.2045 | 95.2466 | 436:52 | 145:37 | 98.5008 | 98.1888
29 | DANDELI | 8 | 8 | 4:40 | 570:10 | 48:49 | 3:44 | 52:33 | 1269:56 | 57:13 | 7:09 | 99.0562 | 98.9724 | 1840:06 | 230:01 | 98.0256 | 97.1391
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 15:20 | 2:05 | 17:25 | 210:00 | 17:25 | 8:42 | 98.7488 | 98.7488 | 210:00 | 105:00 | 98.694 | 98.694
31 | ANKOLA | 2 | 2 | 13:50 | 209:58 | 5:20 | 4:18 | 9:38 | 206:33 | 23:28 | 11:44 | 99.308 | 98.3142 | 416:31 | 208:16 | 98.7155 | 97.4097
32 | KUMTA | 3 | 3 | 6:12 | 35:36 | 16:11 | 3:37 | 19:48 | 533:38 | 26:00 | 8:40 | 99.0517 | 98.7548 | 569:14 | 189:45 | 97.7876 | 97.64
33 | GOKARNA | 1 | 1 | 10:26 | 291:35 | 4:00 | 0:25 | 4:25 | 49:40 | 14:51 | 14:51 | 99.3654 | 97.8664 | 341:15 | 341:15 | 99.3823 | 95.7556
34 | HONNAVAR | 3 | 3 | 6:12 | 71:12 | 19:35 | 6:04 | 25:39 | 427:37 | 31:51 | 10:37 | 98.7716 | 98.4746 | 498:49 | 166:16 | 98.2271 | 97.9319
35 | BHATKAL | 3 | 3 | 0:48 | 91:04 | 14:42 | 2:31 | 17:13 | 336:31 | 18:01 | 6:00 | 99.1754 | 99.1371 | 427:35 | 142:32 | 98.6048 | 98.2273
36 | KHANAPUR | 2 | 2 | 0:00 | 60:05 | 69:45 | 4:50 | 74:35 | 488:00 | 74:35 | 37:18 | 94.642 | 94.642 | 548:05 | 274:02 | 96.9652 | 96.5915
37 | BAILHONGAL | 3 | 3 | 0:00 | 14:51 | 33:20 | 9:30 | 42:50 | 488:30 | 42:50 | 14:17 | 97.9486 | 97.9486 | 503:21 | 167:47 | 97.9747 | 97.9131
38 | KITTUR | 3 | 3 | 0:10 | 22:05 | 48:25 | 2:35 | 51:00 | 505:15 | 51:10 | 17:03 | 97.5575 | 97.5495 | 527:20 | 175:47 | 97.9053 | 97.8137
39 | M K HUBLI | 1 | 1 | 0:00 | 1:50 | 10:55 | 1:35 | 12:30 | 248:50 | 12:30 | 12:30 | 98.204 | 98.204 | 250:40 | 250:40 | 96.9051 | 96.8823
40 | SOUNDATTI | 3 | 3 | 3:38 | 57:50 | 10:05 | 0:50 | 10:55 | 236:52 | 14:33 | 4:51 | 99.4772 | 99.3032 | 294:42 | 98:14 | 99.018 | 98.7782
41 | MUNAVALLI | 1 | 1 | 0:35 | 59:55 | 13:40 | 1:35 | 15:15 | 395:20 | 15:50 | 15:50 | 97.8089 | 97.7251 | 455:15 | 455:15 | 95.0829 | 94.3377
42 | YARAGATTI | 1 | 1 | 6:38 | 42:12 | 27:26 | 10:14 | 37:40 | 420:30 | 44:18 | 44:18 | 94.5881 | 93.6351 | 462:42 | 462:42 | 94.7699 | 94.245
43 | RAMDURG | 2 | 2 | 1:28 | 74:03 | 15:30 | 1:40 | 17:10 | 274:21 | 18:38 | 9:19 | 98.7668 | 98.6614 | 348:24 | 174:12 | 98.2938 | 97.8333
44 | GOKAK | 10 | 10 | 13:04 | 158:52 | 10:17 | 2:41 | 12:58 | 481:58 | 26:02 | 2:36 | 99.8137 | 99.626 | 640:50 | 64:05 | 99.4005 | 99.2029
45 | MUDALAGI | 2 | 2 | 1:00 | 24:10 | 14:30 | 8:50 | 23:20 | 310:30 | 24:20 | 12:10 | 98.3238 | 98.2519 | 334:40 | 167:20 | 98.069 | 97.9187
46 | KONNUR | 1 | 1 | 0:00 | 5:19 | 3:30 | 2:50 | 6:20 | 185:16 | 6:20 | 6:20 | 99.09 | 99.09 | 190:35 | 190:35 | 97.6957 | 97.6296
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 17:45 | 2:35 | 20:20 | 359:47 | 20:20 | 20:20 | 97.0785 | 97.0785 | 359:47 | 359:47 | 95.5251 | 95.5251
48 | KUDACHI | 1 | 1 | 0:15 | 4:00 | 29:25 | 1:30 | 30:55 | 331:50 | 31:10 | 31:10 | 95.558 | 95.522 | 335:50 | 335:50 | 95.8727 | 95.823
49 | ATHANI | 7 | 7 | 48:24 | 381:12 | 71:30 | 25:19 | 96:49 | 2125:41 | 145:13 | 20:45 | 98.0128 | 97.0194 | 2506:53 | 358:08 | 96.223 | 95.5457
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 35:10 | 1:35 | 36:45 | 643:11 | 36:45 | 9:11 | 98.68 | 98.68 | 643:11 | 160:48 | 98.0001 | 98.0001
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 73:45 | 12:05 | 85:50 | 866:05 | 85:50 | 17:10 | 97.5335 | 97.5335 | 866:05 | 173:13 | 97.8456 | 97.8456
52 | SADALAGA | 1 | 1 | 0:00 | 27:20 | 23:05 | 2:15 | 25:20 | 228:16 | 25:20 | 25:20 | 96.3602 | 96.3602 | 255:36 | 255:36 | 97.1609 | 96.8209
53 | MUDDEBIHAL | 2 | 2 | 0:00 | 138:00 | 25:15 | 3:20 | 28:35 | 559:52 | 28:35 | 14:17 | 97.9466 | 97.9466 | 697:52 | 348:56 | 96.5182 | 95.66
54 | TALIKOTI | 1 | 1 | 5:40 | 99:30 | 16:25 | 7:00 | 23:25 | 362:45 | 29:05 | 29:05 | 96.6355 | 95.8214 | 462:15 | 462:15 | 95.4882 | 94.2506
55 | B.BAGEWADI | 2 | 2 | 1:50 | 25:03 | 3:35 | 1:23 | 4:58 | 153:27 | 6:48 | 3:24 | 99.6432 | 99.5115 | 178:30 | 89:15 | 99.0457 | 98.8899
56 | INDI | 3 | 3 | 22:55 | 103:01 | 7:58 | 4:06 | 12:04 | 309:44 | 34:59 | 11:40 | 99.4221 | 98.3246 | 412:45 | 137:35 | 98.7159 | 98.2888
57 | SINDAGI | 2 | 2 | 12:50 | 45:25 | 18:55 | 0:25 | 19:20 | 610:45 | 32:10 | 16:05 | 98.6111 | 97.6892 | 656:10 | 328:05 | 96.2018 | 95.9194
58 | GULEDGUDDA | 2 | 2 | 0:48 | 62:57 | 62:40 | 7:38 | 70:18 | 336:49 | 71:06 | 35:33 | 94.9497 | 94.8922 | 399:46 | 199:53 | 97.9054 | 97.5139
59 | ILKAL | 7 | 7 | 5:57 | 69:28 | 13:21 | 23:23 | 36:44 | 1563:32 | 42:41 | 6:06 | 99.246 | 99.1239 | 1633:00 | 233:17 | 97.2219 | 97.0984
60 | KERUR | 1 | 1 | 0:20 | 16:02 | 8:50 | 3:21 | 12:11 | 195:34 | 12:31 | 12:31 | 98.2495 | 98.2016 | 211:36 | 211:36 | 97.5676 | 97.3682
61 | HUNGUND | 4 | 4 | 3:12 | 70:39 | 112:20 | 25:15 | 137:35 | 883:37 | 140:47 | 35:12 | 95.0581 | 94.9431 | 954:16 | 238:34 | 97.2524 | 97.0328
62 | BADAMI | 2 | 2 | 0:20 | 18:52 | 8:46 | 4:23 | 13:09 | 336:40 | 13:29 | 6:44 | 99.0553 | 99.0314 | 355:32 | 177:46 | 97.9063 | 97.789
63 | JAMKHANDI | 6 | 6 | 4:00 | 208:48 | 21:45 | 3:40 | 25:25 | 839:30 | 29:25 | 4:54 | 99.3914 | 99.2956 | 1048:18 | 174:43 | 98.2597 | 97.8269
64 | MAHALINGAPUR | 2 | 2 | 0:46 | 15:39 | 37:15 | 2:00 | 39:15 | 544:12 | 40:01 | 20:00 | 97.1803 | 97.1252 | 559:51 | 279:56 | 96.6157 | 96.5183
65 | RABAKAVI | 2 | 2 | 3:20 | 41:55 | 12:35 | 0:55 | 13:30 | 204:35 | 16:50 | 8:25 | 99.0302 | 98.7907 | 246:30 | 123:15 | 98.7277 | 98.467
66 | BANAHATTI | 2 | 2 | 0:30 | 35:22 | 3:20 | 0:40 | 4:00 | 260:21 | 4:30 | 2:15 | 99.7126 | 99.6767 | 295:43 | 147:51 | 98.3809 | 98.161
67 | TERDAL | 2 | 2 | 1:00 | 43:55 | 14:50 | 2:15 | 17:05 | 503:40 | 18:05 | 9:02 | 98.7727 | 98.7009 | 547:35 | 273:47 | 96.8677 | 96.5946
68 | MUDHOL | 4 | 4 | 2:15 | 101:25 | 56:09 | 25:14 | 81:23 | 792:19 | 83:38 | 20:54 | 97.0767 | 96.9959 | 893:44 | 223:26 | 97.5363 | 97.221
69 | BILAGI | 1 | 1 | 0:15 | 38:28 | 11:50 | 2:45 | 14:35 | 173:17 | 14:50 | 14:50 | 97.9047 | 97.8688 | 211:45 | 211:45 | 97.8447 | 97.3663
70 | LOKAPUR | 2 | 2 | 0:00 | 2:56 | 36:00 | 2:45 | 38:45 | 725:31 | 38:45 | 19:22 | 97.2162 | 97.2162 | 728:27 | 364:13 | 95.4881 | 95.4698
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of MARCH-2024
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of March-24 |  |  |  | Reliability for cumulative period from Apr-23 to Mar-24
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 85 | 85 | 19:43 | 678:10 | 283:52 | 151:44 | 435:36 | 6556:22 | 455:19 | 5:21 | 99.3112 | 99.28 | 7234:32 | 85:07 | 99.1219 | 99.0311
2 | DHARWAD (RURAL) | 13 | 13 | 0:40 | 35:22 | 132:38 | 40:04 | 172:42 | 2563:38 | 173:22 | 13:20 | 98.2144 | 98.2075 | 2599:00 | 199:55 | 97.755 | 97.724
3 | KUNDAGOL | 1 | 1 | 1:23 | 152:37 | 5:50 | 1:11 | 7:01 | 85:21 | 8:24 | 8:24 | 99.0569 | 98.871 | 237:58 | 237:58 | 99.0283 | 97.2909
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 2:32 | 2:32 | 5:04 | 146:15 | 5:04 | 5:04 | 99.319 | 99.319 | 146:15 | 146:15 | 98.335 | 98.335
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 5:50 | 3:43 | 9:33 | 159:06 | 9:33 | 9:33 | 98.7164 | 98.7164 | 159:06 | 159:06 | 98.1888 | 98.1888
6 | KALGHATAGI | 2 | 2 | 0:00 | 7:50 | 12:50 | 2:50 | 15:40 | 410:55 | 15:40 | 7:50 | 98.9471 | 98.9471 | 418:45 | 209:22 | 97.661 | 97.6164
7 | ALNAVAR | 2 | 2 | 4:40 | 34:20 | 19:30 | 3:00 | 22:30 | 215:50 | 27:10 | 13:35 | 98.4879 | 98.1743 | 250:10 | 125:05 | 98.7714 | 98.576
8 | NARAGUND | 2 | 2 | 4:00 | 61:10 | 31:25 | 8:10 | 39:35 | 455:20 | 43:35 | 21:48 | 97.3398 | 97.071 | 516:30 | 258:15 | 97.4082 | 97.06
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 5:55 | 1:00 | 6:55 | 215:43 | 6:55 | 6:55 | 99.0703 | 99.0703 | 215:43 | 215:43 | 97.5442 | 97.5442
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 17:25 | 6:12 | 23:37 | 582:05 | 23:37 | 7:52 | 98.9419 | 98.9419 | 582:05 | 194:02 | 97.7911 | 97.7911
11 | NAREGAL | 1 | 1 | 0:00 | 12:50 | 2:20 | 1:10 | 3:30 | 116:25 | 3:30 | 3:30 | 99.5296 | 99.5296 | 129:15 | 129:15 | 98.6747 | 98.5286
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 18:10 | 3:45 | 21:55 | 298:15 | 21:55 | 10:58 | 98.5271 | 98.5271 | 298:15 | 149:08 | 98.3023 | 98.3023
13 | RON | 3 | 3 | 0:00 | 0:00 | 11:35 | 6:50 | 18:25 | 434:17 | 18:25 | 6:08 | 99.1749 | 99.1749 | 434:17 | 144:46 | 98.352 | 98.352
14 | MUNDARAGI | 1 | 1 | 0:00 | 26:13 | 13:30 | 3:25 | 16:55 | 238:20 | 16:55 | 16:55 | 97.7263 | 97.7263 | 264:33 | 264:33 | 97.2867 | 96.9883
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 7:00 | 5:45 | 12:45 | 584:50 | 12:45 | 12:45 | 98.2863 | 98.2863 | 584:50 | 584:50 | 93.3421 | 93.3421
16 | SAVANUR | 2 | 2 | 0:00 | 17:40 | 19:10 | 4:25 | 23:35 | 340:30 | 23:35 | 11:48 | 98.4151 | 98.4151 | 358:10 | 179:05 | 98.0618 | 97.9613
17 | SHIGGAON | 3 | 3 | 21:25 | 155:25 | 18:40 | 6:40 | 25:20 | 278:35 | 46:45 | 15:35 | 98.865 | 97.9055 | 434:00 | 144:40 | 98.9428 | 98.3531
18 | BANKAPUR | 1 | 1 | 2:20 | 102:30 | 4:15 | 6:45 | 11:00 | 234:15 | 13:20 | 13:20 | 98.5215 | 98.2079 | 336:45 | 336:45 | 97.3332 | 96.1663
19 | HANGAL | 2 | 2 | 1:00 | 185:30 | 26:45 | 24:55 | 51:40 | 449:55 | 52:40 | 26:20 | 96.5278 | 96.4606 | 635:25 | 317:42 | 97.439 | 96.3831
20 | RANEBENNUR | 10 | 10 | 7:50 | 166:08 | 96:10 | 19:07 | 115:17 | 1711:32 | 123:07 | 12:19 | 98.4505 | 98.3452 | 1877:40 | 187:46 | 98.0515 | 97.8624
21 | TUMINAKATTI | 1 | 1 | 2:50 | 36:45 | 5:25 | 0:00 | 5:25 | 174:32 | 8:15 | 8:15 | 99.272 | 98.8911 | 211:17 | 211:17 | 98.0131 | 97.5947
22 | RATTIHALLI | 1 | 1 | 2:05 | 34:25 | 10:25 | 1:05 | 11:30 | 238:24 | 13:35 | 13:35 | 98.4543 | 98.1743 | 272:49 | 272:49 | 97.286 | 96.8942
23 | HIREKERUR | 1 | 1 | 2:40 | 23:50 | 11:00 | 1:40 | 12:40 | 238:16 | 15:20 | 15:20 | 98.2975 | 97.9391 | 262:06 | 262:06 | 97.2875 | 97.0162
24 | BYADAGI | 5 | 5 | 10:30 | 201:17 | 74:30 | 8:30 | 83:00 | 1372:54 | 93:30 | 18:42 | 97.7688 | 97.4866 | 1574:11 | 314:50 | 96.8741 | 96.4158
25 | SIRSI | 6 | 6 | 6:34 | 206:01 | 49:31 | 12:02 | 61:33 | 1068:09 | 68:07 | 11:21 | 98.6212 | 98.4741 | 1274:10 | 212:22 | 97.9733 | 97.5824
26 | YELLAPUR | 1 | 1 | 9:20 | 79:15 | 9:35 | 2:40 | 12:15 | 140:03 | 21:35 | 21:35 | 98.3535 | 97.099 | 219:18 | 219:18 | 98.4056 | 97.5034
27 | MUNDAGOD | 2 | 2 | 0:00 | 13:44 | 15:25 | 1:45 | 17:10 | 158:02 | 17:10 | 8:35 | 98.8463 | 98.8463 | 171:46 | 85:53 | 99.1004 | 99.0223
28 | SIDDAPUR | 3 | 3 | 24:30 | 99:45 | 10:35 | 7:05 | 17:40 | 379:17 | 42:10 | 14:03 | 99.2085 | 98.1108 | 479:02 | 159:41 | 98.5607 | 98.1822
29 | DANDELI | 8 | 8 | 4:40 | 574:50 | 48:49 | 3:44 | 52:33 | 1322:29 | 57:13 | 7:09 | 99.1171 | 99.0387 | 1897:19 | 237:10 | 98.1181 | 97.3
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 12:35 | 4:30 | 17:05 | 227:05 | 17:05 | 8:32 | 98.8519 | 98.8519 | 227:05 | 113:32 | 98.7074 | 98.7074
31 | ANKOLA | 2 | 2 | 0:00 | 209:58 | 6:38 | 4:07 | 10:45 | 217:18 | 10:45 | 5:22 | 99.2776 | 99.2776 | 427:16 | 213:38 | 98.7631 | 97.5679
32 | KUMTA | 3 | 3 | 6:45 | 42:21 | 9:40 | 6:44 | 16:24 | 550:02 | 23:09 | 7:43 | 99.2652 | 98.9628 | 592:23 | 197:28 | 97.9127 | 97.752
33 | GOKARNA | 1 | 1 | 0:48 | 292:23 | 0:45 | 0:00 | 0:45 | 50:25 | 1:33 | 1:33 | 99.8992 | 99.7917 | 342:48 | 342:48 | 99.426 | 96.0974
34 | HONNAVAR | 3 | 3 | 20:45 | 91:57 | 12:44 | 6:44 | 19:28 | 447:05 | 40:13 | 13:24 | 99.1278 | 98.1982 | 539:02 | 179:41 | 98.3034 | 97.9545
35 | BHATKAL | 3 | 3 | 25:23 | 116:27 | 9:53 | 9:51 | 19:44 | 356:15 | 45:07 | 15:02 | 99.1159 | 97.9786 | 472:42 | 157:34 | 98.6481 | 98.2062
36 | KHANAPUR | 2 | 2 | 22:10 | 82:15 | 56:00 | 8:25 | 64:25 | 552:25 | 86:35 | 43:18 | 95.6709 | 94.1812 | 634:40 | 317:20 | 96.8556 | 96.3874
37 | BAILHONGAL | 3 | 3 | 0:00 | 14:51 | 12:05 | 6:45 | 18:50 | 507:20 | 18:50 | 6:17 | 99.1562 | 99.1562 | 522:11 | 174:04 | 98.0748 | 98.0184
38 | KITTUR | 3 | 3 | 0:00 | 22:05 | 16:20 | 55:30 | 71:50 | 577:05 | 71:50 | 23:57 | 96.7817 | 96.7817 | 599:10 | 199:43 | 97.8101 | 97.7263
39 | M K HUBLI | 1 | 1 | 0:00 | 1:50 | 29:30 | 2:30 | 32:00 | 280:50 | 32:00 | 32:00 | 95.6989 | 95.6989 | 282:40 | 282:40 | 96.8029 | 96.782
40 | SOUNDATTI | 3 | 3 | 20:11 | 78:01 | 17:47 | 2:56 | 20:43 | 257:35 | 40:54 | 13:38 | 99.0718 | 98.1676 | 335:36 | 111:52 | 99.0225 | 98.7265
41 | MUNAVALLI | 1 | 1 | 5:35 | 65:30 | 17:35 | 2:45 | 20:20 | 415:40 | 25:55 | 25:55 | 97.267 | 96.5166 | 481:10 | 481:10 | 95.2679 | 94.5222
42 | YARAGATTI | 1 | 1 | 5:54 | 48:06 | 24:51 | 11:20 | 36:11 | 456:41 | 42:05 | 42:05 | 95.1366 | 94.3436 | 504:47 | 504:47 | 94.801 | 94.2534
43 | RAMDURG | 2 | 2 | 7:52 | 81:55 | 16:55 | 0:55 | 17:50 | 292:11 | 25:42 | 12:51 | 98.8015 | 98.2728 | 374:06 | 187:03 | 98.3368 | 97.8706
44 | GOKAK | 10 | 10 | 61:13 | 220:05 | 35:49 | 8:39 | 44:28 | 526:26 | 105:41 | 10:34 | 99.4023 | 98.5795 | 746:31 | 74:39 | 99.4007 | 99.1501
45 | MUDALAGI | 2 | 2 | 0:45 | 24:55 | 16:20 | 6:10 | 22:30 | 333:00 | 23:15 | 11:38 | 98.4879 | 98.4375 | 357:55 | 178:58 | 98.1045 | 97.9627
46 | KONNUR | 1 | 1 | 0:00 | 5:19 | 10:55 | 0:45 | 11:40 | 196:56 | 11:40 | 11:40 | 98.4319 | 98.4319 | 202:15 | 202:15 | 97.758 | 97.6975
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 23:35 | 7:10 | 30:45 | 390:32 | 30:45 | 30:45 | 95.8669 | 95.8669 | 390:32 | 390:32 | 95.554 | 95.554
48 | KUDACHI | 1 | 1 | 2:00 | 6:00 | 30:45 | 0:25 | 31:10 | 363:00 | 33:10 | 33:10 | 95.8109 | 95.5421 | 369:00 | 369:00 | 95.8675 | 95.7992
49 | ATHANI | 7 | 7 | 25:39 | 406:51 | 87:44 | 30:35 | 118:19 | 2244:00 | 143:58 | 20:34 | 97.7282 | 97.2357 | 2650:51 | 378:42 | 96.3505 | 95.6888
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 54:30 | 5:55 | 60:25 | 703:36 | 60:25 | 15:06 | 97.9699 | 97.9699 | 703:36 | 175:54 | 97.9975 | 97.9975
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 34:40 | 13:55 | 48:35 | 914:40 | 48:35 | 9:43 | 98.694 | 98.694 | 914:40 | 182:56 | 97.9174 | 97.9174
52 | SADALAGA | 1 | 1 | 0:00 | 27:20 | 6:35 | 3:30 | 10:05 | 238:21 | 10:05 | 10:05 | 98.6447 | 98.6447 | 265:41 | 265:41 | 97.2865 | 96.9754
53 | MUDDEBIHAL | 2 | 2 | 23:30 | 161:30 | 29:10 | 2:46 | 31:56 | 591:48 | 55:26 | 27:43 | 97.8539 | 96.2746 | 753:18 | 376:39 | 96.6314 | 95.7121
54 | TALIKOTI | 1 | 1 | 0:15 | 99:45 | 6:00 | 5:10 | 11:10 | 373:55 | 11:25 | 11:25 | 98.4991 | 98.4655 | 473:40 | 473:40 | 95.7432 | 94.6076
55 | B.BAGEWADI | 2 | 2 | 23:22 | 48:25 | 4:50 | 1:25 | 6:15 | 159:42 | 29:37 | 14:48 | 99.58 | 98.0096 | 208:07 | 104:04 | 99.091 | 98.8154
56 | INDI | 3 | 3 | 0:00 | 103:01 | 6:11 | 3:38 | 9:49 | 319:33 | 9:49 | 3:16 | 99.5602 | 99.5602 | 422:34 | 140:51 | 98.7874 | 98.3965
57 | SINDAGI | 2 | 2 | 0:00 | 45:25 | 35:35 | 0:50 | 36:25 | 647:10 | 36:25 | 18:12 | 97.5526 | 97.5526 | 692:35 | 346:18 | 96.3162 | 96.0577
58 | GULEDGUDDA | 2 | 2 | 7:39 | 70:36 | 28:10 | 13:52 | 42:02 | 378:51 | 49:41 | 24:50 | 97.1752 | 96.6611 | 449:27 | 224:44 | 97.8435 | 97.4417
59 | ILKAL | 7 | 7 | 0:00 | 69:28 | 66:01 | 48:21 | 114:22 | 1677:54 | 114:22 | 16:20 | 97.804 | 97.804 | 1747:22 | 249:37 | 97.2712 | 97.1582
60 | KERUR | 1 | 1 | 7:15 | 23:17 | 9:54 | 2:50 | 12:44 | 208:18 | 19:59 | 19:59 | 98.2885 | 97.3141 | 231:35 | 231:35 | 97.6286 | 97.3636
61 | HUNGUND | 4 | 4 | 0:00 | 70:39 | 53:35 | 20:51 | 74:26 | 958:03 | 74:26 | 18:36 | 97.4989 | 97.4989 | 1028:42 | 257:10 | 97.2733 | 97.0722
62 | BADAMI | 2 | 2 | 1:26 | 20:18 | 23:39 | 8:35 | 32:14 | 368:54 | 33:40 | 16:50 | 97.8338 | 97.7375 | 389:12 | 194:36 | 97.9002 | 97.7846
63 | JAMKHANDI | 6 | 6 | 2:30 | 211:18 | 90:50 | 5:40 | 96:30 | 936:00 | 99:00 | 16:30 | 97.8383 | 97.7823 | 1147:18 | 191:13 | 98.224 | 97.8231
64 | MAHALINGAPUR | 2 | 2 | 1:37 | 17:16 | 9:55 | 5:51 | 15:46 | 559:58 | 17:23 | 8:42 | 98.9404 | 98.8318 | 577:14 | 288:37 | 96.8126 | 96.7143
65 | RABAKAVI | 2 | 2 | 5:30 | 47:25 | 7:15 | 0:50 | 8:05 | 212:40 | 13:35 | 6:48 | 99.4568 | 99.0871 | 260:05 | 130:02 | 98.7895 | 98.5196
66 | BANAHATTI | 2 | 2 | 0:00 | 35:22 | 13:46 | 0:25 | 14:11 | 274:32 | 14:11 | 7:06 | 99.0468 | 99.0468 | 309:54 | 154:57 | 98.4373 | 98.236
67 | TERDAL | 2 | 2 | 0:10 | 44:05 | 13:15 | 1:50 | 15:05 | 518:45 | 15:15 | 7:38 | 98.9863 | 98.9751 | 562:50 | 281:25 | 97.0472 | 96.7963
68 | MUDHOL | 4 | 4 | 10:40 | 112:05 | 29:13 | 8:44 | 37:57 | 830:16 | 48:37 | 12:09 | 98.7248 | 98.3664 | 942:21 | 235:35 | 97.637 | 97.318
69 | BILAGI | 1 | 1 | 19:20 | 57:48 | 13:30 | 1:30 | 15:00 | 188:17 | 34:20 | 34:20 | 97.9839 | 95.3853 | 246:05 | 246:05 | 97.8565 | 97.1985
70 | LOKAPUR | 2 | 2 | 7:15 | 10:11 | 47:00 | 12:15 | 59:15 | 784:46 | 66:30 | 33:15 | 96.0181 | 95.5309 | 794:57 | 397:28 | 95.533 | 95.475
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]

## RURAL (Incl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2023
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Apr-23
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 50 | 50 | 178:08 | 178:08 | 7978:12 | 1010:20 | 8988:32 | 8988:32 | 9166:40 | 183:20 | 75.0319 | 74.537 | 9166:40 | 183:20 | 75.0319 | 74.537
2 | DHARWAD RURAL | 99 | 99 | 94:01 | 94:01 | 15372:26 | 1712:43 | 17085:09 | 17085:09 | 17179:10 | 173:32 | 76.0309 | 75.899 | 17179:10 | 173:32 | 76.0309 | 75.899
3 | GADAG | 112 | 112 | 465:32 | 465:32 | 23690:22 | 1565:44 | 1052.3375 | 1052.3375 | 1071.7347 | 229:39 | 68.6804 | 68.1031 | 1071.7347 | 229:39 | 68.6804 | 68.1031
4 | RON | 61 | 61 | 185:05 | 185:05 | 15072:23 | 1316:04 | 16388:27 | 16388:27 | 16573:32 | 271:42 | 62.6857 | 62.2643 | 16573:32 | 271:42 | 62.6857 | 62.2643
5 | HAVERI | 210 | 210 | 979:45 | 979:45 | 2706.859 | 3311:05 | 2844.8208 | 2844.8208 | 2885.6437 | 329:47 | 54.8441 | 54.1961 | 2885.6437 | 329:47 | 54.8441 | 54.1961
6 | RANEBENNUR | 212 | 212 | 878:04 | 878:04 | 2803.5271 | 2441:52 | 2905.2715 | 2905.2715 | 2941.8576 | 333:02 | 54.3196 | 53.7444 | 2941.8576 | 333:02 | 54.3196 | 53.7444
7 | SIRSI | 59 | 58 | 194:23 | 194:23 | 381:11 | 1094:40 | 1475:51 | 1475:51 | 1670:14 | 28:19 | 96.5258 | 96.0682 | 1670:14 | 28:19 | 96.5258 | 96.0682
8 | DANDELI | 27 | 27 | 101:46 | 101:46 | 754:48 | 355:24 | 1110:12 | 1110:12 | 1211:58 | 44:53 | 94.2891 | 93.7656 | 1211:58 | 44:53 | 94.2891 | 93.7656
9 | KARWAR | 31 | 31 | 147:38 | 147:38 | 209:19 | 127:07 | 336:26 | 336:26 | 484:04 | 15:37 | 98.4927 | 97.8312 | 484:04 | 15:37 | 98.4927 | 97.8312
10 | HONNAVAR | 49 | 49 | 564:27 | 564:27 | 563:22 | 325:34 | 888:56 | 888:56 | 1453:23 | 29:40 | 97.4803 | 95.8804 | 1453:23 | 29:40 | 97.4803 | 95.8804
11 | BELAGAVI RURAL | 151 | 150 | 414:09 | 414:09 | 18437:48 | 3235:08 | 21672:56 | 21672:56 | 22087:05 | 146:16 | 80.0654 | 79.6844 | 22087:05 | 146:16 | 80.0654 | 79.6844
12 | BAILHONGAL | 206 | 205 | 1550:45 | 1550:45 | 2186.5257 | 3732:19 | 2342.0389 | 2342.0389 | 2406.6535 | 280:23 | 62.1029 | 61.0574 | 2406.6535 | 280:23 | 62.1029 | 61.0574
13 | RAMDURG | 95 | 95 | 285:48 | 285:48 | 1302.4285 | 1885:12 | 1380.9785 | 1380.9785 | 1392.8868 | 351:53 | 51.5446 | 51.1268 | 1392.8868 | 351:53 | 51.5446 | 51.1268
14 | GHATAPRABHA | 179 | 179 | 314:36 | 314:36 | 1808.8451 | 2224:06 | 1901.516 | 1901.516 | 1914.6243 | 256:43 | 64.59 | 64.3459 | 1914.6243 | 256:43 | 64.59 | 64.3459
15 | RAIBAG | 183 | 179 | 333:16 | 333:16 | 1883.5389 | 910:09 | 1921.4618 | 1921.4618 | 1935.3479 | 253:49 | 65.0007 | 64.7478 | 1935.3479 | 253:49 | 65.0007 | 64.7478
16 | ATHANI | 207 | 207 | 768:52 | 768:52 | 1901.0264 | 1347:41 | 1957.1799 | 1957.1799 | 1989.216 | 230:38 | 68.4834 | 67.9675 | 1989.216 | 230:38 | 68.4834 | 67.9675
17 | CHIKKODI | 199 | 199 | 416:45 | 416:45 | 2105.6576 | 2673:11 | 2217.0403 | 2217.0403 | 2234.4049 | 269:29 | 62.8636 | 62.5728 | 2234.4049 | 269:29 | 62.8636 | 62.5728
18 | VIJAYAPUR | 217 | 217 | 343:35 | 343:35 | 2496.2924 | 3060:26 | 2623.8104 | 2623.8104 | 2638.1264 | 291:46 | 59.6957 | 59.4758 | 2638.1264 | 291:46 | 59.6957 | 59.4758
19 | INDI | 286 | 286 | 1877:44 | 1877:44 | 2983.5035 | 7255:19 | 3285.8083 | 3285.8083 | 3364.0472 | 282:18 | 61.7039 | 60.792 | 3364.0472 | 282:18 | 61.7039 | 60.792
20 | B.BAGEWADI | 156 | 155 | 612:11 | 612:11 | 1603.7451 | 3884:16 | 1765.5896 | 1765.5896 | 1791.0972 | 275:33 | 62.2737 | 61.7287 | 1791.0972 | 275:33 | 62.2737 | 61.7287
21 | BAGALKOT | 230 | 230 | 1111:51 | 1111:51 | 2533.2056 | 5839:34 | 2776.5208 | 2776.5208 | 2822.8479 | 294:33 | 59.7606 | 59.0892 | 2822.8479 | 294:33 | 59.7606 | 59.0892
22 | JAMAKHANDI | 213 | 213 | 529:00 | 529:00 | 2390.4569 | 1072:32 | 2435.1458 | 2435.1458 | 2457.1875 | 276:52 | 61.8913 | 61.5464 | 2457.1875 | 276:52 | 61.8913 | 61.5464
23 | MUDHOL | 213 | 213 | 756:42 | 756:42 | 2915.134 | 1947:07 | 2996.2639 | 2996.2639 | 3027.7931 | 341:10 | 53.1101 | 52.6167 | 3027.7931 | 341:10 | 53.1101 | 52.6167
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2023
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2023 |  |  |  | Reliability for cumulative period from Apr-23 to May-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 50 | 50 | 295:01 | 473:09 | 8208:56 | 1983:01 | 10191:57 | 19180:29 | 10486:58 | 209:44 | 72.6023 | 71.8092 | 19653:38 | 393:04 | 73.7972 | 73.1508
2 | DHARWAD RURAL | 99 | 99 | 411:50 | 505:51 | 14294:44 | 4585:04 | 18879:48 | 1498.5396 | 19291:38 | 194:52 | 74.3676 | 73.8085 | 1519.6167 | 368:24 | 75.1856 | 74.8366
3 | GADAG | 115 | 114 | 231:04 | 696:36 | 1023.4618 | 2649:44 | 1133.8674 | 2186.2049 | 1143.4951 | 238:39 | 68.1945 | 67.9244 | 2215.2299 | 462:19 | 68.8353 | 68.4215
4 | RON | 59 | 59 | 56:50 | 241:55 | 15195:30 | 1388:45 | 16584:15 | 1373.8625 | 16641:05 | 282:03 | 62.2192 | 62.0898 | 1383.9424 | 562:58 | 61.8265 | 61.5465
5 | HAVERI | 210 | 210 | 2475:28 | 3455:13 | 2656.3688 | 11078:33 | 3117.975 | 5962.7958 | 3221.1194 | 368:08 | 52.1048 | 50.5204 | 6106.7632 | 697:55 | 53.452 | 52.3282
6 | RANEBENNUR | 212 | 212 | 1390:19 | 2268:23 | 2773.7792 | 9227:39 | 3158.2646 | 6063.5361 | 3216.1944 | 364:06 | 51.9436 | 51.0622 | 6158.0521 | 697:08 | 53.1122 | 52.3813
7 | SIRSI | 60 | 60 | 328:01 | 522:24 | 693:49 | 2374:31 | 3068:20 | 4544:11 | 3396:21 | 56:36 | 93.1265 | 92.3917 | 5066:35 | 84:27 | 94.8267 | 94.232
8 | DANDELI | 28 | 28 | 110:40 | 212:26 | 769:53 | 634:52 | 1404:45 | 2514:57 | 1515:25 | 54:07 | 93.2568 | 92.7255 | 2727:23 | 97:24 | 93.8648 | 93.3465
9 | KARWAR | 31 | 31 | 564:56 | 712:34 | 352:56 | 487:40 | 840:36 | 1177:02 | 1405:32 | 45:20 | 96.3554 | 93.9059 | 1889:36 | 60:57 | 97.4065 | 95.8364
10 | HONNAVAR | 50 | 50 | 550:27 | 1114:54 | 696:56 | 683:52 | 1380:48 | 2269:44 | 1931:15 | 38:38 | 96.2882 | 94.8085 | 3384:38 | 67:42 | 96.8993 | 95.3762
11 | BELAGAVI RURAL | 152 | 149 | 586:22 | 1000:31 | 17757:55 | 4432:57 | 22190:52 | 1827.6583 | 22777:14 | 149:51 | 80.3773 | 79.8588 | 1869.3465 | 295:10 | 80.2884 | 79.8388
12 | BAILHONGAL | 215 | 215 | 2090:55 | 3641:40 | 2371.0125 | 4758:40 | 2569.2903 | 4911.3292 | 2656.4118 | 296:32 | 61.451 | 60.1439 | 5063.0653 | 565:11 | 62.5518 | 61.3949
13 | RAMDURG | 93 | 93 | 534:28 | 820:16 | 1283.6646 | 2417:17 | 1384.3847 | 2765.3632 | 1406.6542 | 363:00 | 51.9811 | 51.2087 | 2799.541 | 722:28 | 51.254 | 50.6515
14 | GHATAPRABHA | 182 | 182 | 592:50 | 907:26 | 1885.6347 | 4161:07 | 2059.0146 | 3960.5306 | 2083.716 | 274:47 | 63.5056 | 63.0678 | 3998.3403 | 527:15 | 64.326 | 63.9854
15 | RAIBAG | 182 | 182 | 251:20 | 584:36 | 1945.5312 | 2268:11 | 2040.0389 | 3961.5007 | 2050.5111 | 270:24 | 63.8419 | 63.6563 | 3985.859 | 525:36 | 64.3172 | 64.0978
16 | ATHANI | 209 | 209 | 1026:05 | 1794:57 | 1968.8333 | 3230:14 | 2103.4264 | 4060.6063 | 2146.1799 | 246:27 | 67.5347 | 66.8748 | 4135.3958 | 474:53 | 68.1496 | 67.563
17 | CHIKKODI | 199 | 199 | 436:00 | 852:45 | 2163.4472 | 2337:36 | 2260.8472 | 4477.8875 | 2279.0139 | 274:51 | 63.3515 | 63.057 | 4513.4187 | 544:20 | 63.1116 | 62.8189
18 | VIJAYAPUR | 214 | 214 | 512:30 | 856:05 | 2523.0132 | 6045:07 | 2774.8931 | 5398.7035 | 2796.2472 | 313:36 | 58.1716 | 57.8498 | 5434.3736 | 609:28 | 58.6433 | 58.3701
19 | INDI | 289 | 288 | 1129:31 | 3007:15 | 3060.2063 | 8258:28 | 3404.309 | 6690.1174 | 3451.3722 | 286:37 | 62.0012 | 61.4759 | 6815.4194 | 565:59 | 62.0505 | 61.3397
20 | B.BAGEWADI | 155 | 155 | 486:45 | 1098:56 | 1647.3396 | 3953:27 | 1812.0667 | 3577.6562 | 1832.3479 | 283:43 | 62.2879 | 61.8658 | 3623.4451 | 561:03 | 62.1612 | 61.6769
21 | BAGALKOT | 228 | 228 | 449:57 | 1561:48 | 2565.7625 | 5337:27 | 2788.1562 | 5564.6771 | 2806.9042 | 295:28 | 60.5524 | 60.2872 | 5629.7521 | 592:36 | 59.9894 | 59.5215
22 | JAMAKHANDI | 214 | 214 | 483:21 | 1012:21 | 2471.8674 | 3056:32 | 2599.2229 | 5034.3687 | 2619.3625 | 293:46 | 60.8197 | 60.5161 | 5076.55 | 569:20 | 61.4343 | 61.1112
23 | MUDHOL | 215 | 216 | 362:59 | 1119:41 | 3044.4104 | 2928:08 | 3166.416 | 6162.6799 | 3181.5403 | 355:09 | 52.4919 | 52.265 | 6209.3333 | 693:08 | 53.0104 | 52.6547
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2023 (Including Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2023 |  |  |  | Reliability for cumulative period from Apr-23 to June-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 50 | 50 | 255:02 | 728:11 | 8012:23 | 1485:27 | 9497:50 | 1194.9299 | 9752:52 | 195:03 | 73.6171 | 72.9087 | 1225.2708 | 588:08 | 73.7378 | 73.071
2 | DHARWAD RURAL | 99 | 99 | 52:02 | 557:53 | 14988:19 | 3216:33 | 18204:52 | 2257.0757 | 18256:54 | 184:25 | 74.4601 | 74.3871 | 2280.3208 | 552:48 | 74.9464 | 74.6884
3 | GADAG | 115 | 114 | 549:14 | 1245:50 | 23544:08 | 2758:11 | 1095.9299 | 3282.1347 | 1118.8146 | 233:30 | 68.2339 | 67.5706 | 3334.0444 | 695:48 | 68.637 | 68.141
4 | RON | 60 | 60 | 174:28 | 416:23 | 15348:53 | 1266:02 | 16614:55 | 2066.1507 | 16789:23 | 279:49 | 61.5395 | 61.1357 | 2083.5 | 833:24 | 62.1584 | 61.8407
5 | HAVERI | 211 | 211 | 1929:17 | 5384:30 | 2585.7271 | 8939:01 | 2958.1861 | 8920.9819 | 3038.5729 | 345:37 | 53.2672 | 51.9973 | 9145.3361 | 1040:14 | 53.539 | 52.3705
6 | RANEBENNUR | 213 | 213 | 1057:56 | 3326:19 | 2740.6722 | 5160:38 | 2955.6986 | 9019.2347 | 2999.7792 | 338:00 | 53.7449 | 53.0551 | 9157.8313 | 1031:52 | 53.4683 | 52.7533
7 | SIRSI | 61 | 61 | 413:26 | 935:50 | 767:41 | 2728:02 | 3495:43 | 8039:54 | 3909:09 | 64:05 | 92.0407 | 91.0994 | 8975:44 | 147:09 | 93.9651 | 93.2627
8 | DANDELI | 28 | 25 | 116:03 | 328:29 | 294:03 | 639:14 | 933:17 | 3448:14 | 1049:20 | 37:29 | 95.3706 | 94.795 | 3776:43 | 134:53 | 94.3612 | 93.8241
9 | KARWAR | 31 | 31 | 366:32 | 1079:06 | 376:10 | 831:50 | 1208:00 | 2385:02 | 1574:32 | 50:47 | 94.5878 | 92.9456 | 3464:08 | 111:45 | 96.4773 | 94.8834
10 | HONNAVAR | 52 | 51 | 766:50 | 1881:44 | 757:18 | 1245:10 | 2002:28 | 4272:12 | 2769:18 | 53:15 | 94.6515 | 92.6034 | 6153:56 | 118:21 | 96.2382 | 94.5813
11 | BELAGAVI RURAL | 153 | 153 | 431:25 | 1431:56 | 16949:32 | 3256:10 | 20205:42 | 2669.5625 | 20637:07 | 134:53 | 81.6579 | 81.2662 | 2729.2264 | 428:07 | 80.8262 | 80.3977
12 | BAILHONGAL | 216 | 215 | 1741:08 | 5382:48 | 2327.6694 | 4613:26 | 2519.8958 | 7431.225 | 2592.4431 | 288:03 | 61.1127 | 59.9932 | 7655.5083 | 850:37 | 62.1936 | 61.0526
13 | RAMDURG | 95 | 95 | 754:02 | 1574:18 | 1337.8451 | 1574:56 | 1403.4674 | 4168.8306 | 1434.8854 | 362:30 | 50.7555 | 49.6531 | 4234.4264 | 1069:45 | 51.7776 | 51.0188
14 | GHATAPRABHA | 185 | 185 | 431:43 | 1339:09 | 1907.8167 | 2364:52 | 2006.3528 | 5966.8833 | 2024.341 | 262:37 | 63.8495 | 63.5254 | 6022.6812 | 781:19 | 64.5567 | 64.2252
15 | RAIBAG | 181 | 181 | 461:06 | 1045:42 | 1866.3375 | 1037:47 | 1909.5785 | 5871.0792 | 1928.791 | 255:45 | 64.8328 | 64.479 | 5914.65 | 784:16 | 64.3551 | 64.0905
16 | ATHANI | 209 | 209 | 731:45 | 2526:42 | 1900.0111 | 2006:25 | 1983.6118 | 6044.2181 | 2014.1014 | 231:17 | 68.3634 | 67.8772 | 6149.4972 | 706:10 | 68.2201 | 67.6666
17 | CHIKKODI | 198 | 198 | 357:05 | 1209:50 | 2067.4292 | 1475:05 | 2128.891 | 6606.7785 | 2143.7694 | 259:51 | 64.1601 | 63.9096 | 6657.1882 | 806:56 | 63.3323 | 63.0526
18 | VIJAYAPUR | 215 | 215 | 1226:49 | 2082:54 | 2526.6736 | 3944:20 | 2691.0208 | 8089.7243 | 2742.1382 | 306:06 | 58.2787 | 57.4862 | 8176.5118 | 912:44 | 58.6521 | 58.2085
19 | INDI | 292 | 291 | 1828:25 | 4835:40 | 2948.2576 | 7284:41 | 3251.7861 | 9941.9035 | 3327.9701 | 273:32 | 62.8792 | 62.0095 | 10143.3896 | 833:42 | 62.585 | 61.8268
20 | B.BAGEWADI | 155 | 155 | 1048:08 | 2147:04 | 1611.0917 | 3686:17 | 1764.6868 | 5342.3431 | 1808.359 | 280:00 | 62.0497 | 61.1106 | 5431.8042 | 841:03 | 62.1245 | 61.4902
21 | BAGALKOT | 230 | 229 | 1041:58 | 2603:46 | 2568.0882 | 3942:32 | 2732.3604 | 8297.0375 | 2775.7757 | 289:39 | 60.4006 | 59.7714 | 8405.5278 | 877:06 | 60.3582 | 59.8398
22 | JAMAKHANDI | 214 | 214 | 906:01 | 1918:22 | 2566.7076 | 1421:10 | 2625.9229 | 7660.2917 | 2663.6736 | 298:44 | 59.0978 | 58.5098 | 7740.2236 | 868:04 | 60.664 | 60.2536
23 | MUDHOL | 219 | 219 | 1359:43 | 2479:24 | 3007.7 | 1518:07 | 3070.9549 | 9233.6347 | 3127.6097 | 342:45 | 53.2579 | 52.3956 | 9336.9431 | 1023:14 | 53.6673 | 53.149
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of July-2023 (Including Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of July-2023 |  |  |  | Reliability for cumulative period from Apr-23 to July-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 50 | 50 | 250:02 | 978:13 | 7708:22 | 2406:39 | 10115:01 | 1616.3889 | 10365:03 | 207:18 | 72.8091 | 72.137 | 1657.1479 | 795:26 | 73.5018 | 72.8336
2 | DHARWAD RURAL | 99 | 99 | 85:45 | 643:38 | 15259:55 | 4710:16 | 19970:11 | 3089.1667 | 20055:56 | 202:35 | 72.8872 | 72.7708 | 3115.9847 | 755:23 | 74.4232 | 74.2012
3 | GADAG | 115 | 112 | 235:09 | 1480:59 | 23455:25 | 3336:38 | 1116.3354 | 4398.4701 | 1126.1333 | 235:01 | 68.6862 | 68.4114 | 4460.1778 | 930:49 | 68.6495 | 68.2097
4 | RON | 60 | 60 | 91:08 | 507:31 | 15552:45 | 1344:40 | 16897:25 | 2770.2097 | 16988:33 | 283:09 | 62.1474 | 61.9432 | 2791.3562 | 1116:33 | 62.1556 | 61.8667
5 | HAVERI | 211 | 211 | 731:10 | 6115:40 | 2862.0535 | 13275:53 | 3415.2153 | 12336.1972 | 3445.6806 | 391:56 | 47.7876 | 47.3218 | 12591.0167 | 1432:09 | 52.0775 | 51.0877
6 | RANEBENNUR | 213 | 213 | 477:27 | 3803:46 | 2764.5785 | 11769:39 | 3254.9806 | 12274.2153 | 3274.8743 | 369:00 | 50.7045 | 50.4032 | 12432.7056 | 1400:52 | 52.766 | 52.1561
7 | SIRSI | 61 | 61 | 358:06 | 1293:56 | 1187:26 | 688:02 | 1875:28 | 9915:22 | 2233:34 | 36:37 | 95.8676 | 95.0785 | 11209:18 | 183:46 | 94.4485 | 93.7241
8 | DANDELI | 28 | 28 | 74:14 | 402:43 | 481:59 | 1362:27 | 1844:26 | 5292:40 | 1918:40 | 68:31 | 91.1462 | 90.7898 | 5695:23 | 203:24 | 93.5443 | 93.0531
9 | KARWAR | 31 | 31 | 509:56 | 1589:02 | 522:31 | 1159:56 | 1682:27 | 4067:29 | 2192:23 | 70:43 | 92.7053 | 90.4943 | 5656:31 | 182:28 | 95.5188 | 93.7682
10 | HONNAVAR | 51 | 51 | 1219:05 | 3100:49 | 1446:41 | 2166:34 | 3613:15 | 7885:27 | 4832:20 | 94:45 | 90.4774 | 87.2646 | 10986:16 | 215:25 | 94.7194 | 92.6429
11 | BELAGAVI RURAL | 153 | 149 | 187:53 | 1619:49 | 15997:37 | 4620:30 | 20618:07 | 3528.6507 | 20806:00 | 135:59 | 81.8872 | 81.7222 | 3596.1431 | 564:06 | 81.0958 | 80.7343
12 | BAILHONGAL | 212 | 211 | 1363:39 | 6746:27 | 2265.2035 | 6526:17 | 2537.1319 | 9968.3569 | 2593.9507 | 293:39 | 61.3948 | 60.5303 | 10249.459 | 1160:19 | 61.4586 | 60.3717
13 | RAMDURG | 93 | 93 | 528:04 | 2102:22 | 1307.3278 | 2118:40 | 1395.6056 | 5564.4361 | 1417.6083 | 365:50 | 51.5919 | 50.8287 | 5652.0347 | 1458:35 | 50.9568 | 50.1848
14 | GHATAPRABHA | 184 | 184 | 165:32 | 1504:41 | 1970.7257 | 2259:55 | 2064.8889 | 8031.7722 | 2071.7861 | 270:14 | 63.7993 | 63.6784 | 8094.4674 | 1055:48 | 64.2205 | 63.9413
15 | RAIBAG | 181 | 181 | 62:30 | 1108:12 | 1924.1222 | 1289:38 | 1977.8569 | 7848.9361 | 1980.4611 | 262:36 | 64.7504 | 64.704 | 7895.1111 | 1046:52 | 64.4555 | 64.2464
16 | ATHANI | 211 | 211 | 310:24 | 2837:06 | 1938.809 | 2156:04 | 2028.6451 | 8072.8632 | 2041.5785 | 232:13 | 68.9857 | 68.788 | 8191.0757 | 931:41 | 68.6393 | 68.1801
17 | CHIKKODI | 199 | 199 | 210:05 | 1419:55 | 2136.0833 | 2872:49 | 2255.784 | 8862.5625 | 2264.5375 | 273:07 | 63.4336 | 63.2917 | 8921.7257 | 1075:59 | 63.4955 | 63.2518
18 | VIJAYAPUR | 218 | 218 | 334:52 | 2417:46 | 2653.2486 | 5734:10 | 2892.1722 | 10981.8965 | 2906.125 | 319:56 | 57.2037 | 56.9973 | 11082.6368 | 1220:06 | 58.7085 | 58.3297
19 | INDI | 295 | 295 | 1813:06 | 6648:46 | 3163.8222 | 13102:37 | 3709.7646 | 13651.6681 | 3785.3104 | 307:57 | 59.434 | 58.6079 | 13928.7 | 1133:11 | 62.0682 | 61.2984
20 | B.BAGEWADI | 155 | 155 | 633:04 | 2780:08 | 1666.1826 | 5231:09 | 1884.1472 | 7226.4903 | 1910.525 | 295:49 | 60.7878 | 60.2388 | 7342.3292 | 1136:53 | 61.7848 | 61.1722
21 | BAGALKOT | 230 | 230 | 473:55 | 3077:41 | 2612.4299 | 6596:10 | 2887.2701 | 11184.3076 | 2907.0167 | 303:20 | 59.5053 | 59.2284 | 11312.5444 | 1180:26 | 60.1415 | 59.6844
22 | JAMAKHANDI | 215 | 214 | 912:38 | 2831:00 | 2546.5667 | 1401:38 | 2604.9681 | 10265.2597 | 2642.9944 | 295:02 | 60.9157 | 60.3452 | 10383.2181 | 1159:03 | 60.8644 | 60.4147
23 | MUDHOL | 219 | 219 | 232:12 | 2711:36 | 3125.2521 | 2417:13 | 3225.9694 | 12459.6042 | 3235.6444 | 354:35 | 52.4824 | 52.3399 | 12572.5875 | 1377:49 | 53.3663 | 52.9434
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of August-2023 (Including Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Aug-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Aug-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 52 | 52 | 113:18 | 1091:31 | 8748:16 | 1355:00 | 10103:16 | 2037.3583 | 10216:34 | 196:28 | 73.8853 | 73.5924 | 2082.8382 | 961:19 | 74.3922 | 73.8205
2 | DHARWAD RURAL | 103 | 103 | 339:25 | 983:03 | 20132:02 | 1692:11 | 21824:13 | 3998.509 | 22163:38 | 215:11 | 71.5208 | 71.0778 | 4039.4694 | 941:14 | 74.6271 | 74.3672
3 | GADAG | 117 | 116 | 137:55 | 1618:54 | 1090.4681 | 2973:48 | 1214.3764 | 5612.8465 | 1220.1229 | 250:17 | 66.5184 | 66.36 | 5680.3007 | 1165:11 | 68.6451 | 68.2682
4 | RON | 60 | 60 | 86:45 | 594:16 | 16921:46 | 774:25 | 17696:11 | 3507.5507 | 17782:56 | 296:23 | 60.358 | 60.1637 | 3532.3118 | 1412:55 | 61.7914 | 61.5217
5 | HAVERI | 212 | 212 | 1192:20 | 7308:00 | 2866.8438 | 3838:43 | 3026.7903 | 15362.9875 | 3076.4708 | 348:17 | 53.9442 | 53.1882 | 15667.4875 | 1773:41 | 52.636 | 51.6972
6 | RANEBENNUR | 214 | 214 | 1903:58 | 5707:44 | 2935.9667 | 2944:56 | 3058.6722 | 15332.8875 | 3138.0042 | 351:56 | 53.894 | 52.6982 | 15570.7097 | 1746:15 | 53.1706 | 52.4442
7 | SIRSI | 61 | 61 | 326:47 | 1620:43 | 715:10 | 1581:58 | 2297:08 | 12212:30 | 2623:55 | 43:01 | 94.9385 | 94.2184 | 13833:13 | 226:46 | 94.5478 | 93.8242
8 | DANDELI | 28 | 28 | 100:06 | 502:49 | 299:39 | 512:20 | 811:59 | 6104:39 | 912:05 | 32:34 | 96.1022 | 95.6217 | 6607:28 | 235:59 | 94.0625 | 93.5735
9 | KARWAR | 31 | 31 | 153:37 | 1742:39 | 308:17 | 467:52 | 776:09 | 4843:38 | 929:46 | 30:00 | 96.6348 | 95.9688 | 6586:17 | 212:28 | 95.7449 | 94.214
10 | HONNAVAR | 52 | 52 | 335:40 | 3436:29 | 543:06 | 487:33 | 1030:39 | 8916:06 | 1366:19 | 26:17 | 97.336 | 96.4684 | 12352:35 | 237:33 | 95.3305 | 93.5308
11 | BELAGAVI RURAL | 152 | 152 | 348:22 | 1968:11 | 19627:41 | 1910:57 | 21538:38 | 4426.0938 | 21887:00 | 144:00 | 80.9541 | 80.646 | 4508.1014 | 711:48 | 80.9679 | 80.6153
12 | BAILHONGAL | 215 | 215 | 1266:16 | 8012:43 | 2445.6271 | 2283:56 | 2540.791 | 12509.1479 | 2593.5521 | 289:31 | 61.8786 | 61.087 | 12843.0111 | 1433:38 | 61.9725 | 60.9576
13 | RAMDURG | 96 | 96 | 546:40 | 2649:02 | 1422.8993 | 1442:10 | 1482.9896 | 7047.4257 | 1505.7674 | 376:27 | 50.1684 | 49.403 | 7157.8021 | 1789:27 | 52.0192 | 51.2677
14 | GHATAPRABHA | 185 | 185 | 390:01 | 1894:42 | 2138.3715 | 995:36 | 2179.8549 | 10211.6271 | 2196.1056 | 284:54 | 61.9903 | 61.707 | 10290.5729 | 1335:00 | 63.9229 | 63.644
15 | RAIBAG | 186 | 186 | 308:31 | 1416:43 | 2035.084 | 697:56 | 2064.1646 | 9913.1007 | 2077.0194 | 268:00 | 64.2011 | 63.9782 | 9972.1306 | 1286:44 | 65.1659 | 64.9584
16 | ATHANI | 214 | 214 | 914:47 | 3751:53 | 2137.4972 | 959:29 | 2177.4757 | 10250.3389 | 2215.5917 | 248:29 | 67.177 | 66.6025 | 10406.6674 | 1167:06 | 68.6936 | 68.2162
17 | CHIKKODI | 198 | 198 | 941:43 | 2361:38 | 2297.7562 | 1211:55 | 2348.2528 | 11210.8153 | 2387.491 | 289:24 | 61.7424 | 61.1031 | 11309.2167 | 1370:49 | 62.9933 | 62.6685
18 | VIJAYAPUR | 219 | 219 | 692:45 | 3110:31 | 2793.2715 | 2423:48 | 2894.2632 | 13876.1597 | 2923.1278 | 320:21 | 57.3683 | 56.9432 | 14005.7646 | 1534:53 | 58.5873 | 58.2005
19 | INDI | 298 | 298 | 3032:09 | 9680:55 | 3255.5896 | 5124:19 | 3469.1028 | 17120.7708 | 3595.4424 | 289:34 | 62.4475 | 61.0799 | 17524.1424 | 1411:20 | 62.4495 | 61.5648
20 | B.BAGEWADI | 164 | 164 | 2163:32 | 4943:40 | 1821.1167 | 2748:41 | 1935.6451 | 9162.1354 | 2025.7924 | 296:27 | 61.9267 | 60.1536 | 9368.1215 | 1370:57 | 63.4858 | 62.6649
21 | BAGALKOT | 232 | 232 | 731:15 | 3808:56 | 2737.2333 | 3165:20 | 2869.1222 | 14053.4299 | 2899.591 | 299:57 | 60.1068 | 59.6831 | 14212.1354 | 1470:13 | 60.4084 | 59.9613
22 | JAMAKHANDI | 218 | 218 | 1425:12 | 4256:12 | 2719.8944 | 987:32 | 2761.0417 | 13026.3014 | 2820.425 | 310:30 | 59.1441 | 58.2654 | 13203.6431 | 1453:37 | 60.9453 | 60.4136
23 | MUDHOL | 221 | 221 | 1711:02 | 4422:38 | 3273.6993 | 961:14 | 3313.7507 | 15773.3549 | 3385.0437 | 367:36 | 51.6311 | 50.5905 | 15957.6312 | 1732:57 | 53.3512 | 52.8062
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of September-2023 (Including Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of Sept-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Sept-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 53 | 53 | 42:59 | 1134:30 | 9086:14 | 799:54 | 9886:08 | 2449.2806 | 9929:07 | 187:21 | 74.0929 | 73.9803 | 2496.5514 | 1130:31 | 74.7471 | 74.2597
2 | DHARWAD RURAL | 104 | 102 | 108:30 | 1091:33 | 16025:05 | 1502:04 | 17527:09 | 4728.8069 | 17635:39 | 169:34 | 76.593 | 76.4481 | 4774.2882 | 1101:46 | 75.1534 | 74.9144
3 | GADAG | 116 | 114 | 531:10 | 2150:04 | 1002.6361 | 1680:38 | 1072.6625 | 6685.509 | 1094.7944 | 226:31 | 69.1764 | 68.5404 | 6775.0951 | 1401:45 | 68.5062 | 68.0842
4 | RON | 62 | 61 | 150:50 | 745:06 | 15720:50 | 692:47 | 16413:37 | 4191.4514 | 16564:27 | 267:10 | 63.2311 | 62.8933 | 4222.4972 | 1634:31 | 63.0579 | 62.7843
5 | HAVERI | 213 | 213 | 1585:13 | 8893:13 | 2800.6438 | 3617:51 | 2951.3875 | 18314.375 | 3017.4382 | 340:00 | 53.8124 | 52.7787 | 18684.9257 | 2105:21 | 53.0148 | 52.0641
6 | RANEBENNUR | 214 | 214 | 578:18 | 6286:02 | 2795.7306 | 2481:53 | 2899.1424 | 18232.0299 | 2923.2382 | 327:50 | 54.842 | 54.4667 | 18493.9479 | 2074:05 | 53.4446 | 52.7758
7 | SIRSI | 61 | 61 | 152:35 | 1773:18 | 634:32 | 1545:20 | 2179:52 | 14392:22 | 2332:27 | 38:14 | 95.0367 | 94.6893 | 16165:40 | 265:01 | 94.6279 | 93.9661
8 | DANDELI | 29 | 29 | 224:12 | 727:01 | 313:44 | 514:30 | 828:14 | 6932:53 | 1052:26 | 36:17 | 96.0334 | 94.9596 | 7659:54 | 264:08 | 94.5568 | 93.986
9 | KARWAR | 31 | 31 | 328:12 | 2070:51 | 374:52 | 638:21 | 1013:13 | 5856:51 | 1341:25 | 43:16 | 95.4605 | 93.9901 | 7927:42 | 255:44 | 95.6983 | 94.1773
10 | HONNAVAR | 52 | 52 | 824:08 | 4260:37 | 622:18 | 837:22 | 1459:40 | 10375:46 | 2283:48 | 43:55 | 96.1013 | 93.9001 | 14636:23 | 281:28 | 95.4569 | 93.5913
11 | BELAGAVI RURAL | 153 | 152 | 574:27 | 2542:38 | 16992:02 | 2025:44 | 19017:46 | 5218.5007 | 19592:13 | 128:03 | 82.7362 | 82.2148 | 5324.4437 | 835:12 | 81.3618 | 80.9835
12 | BAILHONGAL | 223 | 223 | 1531:10 | 9543:53 | 2431.7486 | 2708:42 | 2544.6111 | 15053.759 | 2608.4097 | 280:44 | 61.964 | 61.0103 | 15451.4208 | 1662:56 | 63.1117 | 62.1372
13 | RAMDURG | 97 | 97 | 352:44 | 3001:46 | 1355.0819 | 1558:50 | 1420.0333 | 8467.459 | 1434.7306 | 354:59 | 51.2016 | 50.6965 | 8592.5326 | 2125:59 | 52.2987 | 51.5941
14 | GHATAPRABHA | 190 | 190 | 202:17 | 2096:59 | 2000.5722 | 1830:48 | 2076.8556 | 12288.4826 | 2085.284 | 263:24 | 63.5639 | 63.4161 | 12375.8569 | 1563:16 | 64.6578 | 64.4065
15 | RAIBAG | 188 | 188 | 276:37 | 1693:20 | 1978.8743 | 1050:31 | 2022.6458 | 11935.7465 | 2034.1715 | 259:41 | 64.1375 | 63.9331 | 12006.3021 | 1532:43 | 65.3071 | 65.102
16 | ATHANI | 217 | 217 | 810:53 | 4562:46 | 1975.5299 | 1638:31 | 2043.8014 | 12294.1403 | 2077.5882 | 229:47 | 68.6052 | 68.0862 | 12484.2556 | 1380:45 | 69.041 | 68.5622
17 | CHIKKODI | 198 | 198 | 446:45 | 2808:23 | 2105.0701 | 1278:23 | 2158.3361 | 13369.1514 | 2176.9507 | 263:52 | 63.6644 | 63.351 | 13486.1674 | 1634:41 | 63.1033 | 62.7804
18 | VIJAYAPUR | 218 | 218 | 750:33 | 3861:04 | 2827.2931 | 3528:01 | 2974.2937 | 16850.4535 | 3005.5667 | 330:53 | 54.5215 | 54.0433 | 17011.3312 | 1872:48 | 57.7619 | 57.3587
19 | INDI | 299 | 299 | 2661:03 | 12341:58 | 3151.9625 | 7816:49 | 3477.6632 | 20598.434 | 3588.5403 | 288:03 | 61.2301 | 59.994 | 21112.6826 | 1694:40 | 62.3546 | 61.4148
20 | B.BAGEWADI | 164 | 164 | 394:29 | 5338:09 | 1711.8611 | 3256:57 | 1847.5674 | 11009.7028 | 1864.0042 | 272:47 | 62.4478 | 62.1137 | 11232.1257 | 1643:44 | 63.3157 | 62.5746
21 | BAGALKOT | 232 | 233 | 874:50 | 4683:46 | 2531.4097 | 4552:39 | 2721.1035 | 16774.5333 | 2757.5549 | 285:16 | 60.9037 | 60.38 | 16969.6903 | 1755:29 | 60.4896 | 60.0299
22 | JAMAKHANDI | 219 | 219 | 337:06 | 4593:18 | 2487.1229 | 1584:38 | 2553.1493 | 15579.4507 | 2567.1951 | 281:20 | 61.1393 | 60.9255 | 15770.8382 | 1728:19 | 61.1262 | 60.6487
23 | MUDHOL | 221 | 221 | 211:45 | 4634:23 | 3029.5174 | 1950:33 | 3110.7903 | 18884.1451 | 3119.6132 | 338:47 | 53.0801 | 52.947 | 19077.2444 | 2071:44 | 53.3068 | 52.8293
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of October-2023 (Including Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of October-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Oct-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 53 | 53 | 50:26 | 1184:56 | 10747:52 | 447:31 | 11195:23 | 2915.7549 | 11245:49 | 212:11 | 71.6084 | 71.4805 | 2965.1271 | 1342:42 | 74.2924 | 73.8571
2 | DHARWAD RURAL | 103 | 103 | 61:07 | 1152:40 | 1056.1944 | 1570:42 | 1121.6403 | 5850.4472 | 1124.1868 | 261:57 | 64.8719 | 64.7921 | 5898.475 | 1374:24 | 73.4577 | 73.2398
3 | GADAG | 116 | 115 | 82:55 | 2232:59 | 1302.6104 | 737:46 | 1333.3507 | 8018.8597 | 1336.8056 | 276:35 | 62.9213 | 62.8252 | 8111.9007 | 1678:19 | 67.6971 | 67.3223
4 | RON | 61 | 61 | 28:55 | 774:01 | 20209:30 | 342:29 | 20551:59 | 5047.784 | 20580:54 | 337:24 | 54.7154 | 54.6516 | 5080.0347 | 1998:42 | 61.3315 | 61.0845
5 | HAVERI | 213 | 213 | 1460:44 | 10353:57 | 3142.1347 | 2669:34 | 3253.3667 | 21567.7417 | 3314.2306 | 373:26 | 50.729 | 49.8072 | 21999.1562 | 2478:47 | 52.6836 | 51.7372
6 | RANEBENNUR | 214 | 214 | 664:38 | 6950:40 | 3205.4764 | 2022:45 | 3289.7576 | 21521.7875 | 3317.4507 | 372:03 | 50.4106 | 49.9932 | 21811.3986 | 2446:08 | 53.0051 | 52.3727
7 | SIRSI | 61 | 61 | 341:30 | 2114:48 | 780:59 | 1534:01 | 2315:00 | 16707:22 | 2656:30 | 43:33 | 94.8991 | 94.1466 | 18822:10 | 308:34 | 94.6672 | 93.9922
8 | DANDELI | 30 | 30 | 224:55 | 951:56 | 187:50 | 543:02 | 730:52 | 7663:45 | 955:47 | 31:52 | 96.7255 | 95.7178 | 8615:41 | 287:11 | 95.0261 | 94.4083
9 | KARWAR | 31 | 31 | 189:32 | 2260:23 | 262:55 | 437:45 | 700:40 | 6557:31 | 890:12 | 28:43 | 96.9621 | 96.1403 | 8817:54 | 284:27 | 95.8814 | 94.4617
10 | HONNAVAR | 52 | 52 | 640:30 | 4901:07 | 634:59 | 684:02 | 1319:01 | 11694:47 | 1959:31 | 37:41 | 96.5906 | 94.9351 | 16595:54 | 319:09 | 95.6211 | 93.786
11 | BELAGAVI RURAL | 153 | 151 | 387:51 | 2930:29 | 1326.4507 | 1764:35 | 1399.975 | 6618.4757 | 1416.1354 | 222:08 | 70.4833 | 70.1426 | 6740.5792 | 1057:21 | 79.786 | 79.4131
12 | BAILHONGAL | 227 | 227 | 1099:04 | 10642:57 | 3096.9938 | 1731:20 | 3169.1326 | 18222.8917 | 3214.9271 | 339:54 | 54.9647 | 54.314 | 18666.3479 | 1973:32 | 62.4874 | 61.5745
13 | RAMDURG | 97 | 97 | 277:38 | 3279:24 | 1557.1215 | 812:39 | 1590.9819 | 10058.441 | 1602.55 | 396:30 | 47.0907 | 46.706 | 10195.0826 | 2522:30 | 51.5443 | 50.886
14 | GHATAPRABHA | 190 | 190 | 311:18 | 2408:17 | 2934.4069 | 900:08 | 2971.9125 | 15260.3951 | 2984.8833 | 377:02 | 49.5431 | 49.3229 | 15360.7403 | 1940:18 | 62.4683 | 62.2215
15 | RAIBAG | 189 | 189 | 262:13 | 1955:33 | 3132.4674 | 660:19 | 3159.9806 | 15095.7271 | 3170.9062 | 402:39 | 46.0662 | 45.8797 | 15177.2083 | 1927:16 | 62.6768 | 62.4754
16 | ATHANI | 219 | 219 | 605:48 | 5168:34 | 3091.8743 | 1253:37 | 3144.1083 | 15438.2486 | 3169.35 | 347:20 | 53.6882 | 53.3164 | 15653.6056 | 1715:28 | 67.0587 | 66.5992
17 | CHIKKODI | 198 | 198 | 270:17 | 3078:40 | 2947.3417 | 851:27 | 2982.8187 | 16351.9701 | 2994.0806 | 362:55 | 51.4041 | 51.2206 | 16480.2479 | 1997:36 | 61.4085 | 61.1058
18 | VIJAYAPUR | 219 | 219 | 991:10 | 4852:14 | 3398.5333 | 2003:15 | 3482.0021 | 20332.4556 | 3523.3007 | 386:07 | 48.7111 | 48.1028 | 20534.6319 | 2250:22 | 56.6158 | 56.1844
19 | INDI | 299 | 298 | 901:12 | 13243:10 | 4104.5472 | 5111:35 | 4317.5299 | 24915.9639 | 4355.0799 | 349:34 | 53.4197 | 53.0146 | 25467.7625 | 2044:14 | 61.0603 | 60.1979
20 | B.BAGEWADI | 167 | 166 | 2629:08 | 7967:17 | 1990.1014 | 1319:53 | 2045.0965 | 13054.7993 | 2154.6438 | 309:39 | 60.4965 | 58.3805 | 13386.7694 | 1923:51 | 63.4708 | 62.5419
21 | BAGALKOT | 233 | 233 | 1287:22 | 5971:08 | 3083.091 | 2947:25 | 3205.9 | 19980.4333 | 3259.5403 | 335:45 | 55.6154 | 54.8728 | 20229.2306 | 2083:42 | 59.9285 | 59.4296
22 | JAMAKHANDI | 224 | 222 | 898:56 | 5492:14 | 3392.9729 | 930:34 | 3431.7465 | 19011.1972 | 3469.2021 | 371:42 | 50.5797 | 50.0403 | 19240.0403 | 2061:26 | 60.3405 | 59.8631
23 | MUDHOL | 222 | 222 | 627:50 | 5262:13 | 3765.9958 | 1244:31 | 3817.8507 | 22701.9958 | 3844.0104 | 415:34 | 44.5241 | 44.144 | 22921.2549 | 2477:58 | 52.2144 | 51.7529
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of NOVEMBER-2023 (Including Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of November-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Nov-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 53 | 53 | 93:10 | 1278:06 | 9110:53 | 586:34 | 9697:27 | 3319.8153 | 9790:37 | 184:44 | 74.5874 | 74.3432 | 3373.0694 | 1527:26 | 74.3287 | 73.9169
2 | DHARWAD RURAL | 102 | 102 | 90:30 | 1243:10 | 22557:28 | 1235:54 | 23793:22 | 6841.8375 | 23883:52 | 234:09 | 67.6016 | 67.4784 | 6893.6361 | 1622:02 | 72.5095 | 72.3014
3 | GADAG | 116 | 116 | 112:40 | 2345:39 | 1133.7132 | 1156:49 | 1181.9139 | 9200.7736 | 1186.6083 | 245:30 | 66.037 | 65.9021 | 9298.509 | 1923:50 | 67.493 | 67.1477
4 | RON | 61 | 61 | 125:22 | 899:23 | 17457:59 | 477:24 | 17935:23 | 5795.0917 | 18060:45 | 296:05 | 59.1635 | 58.8781 | 5832.566 | 2294:47 | 61.065 | 60.8132
5 | HAVERI | 213 | 213 | 1014:27 | 11368:24 | 2762.4042 | 3549:15 | 2910.2896 | 24478.0312 | 2952.5583 | 332:41 | 54.4556 | 53.7941 | 24951.7146 | 2811:28 | 52.9015 | 51.9901
6 | RANEBENNUR | 216 | 216 | 674:20 | 7625:00 | 2919.2389 | 3124:22 | 3049.4208 | 24571.2083 | 3077.5181 | 341:57 | 52.941 | 52.5074 | 24888.9167 | 2765:26 | 53.3789 | 52.776
7 | SIRSI | 61 | 61 | 341:30 | 2456:18 | 780:59 | 1534:01 | 2315:00 | 19022:22 | 2656:30 | 43:33 | 94.7291 | 93.9515 | 21478:40 | 352:07 | 94.6748 | 93.9872
8 | DANDELI | 30 | 30 | 88:42 | 1040:38 | 189:47 | 288:52 | 478:39 | 8142:24 | 567:21 | 18:55 | 97.784 | 97.3734 | 9183:02 | 306:06 | 95.3652 | 94.7729
9 | KARWAR | 31 | 31 | 226:59 | 2487:22 | 243:41 | 369:28 | 613:09 | 7170:40 | 840:08 | 27:06 | 97.2529 | 96.236 | 9658:02 | 311:33 | 96.05 | 94.6798
10 | HONNAVAR | 53 | 53 | 347:16 | 5248:23 | 552:50 | 481:42 | 1034:32 | 12729:19 | 1381:48 | 26:04 | 97.289 | 96.3789 | 17977:42 | 339:12 | 95.8986 | 94.2076
11 | BELAGAVI RURAL | 149 | 149 | 445:45 | 3376:14 | 1161.2951 | 1372:35 | 1218.4861 | 7836.9618 | 1237.059 | 199:15 | 72.7408 | 72.3253 | 7977.6382 | 1284:59 | 78.4438 | 78.0569
12 | BAILHONGAL | 226 | 226 | 720:36 | 11363:33 | 2822.109 | 2100:35 | 2909.6333 | 21132.525 | 2939.6583 | 312:11 | 57.0851 | 56.6422 | 21606.0062 | 2294:27 | 61.6776 | 60.8189
13 | RAMDURG | 97 | 97 | 206:56 | 3486:20 | 1396.4375 | 794:59 | 1429.5618 | 11488.0028 | 1438.184 | 355:50 | 50.8742 | 50.5779 | 11633.2667 | 2878:20 | 51.4619 | 50.8481
14 | GHATAPRABHA | 191 | 191 | 127:37 | 2535:54 | 2659.1979 | 1233:56 | 2710.6118 | 17971.0069 | 2715.9292 | 341:16 | 52.6944 | 52.6016 | 18076.6694 | 2271:25 | 61.4389 | 61.2122
15 | RAIBAG | 189 | 189 | 472:53 | 2428:26 | 2833.7167 | 488:40 | 2854.0778 | 17949.8049 | 2873.7813 | 364:55 | 49.6635 | 49.316 | 18050.9896 | 2292:11 | 61.0768 | 60.8574
16 | ATHANI | 221 | 221 | 308:10 | 5476:44 | 3022.0931 | 911:11 | 3060.059 | 18498.3076 | 3072.8993 | 333:43 | 53.8453 | 53.6516 | 18726.5049 | 2033:39 | 65.6956 | 65.2724
17 | CHIKKODI | 198 | 198 | 327:24 | 3406:04 | 2511.9181 | 1149:05 | 2559.7965 | 18911.7667 | 2573.4382 | 311:56 | 56.9058 | 56.6761 | 19053.6861 | 2309:32 | 60.8549 | 60.5612
18 | VIJAYAPUR | 220 | 220 | 131:25 | 4983:39 | 2959.2528 | 1731:52 | 3031.4139 | 23363.8694 | 3036.8896 | 331:18 | 54.0695 | 53.9865 | 23571.5215 | 2571:26 | 56.4757 | 56.0888
19 | INDI | 299 | 299 | 595:22 | 13838:32 | 3877.1083 | 3101:42 | 4006.3458 | 28922.3097 | 4031.1528 | 323:34 | 55.3362 | 55.0596 | 29498.9153 | 2367:48 | 60.3565 | 59.5662
20 | B.BAGEWADI | 168 | 168 | 342:31 | 8309:48 | 1767.4389 | 1652:52 | 1836.3083 | 14891.1076 | 1850.5799 | 264:22 | 63.5653 | 63.2821 | 15237.3493 | 2176:46 | 63.6731 | 62.8285
21 | BAGALKOT | 233 | 233 | 250:34 | 6221:42 | 2704.6597 | 2466:32 | 2807.4319 | 22787.8653 | 2817.8722 | 290:15 | 59.8365 | 59.6871 | 23047.1028 | 2373:57 | 59.9172 | 59.4612
22 | JAMAKHANDI | 223 | 223 | 255:40 | 5747:54 | 3104.1889 | 820:19 | 3138.3688 | 22149.566 | 3149.0215 | 338:54 | 53.0887 | 52.9294 | 22389.0618 | 2409:35 | 59.2929 | 58.8527
23 | MUDHOL | 222 | 222 | 109:47 | 5372:00 | 3260.9174 | 1098:33 | 3306.6903 | 26008.6861 | 3311.2646 | 357:58 | 50.35 | 50.2813 | 26232.5194 | 2835:57 | 51.9851 | 51.5719
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of DECEMBER-2023 (Including Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of December-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Dec-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 54 | 54 | 24:20 | 1302:26 | 10057:10 | 195:27 | 10252:37 | 3747.0076 | 10276:57 | 190:19 | 74.4807 | 74.4202 | 3801.2757 | 1689:27 | 74.7676 | 74.4022
2 | DHARWAD RURAL | 105 | 104 | 97:13 | 1340:23 | 23614:38 | 716:59 | 1013.8174 | 7855.6549 | 1017.8681 | 232:39 | 68.8535 | 68.7291 | 7911.5042 | 1808:21 | 72.7943 | 72.6009
3 | GADAG | 117 | 117 | 197:50 | 2543:29 | 1158.8785 | 555:39 | 1182.0306 | 10382.8042 | 1190.2736 | 244:10 | 67.4102 | 67.183 | 10488.7826 | 2151:33 | 67.7302 | 67.4008
4 | RON | 61 | 61 | 123:20 | 1022:43 | 17651:25 | 489:12 | 18140:37 | 6550.9507 | 18263:57 | 299:25 | 60.0286 | 59.7569 | 6593.5639 | 2594:11 | 60.9481 | 60.6941
5 | HAVERI | 213 | 213 | 1447:26 | 12815:50 | 2838.625 | 1642:54 | 2907.0792 | 27385.1104 | 2967.3889 | 334:21 | 55.9734 | 55.06 | 27919.1035 | 3145:49 | 53.2478 | 52.3361
6 | RANEBENNUR | 217 | 215 | 872:39 | 8497:39 | 3044.9375 | 1572:01 | 3110.4382 | 27681.6465 | 3146.7986 | 348:02 | 53.7619 | 53.2214 | 28035.7153 | 3100:43 | 53.6127 | 53.0193
7 | SIRSI | 63 | 63 | 199:20 | 2655:38 | 975:49 | 886:13 | 1862:02 | 20884:24 | 2061:22 | 32:43 | 96.0274 | 95.6021 | 23540:02 | 373:39 | 94.9773 | 94.3386
8 | DANDELI | 30 | 30 | 54:43 | 1095:21 | 282:26 | 222:45 | 505:11 | 8647:35 | 559:54 | 18:40 | 97.7366 | 97.4915 | 9742:56 | 324:46 | 95.6325 | 95.0793
9 | KARWAR | 31 | 31 | 121:11 | 2608:33 | 186:14 | 290:53 | 477:07 | 7647:47 | 598:18 | 19:18 | 97.9313 | 97.4059 | 10256:20 | 330:51 | 96.2621 | 94.9871
10 | HONNAVAR | 53 | 53 | 858:48 | 6107:11 | 710:46 | 380:21 | 1091:07 | 13820:26 | 1949:55 | 36:47 | 97.2329 | 95.055 | 19927:37 | 376:00 | 96.049 | 94.3031
11 | BELAGAVI RURAL | 150 | 150 | 110:03 | 3486:17 | 1164.5424 | 773:21 | 1196.7653 | 9033.7271 | 1201.3507 | 192:13 | 74.2631 | 74.1645 | 9178.9889 | 1468:38 | 78.1001 | 77.7479
12 | BAILHONGAL | 226 | 226 | 1342:47 | 12706:20 | 2826.775 | 1475:40 | 2888.2611 | 24020.7861 | 2944.2104 | 312:40 | 58.7745 | 57.9759 | 24550.2167 | 2607:06 | 61.3503 | 60.4984
13 | RAMDURG | 97 | 97 | 469:45 | 3956:05 | 1437.3986 | 323:17 | 1450.8688 | 12938.8715 | 1470.4417 | 363:49 | 51.7503 | 51.0994 | 13103.7083 | 3242:09 | 51.4944 | 50.8764
14 | GHATAPRABHA | 193 | 193 | 139:39 | 2675:33 | 2723.2674 | 707:58 | 2752.766 | 20723.7729 | 2758.5847 | 343:02 | 53.9902 | 53.893 | 20835.2542 | 2590:55 | 60.9538 | 60.7438
15 | RAIBAG | 190 | 190 | 158:36 | 2587:02 | 2865.841 | 436:38 | 2884.034 | 20833.8389 | 2890.6424 | 365:08 | 51.0351 | 50.9229 | 20941.6319 | 2645:16 | 60.1266 | 59.9203
16 | ATHANI | 220 | 220 | 500:10 | 5976:54 | 3005.9625 | 721:44 | 3036.0347 | 21534.3424 | 3056.875 | 333:29 | 55.4834 | 55.1778 | 21783.3799 | 2376:22 | 64.406 | 63.9944
17 | CHIKKODI | 198 | 198 | 165:40 | 3571:44 | 2575.375 | 662:20 | 2602.9722 | 21514.7389 | 2609.875 | 316:21 | 57.5925 | 57.48 | 21663.5611 | 2625:53 | 60.4872 | 60.2138
18 | VIJAYAPUR | 220 | 220 | 504:08 | 5487:47 | 3028.5708 | 1193:22 | 3078.2944 | 26442.1639 | 3099.3 | 338:06 | 54.8637 | 54.5557 | 26670.8215 | 2909:33 | 56.2939 | 55.916
19 | INDI | 300 | 300 | 771:18 | 14609:50 | 3822.9861 | 1676:44 | 3892.85 | 32815.1597 | 3924.9875 | 314:00 | 58.1414 | 57.7958 | 33423.9028 | 2673:55 | 60.224 | 59.4862
20 | B.BAGEWADI | 168 | 168 | 428:44 | 8738:32 | 1870.1396 | 824:34 | 1904.4965 | 16795.6042 | 1922.3604 | 274:37 | 63.4313 | 63.0883 | 17159.7097 | 2451:23 | 63.6459 | 62.8578
21 | BAGALKOT | 234 | 234 | 458:01 | 6679:43 | 2778.8625 | 1547:19 | 2843.334 | 25631.1993 | 2862.4181 | 293:35 | 60.8032 | 60.5401 | 25909.5208 | 2657:23 | 60.1691 | 59.7366
22 | JAMAKHANDI | 223 | 223 | 180:46 | 5928:40 | 3124.2014 | 395:46 | 3140.6917 | 25290.2576 | 3148.2236 | 338:49 | 54.5683 | 54.4594 | 25537.2854 | 2748:24 | 58.7603 | 58.3575
23 | MUDHOL | 222 | 222 | 230:52 | 5602:52 | 3281.366 | 459:11 | 3300.4986 | 29309.1847 | 3310.1181 | 357:51 | 52.0416 | 51.9018 | 29542.6375 | 3193:48 | 51.9915 | 51.6091
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of JANUARY-2024 (Including Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of January-2024 |  |  |  | Reliability for cumulative period from Apr-23 to Jan-24
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 54 | 54 | 40:37 | 1343:03 | 9890:47 | 219:26 | 10110:13 | 4168.2667 | 10150:50 | 187:59 | 74.8352 | 74.7341 | 4224.2271 | 1877:26 | 74.7745 | 74.4358
2 | DHARWAD RURAL | 104 | 104 | 73:20 | 1413:43 | 1000.0194 | 705:26 | 1029.4125 | 8885.0674 | 1032.4681 | 238:16 | 68.0703 | 67.9756 | 8943.9722 | 2064:00 | 72.0806 | 71.8955
3 | GADAG | 117 | 117 | 41:15 | 2584:44 | 1099.4924 | 507:23 | 1120.6333 | 11503.4375 | 1122.3521 | 230:14 | 69.103 | 69.0556 | 11611.1347 | 2381:46 | 67.8693 | 67.5685
4 | RON | 61 | 61 | 18:44 | 1041:27 | 17459:10 | 362:33 | 17821:43 | 7293.5222 | 17840:27 | 292:28 | 60.7313 | 60.69 | 7336.916 | 2886:39 | 60.9262 | 60.6937
5 | HAVERI | 214 | 214 | 1572:34 | 14388:24 | 2857.5229 | 1862:09 | 2935.1125 | 30320.2229 | 3000.6361 | 336:31 | 55.7565 | 54.7688 | 30919.7396 | 3467:38 | 53.6983 | 52.7828
6 | RANEBENNUR | 217 | 217 | 965:55 | 9463:34 | 2976.1757 | 1543:33 | 3040.4903 | 30722.1368 | 3080.7368 | 340:44 | 54.8017 | 54.2034 | 31116.4521 | 3441:27 | 53.7331 | 53.1393
7 | SIRSI | 62 | 62 | 254:06 | 2909:44 | 625:50 | 1389:27 | 2015:17 | 22899:41 | 2269:23 | 36:36 | 95.6311 | 95.0802 | 1075.3924 | 416:17 | 94.9707 | 94.3317
8 | DANDELI | 30 | 30 | 77:45 | 1173:06 | 166:15 | 287:06 | 453:21 | 9100:56 | 531:06 | 17:42 | 97.9689 | 97.6205 | 10274:02 | 342:28 | 95.8692 | 95.3368
9 | KARWAR | 31 | 29 | 216:01 | 2824:34 | 197:00 | 332:30 | 529:30 | 8177:17 | 745:31 | 24:03 | 97.7042 | 96.7676 | 11001:51 | 354:54 | 96.4082 | 95.1675
10 | HONNAVAR | 54 | 54 | 753:13 | 6860:24 | 650:01 | 579:15 | 1229:16 | 15049:42 | 1982:29 | 36:43 | 96.9403 | 95.0655 | 21910:06 | 405:45 | 96.2051 | 94.4752
11 | BELAGAVI RURAL | 155 | 155 | 356:00 | 3842:17 | 1183.3069 | 882:12 | 1220.0653 | 10253.7924 | 1234.8986 | 191:13 | 74.6084 | 74.2997 | 10413.8875 | 1612:28 | 78.3812 | 78.0437
12 | BAILHONGAL | 226 | 226 | 329:04 | 13035:24 | 2867.6743 | 1010:24 | 2909.7743 | 26930.5604 | 2923.4854 | 310:28 | 58.4674 | 58.2717 | 27473.7021 | 2917:34 | 61.0582 | 60.2729
13 | RAMDURG | 101 | 101 | 87:02 | 4043:07 | 1496.8708 | 372:45 | 1512.4021 | 14451.2736 | 1516.0285 | 360:15 | 51.6959 | 51.5801 | 14619.7368 | 3474:00 | 53.2412 | 52.6961
14 | GHATAPRABHA | 194 | 194 | 171:48 | 2847:21 | 2698.1882 | 734:32 | 2728.7937 | 23452.5667 | 2735.9521 | 338:28 | 54.626 | 54.5069 | 23571.2062 | 2916:02 | 60.4936 | 60.2938
15 | RAIBAG | 193 | 193 | 88:56 | 2675:58 | 2896.3201 | 357:16 | 2911.2062 | 23745.0451 | 2914.9118 | 362:29 | 51.342 | 51.2801 | 23856.5438 | 2966:37 | 59.7937 | 59.6049
16 | ATHANI | 221 | 221 | 367:20 | 6344:14 | 2908.275 | 427:55 | 2926.1049 | 24460.4472 | 2941.4104 | 319:26 | 57.2894 | 57.066 | 24724.7903 | 2685:03 | 63.8298 | 63.4389
17 | CHIKKODI | 198 | 198 | 71:30 | 3643:14 | 2574.6201 | 556:33 | 2597.8097 | 24112.5486 | 2600.7889 | 315:15 | 57.6766 | 57.6281 | 24264.35 | 2941:08 | 60.2024 | 59.9519
18 | VIJAYAPUR | 221 | 221 | 269:16 | 5757:03 | 3012.7618 | 540:23 | 3035.2778 | 29477.4417 | 3046.4972 | 330:50 | 55.6958 | 55.5321 | 29717.3187 | 3227:13 | 56.4111 | 56.0564
19 | INDI | 300 | 300 | 128:05 | 14737:55 | 3781.275 | 902:25 | 3818.8757 | 36634.0354 | 3824.2125 | 305:56 | 58.9368 | 58.8794 | 37248.1153 | 2979:51 | 60.0936 | 59.4247
20 | B.BAGEWADI | 168 | 168 | 428:44 | 9167:16 | 1870.1396 | 824:34 | 1904.4965 | 18700.1007 | 1922.3604 | 274:37 | 63.4313 | 63.0883 | 19082.0701 | 2726:01 | 63.6241 | 62.8811
21 | BAGALKOT | 234 | 234 | 337:07 | 7016:50 | 2793.9701 | 1416:03 | 2852.9722 | 28484.1715 | 2867.0187 | 294:03 | 60.6704 | 60.4767 | 28776.5396 | 2951:26 | 60.2199 | 59.8115
22 | JAMAKHANDI | 223 | 223 | 243:02 | 6171:42 | 3100.2285 | 456:35 | 3119.2528 | 28409.5104 | 3129.3792 | 336:48 | 54.8784 | 54.732 | 28666.6646 | 3085:12 | 58.367 | 57.9902
23 | MUDHOL | 223 | 223 | 137:36 | 5740:28 | 3265.5889 | 576:49 | 3289.6229 | 32598.8076 | 3295.3562 | 354:39 | 52.414 | 52.331 | 32837.9938 | 3534:08 | 52.2278 | 51.8773
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of FEBRUARY-2024 (Including Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of February-2024 |  |  |  | Reliability for cumulative period from Apr-23 to Feb-24
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 54 | 54 | 90:30 | 1433:33 | 9547:53 | 207:22 | 9755:15 | 4574.7354 | 9845:45 | 182:20 | 74.0441 | 73.8033 | 4634.4667 | 2059:46 | 74.7112 | 74.3811
2 | DHARWAD RURAL | 106 | 106 | 96:10 | 1509:53 | 23362:03 | 770:13 | 1005.5111 | 9890.5785 | 1009.5181 | 228:34 | 67.2898 | 67.1595 | 9953.4903 | 2253:37 | 72.1471 | 71.9699
3 | GADAG | 121 | 121 | 260:50 | 2845:34 | 1104.6299 | 502:43 | 1125.5764 | 12629.0139 | 1136.4444 | 225:25 | 67.9232 | 67.6134 | 12747.5792 | 2528:27 | 68.8442 | 68.5517
4 | RON | 61 | 61 | 121:54 | 1163:21 | 15337:39 | 457:16 | 15794:55 | 7951.6437 | 15916:49 | 260:56 | 62.797 | 62.5099 | 8000.1167 | 3147:35 | 61.0881 | 60.8509
5 | HAVERI | 216 | 216 | 1144:40 | 15533:04 | 2722.8715 | 1635:54 | 2791.034 | 33111.2569 | 2838.7285 | 315:25 | 55.4433 | 54.6819 | 33758.4681 | 3750:56 | 54.2409 | 53.3465
6 | RANEBENNUR | 218 | 218 | 1331:49 | 10795:23 | 2831.2576 | 55:56 | 2833.5882 | 33555.725 | 2889.0806 | 318:04 | 55.1789 | 54.3012 | 34005.5326 | 3743:44 | 54.0521 | 53.4362
7 | SIRSI | 64 | 64 | 319:32 | 3229:16 | 692:01 | 1077:37 | 1769:38 | 1027.8882 | 2089:10 | 32:39 | 96.0272 | 95.3099 | 1162.441 | 435:55 | 95.2057 | 94.5782
8 | DANDELI | 30 | 30 | 21:01 | 1194:07 | 256:17 | 287:22 | 543:39 | 9644:35 | 564:40 | 18:49 | 97.3963 | 97.2957 | 10838:42 | 361:17 | 96.0014 | 95.5063
9 | KARWAR | 31 | 31 | 207:23 | 3031:57 | 203:16 | 162:40 | 365:56 | 8543:13 | 573:19 | 18:30 | 98.304 | 97.3428 | 11575:10 | 373:24 | 96.5723 | 95.3558
10 | HONNAVAR | 54 | 54 | 213:28 | 7073:52 | 531:15 | 313:27 | 844:42 | 15894:24 | 1058:10 | 19:36 | 97.7525 | 97.1845 | 22968:16 | 425:20 | 96.339 | 94.7097
11 | BELAGAVI RURAL | 157 | 157 | 284:21 | 4126:38 | 1208.7403 | 947:47 | 1248.2312 | 11502.0236 | 1260.0792 | 192:37 | 72.5844 | 72.3242 | 11673.9667 | 1784:33 | 78.131 | 77.804
12 | BAILHONGAL | 226 | 226 | 854:54 | 13890:18 | 2687.4569 | 1131:04 | 2734.5847 | 29665.1451 | 2770.2056 | 294:11 | 58.2761 | 57.7326 | 30243.9076 | 3211:45 | 60.8174 | 60.053
13 | RAMDURG | 102 | 102 | 281:52 | 4324:59 | 1418.3833 | 271:09 | 1429.6813 | 15880.9549 | 1441.4257 | 339:10 | 51.6673 | 51.2703 | 16061.1625 | 3779:06 | 53.5237 | 52.9963
14 | GHATAPRABHA | 196 | 196 | 81:58 | 2929:19 | 2587.5444 | 427:29 | 2605.3562 | 26057.9229 | 2608.7715 | 319:26 | 54.1633 | 54.1032 | 26179.9778 | 3205:43 | 60.3139 | 60.128
15 | RAIBAG | 196 | 196 | 301:45 | 2977:43 | 2753.1694 | 311:06 | 2766.1319 | 26511.1771 | 2778.7049 | 340:15 | 51.3348 | 51.1136 | 26635.2486 | 3261:28 | 59.6235 | 59.4346
16 | ATHANI | 225 | 225 | 753:42 | 7097:56 | 2790.4431 | 535:21 | 2812.7493 | 27273.1965 | 2844.1535 | 303:23 | 56.8927 | 56.4114 | 27568.9437 | 2940:41 | 63.8167 | 63.4243
17 | CHIKKODI | 198 | 198 | 362:39 | 4005:53 | 2426.434 | 399:03 | 2443.0611 | 26555.6097 | 2458.1715 | 297:58 | 57.4528 | 57.1896 | 26722.5215 | 3239:06 | 59.9644 | 59.7128
18 | VIJAYAPUR | 220 | 220 | 402:44 | 6159:47 | 2807.8951 | 556:50 | 2831.0965 | 32308.5382 | 2847.8771 | 310:41 | 55.6254 | 55.3624 | 32565.1958 | 3552:34 | 56.1621 | 55.8138
19 | INDI | 301 | 301 | 1274:21 | 16012:16 | 3584.5604 | 857:27 | 3620.2875 | 40254.3229 | 3673.3854 | 292:54 | 58.5257 | 57.9175 | 40921.5007 | 3262:51 | 60.079 | 59.4174
20 | B.BAGEWADI | 170 | 170 | 171:02 | 9338:18 | 1809.4042 | 545:32 | 1832.1347 | 20532.2354 | 1839.2611 | 259:40 | 62.837 | 62.6925 | 20921.3312 | 2953:36 | 63.9469 | 63.2637
21 | BAGALKOT | 234 | 234 | 556:25 | 7573:15 | 2641.5097 | 1525:26 | 2705.0694 | 31189.241 | 2728.2535 | 279:49 | 60.1375 | 59.7959 | 31504.7931 | 3231:16 | 60.2127 | 59.8102
22 | JAMAKHANDI | 223 | 223 | 239:29 | 6411:11 | 2927.1875 | 349:40 | 2941.7569 | 31351.2674 | 2951.7354 | 317:41 | 54.5113 | 54.357 | 31618.4 | 3402:53 | 58.0332 | 57.6757
23 | MUDHOL | 224 | 224 | 125:31 | 5865:59 | 3088.1937 | 586:18 | 3112.6229 | 35711.4306 | 3117.8528 | 334:03 | 52.084 | 52.0035 | 35955.8465 | 3852:25 | 52.4101 | 52.0844
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of MARCH-2024 (Including Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of March-2024 |  |  |  | Reliability for cumulative period from Apr-23 to Mar-24
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 57 | 57 | 21:42 | 1455:15 | 10546:17 | 320:45 | 10867:02 | 5027.5285 | 10888:44 | 191:02 | 74.375 | 74.3239 | 5088.1639 | 2142:23 | 75.901 | 75.6104
2 | DHARWAD RURAL | 107 | 106 | 60:30 | 1570:23 | 1031.4188 | 732:20 | 1061.9326 | 10952.5111 | 1064.4535 | 238:45 | 67.9851 | 67.9092 | 11017.9438 | 2471:19 | 72.0328 | 71.8657
3 | GADAG | 120 | 120 | 32:30 | 2878:04 | 1157.6556 | 583:15 | 1181.9576 | 13810.9715 | 1183.3118 | 236:40 | 68.2269 | 68.1905 | 13930.891 | 2786:11 | 68.5543 | 68.2812
4 | RON | 61 | 61 | 136:31 | 1299:52 | 15618:15 | 390:00 | 16008:15 | 8618.6542 | 16144:46 | 264:40 | 64.7271 | 64.4263 | 8672.8153 | 3412:15 | 61.3963 | 61.1537
5 | HAVERI | 216 | 216 | 775:45 | 16308:49 | 2946.2639 | 1606:24 | 3013.1972 | 36124.4542 | 3045.5201 | 338:23 | 55 | 54.5173 | 36803.9882 | 4089:20 | 54.3052 | 53.4457
6 | RANEBENNUR | 218 | 218 | 717:56 | 11513:19 | 3037.9208 | 1312:55 | 3092.6257 | 36648.3507 | 3122.5396 | 343:46 | 54.2376 | 53.7949 | 37128.0722 | 4087:30 | 54.0678 | 53.4666
7 | SIRSI | 65 | 64 | 346:39 | 3575:55 | 701:20 | 1164:10 | 1865:30 | 1105.6174 | 2212:09 | 34:02 | 96.1425 | 95.4257 | 1254.6139 | 463:15 | 95.3526 | 94.7263
8 | DANDELI | 30 | 30 | 46:29 | 1240:36 | 283:06 | 238:47 | 521:53 | 10166:28 | 568:22 | 18:57 | 97.6618 | 97.4536 | 11407:04 | 380:14 | 96.1421 | 95.6713
9 | KARWAR | 31 | 31 | 146:32 | 3178:29 | 286:34 | 134:13 | 420:47 | 8964:00 | 567:19 | 18:18 | 98.1756 | 97.5403 | 12142:29 | 391:42 | 96.7081 | 95.5408
10 | HONNAVAR | 54 | 54 | 306:11 | 7380:03 | 475:41 | 356:35 | 832:16 | 16726:40 | 1138:27 | 21:05 | 97.9284 | 97.1663 | 1004.4465 | 446:25 | 96.4737 | 94.9178
11 | BELAGAVI RURAL | 157 | 151 | 329:20 | 4455:58 | 1289.4076 | 1166:18 | 1338.0035 | 12840.0271 | 1351.7257 | 206:38 | 72.5087 | 72.2267 | 13025.6924 | 1991:11 | 77.6548 | 77.3316
12 | BAILHONGAL | 229 | 229 | 1263:54 | 15154:12 | 2933.5271 | 1213:34 | 2984.0924 | 32649.2375 | 3036.7549 | 318:16 | 57.9646 | 57.2228 | 33280.6625 | 3487:56 | 61.0456 | 60.2922
13 | RAMDURG | 102 | 102 | 876:30 | 5201:29 | 1521.8132 | 348:25 | 1536.3306 | 17417.2854 | 1572.8514 | 370:05 | 51.4127 | 50.2577 | 17634.0139 | 4149:11 | 53.3449 | 52.7643
14 | GHATAPRABHA | 199 | 199 | 146:58 | 3076:17 | 2756.275 | 546:45 | 2779.0563 | 28836.9792 | 2785.1799 | 335:54 | 54.9513 | 54.852 | 28965.1576 | 3493:17 | 60.4073 | 60.2313
15 | RAIBAG | 199 | 199 | 315:10 | 3292:53 | 3020.0951 | 401:23 | 3036.8194 | 29547.9965 | 3049.9514 | 367:50 | 50.7729 | 50.56 | 29685.2 | 3580:07 | 59.431 | 59.2427
16 | ATHANI | 225 | 225 | 854:30 | 7952:26 | 3010.6764 | 538:58 | 3033.1333 | 30306.3299 | 3068.7375 | 327:20 | 56.5142 | 56.0038 | 30637.6812 | 3268:01 | 63.1981 | 62.7958
17 | CHIKKODI | 201 | 201 | 298:00 | 4303:53 | 2535.5826 | 540:54 | 2558.1201 | 29113.7299 | 2570.5368 | 306:56 | 58.9453 | 58.746 | 29293.0583 | 3497:41 | 60.425 | 60.1813
18 | VIJAYAPUR | 224 | 224 | 427:26 | 6587:13 | 3063.6056 | 738:18 | 3094.3681 | 35402.9062 | 3112.1778 | 333:27 | 55.4382 | 55.1818 | 35677.3736 | 3822:35 | 56.8173 | 56.4825
19 | INDI | 301 | 301 | 562:50 | 16575:06 | 3845.8215 | 1269:05 | 3898.7 | 44153.0229 | 3922.1514 | 312:44 | 58.2178 | 57.9664 | 44843.6521 | 3575:34 | 59.9214 | 59.2945
20 | B.BAGEWADI | 172 | 172 | 1000:53 | 10339:11 | 1917.959 | 580:45 | 1942.1569 | 22474.3924 | 1983.8604 | 276:49 | 63.5755 | 62.7933 | 22905.1917 | 3196:04 | 64.2992 | 63.6148
21 | BAGALKOT | 234 | 234 | 1505:51 | 9079:06 | 2822.3854 | 1608:20 | 2889.3993 | 34078.6403 | 2952.1431 | 302:47 | 60.1682 | 59.3032 | 34456.9361 | 3534:03 | 60.209 | 59.7673
22 | JAMAKHANDI | 227 | 227 | 1257:26 | 7668:37 | 3217.0528 | 524:00 | 3238.8861 | 34590.1535 | 3291.2792 | 347:59 | 53.9735 | 53.2289 | 34909.6792 | 3690:53 | 58.3662 | 57.9817
23 | MUDHOL | 231 | 231 | 1305:08 | 7171:07 | 3388.1674 | 667:43 | 3415.9889 | 39127.4194 | 3470.3694 | 360:33 | 52.2973 | 51.5379 | 39426.216 | 4096:14 | 53.7206 | 53.3671
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]

## RURAL(Excl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2023 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of April-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Apr-23
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 50 | 50 | 178:08 | 178:08 | 816:33 | 1010:20 | 1826:53 | 1826:53 | 2005:01 | 40:06 | 94.9253 | 94.4305 | 2005:01 | 40:06 | 94.9253 | 94.4305
2 | DHARWAD RURAL | 99 | 99 | 94:01 | 94:01 | 2001:35 | 1712:43 | 3714:18 | 3714:18 | 3808:19 | 38:28 | 94.7891 | 94.6572 | 3808:19 | 38:28 | 94.7891 | 94.6572
3 | GADAG | 112 | 112 | 465:32 | 465:32 | 1440:02 | 1565:44 | 3005:46 | 3005:46 | 3471:18 | 31:00 | 96.2726 | 95.6953 | 3471:18 | 31:00 | 96.2726 | 95.6953
4 | RON | 61 | 61 | 185:05 | 185:05 | 823:28 | 1316:04 | 2139:32 | 2139:32 | 2324:37 | 38:07 | 95.1286 | 94.7072 | 2324:37 | 38:07 | 95.1286 | 94.7072
5 | HAVERI | 210 | 210 | 979:45 | 979:45 | 2215:00 | 3311:05 | 5526:05 | 5526:05 | 6505:50 | 30:59 | 96.3452 | 95.6972 | 6505:50 | 30:59 | 96.3452 | 95.6972
6 | RANEBENNUR | 212 | 212 | 878:04 | 878:04 | 2496:22 | 2441:52 | 4938:14 | 4938:14 | 5816:18 | 27:26 | 96.7648 | 96.1895 | 5816:18 | 27:26 | 96.7648 | 96.1895
7 | SIRSI | 59 | 58 | 194:23 | 194:23 | 381:11 | 1094:40 | 1475:51 | 1475:51 | 1670:14 | 28:19 | 96.5258 | 96.0682 | 1670:14 | 28:19 | 96.5258 | 96.0682
8 | DANDELI | 27 | 27 | 101:46 | 101:46 | 754:48 | 355:24 | 1110:12 | 1110:12 | 1211:58 | 44:53 | 94.2891 | 93.7656 | 1211:58 | 44:53 | 94.2891 | 93.7656
9 | KARWAR | 31 | 31 | 147:38 | 147:38 | 209:19 | 127:07 | 336:26 | 336:26 | 484:04 | 15:37 | 98.4927 | 97.8312 | 484:04 | 15:37 | 98.4927 | 97.8312
10 | HONNAVAR | 49 | 49 | 564:27 | 564:27 | 563:22 | 325:34 | 888:56 | 888:56 | 1453:23 | 29:40 | 97.4803 | 95.8804 | 1453:23 | 29:40 | 97.4803 | 95.8804
11 | BELAGAVI RURAL | 151 | 150 | 414:09 | 414:09 | 3602:21 | 3235:08 | 6837:29 | 6837:29 | 7251:38 | 48:01 | 93.7109 | 93.33 | 7251:38 | 48:01 | 93.7109 | 93.33
12 | BAILHONGAL | 206 | 205 | 1550:45 | 1550:45 | 4175:30 | 3732:19 | 7907:49 | 7907:49 | 9458:34 | 45:55 | 94.6684 | 93.6229 | 9458:34 | 45:55 | 94.6684 | 93.6229
13 | RAMDURG | 95 | 95 | 285:48 | 285:48 | 1968:54 | 1885:12 | 3854:06 | 3854:06 | 4139:54 | 43:35 | 94.3654 | 93.9475 | 4139:54 | 43:35 | 94.3654 | 93.9475
14 | GHATAPRABHA | 179 | 179 | 314:36 | 314:36 | 1780:54 | 2224:06 | 4005:00 | 4005:00 | 4319:36 | 24:08 | 96.8925 | 96.6484 | 4319:36 | 24:08 | 96.8925 | 96.6484
15 | RAIBAG | 183 | 179 | 333:16 | 333:16 | 4065:41 | 910:09 | 4975:50 | 4975:50 | 5309:06 | 29:01 | 96.2236 | 95.9706 | 5309:06 | 29:01 | 96.2236 | 95.9706
16 | ATHANI | 207 | 207 | 768:52 | 768:52 | 3546:04 | 1347:41 | 4893:45 | 4893:45 | 5662:37 | 27:21 | 96.7165 | 96.2006 | 5662:37 | 27:21 | 96.7165 | 96.2006
17 | CHIKKODI | 199 | 199 | 416:45 | 416:45 | 2282:53 | 2673:11 | 4956:04 | 4956:04 | 5372:49 | 27:00 | 96.541 | 96.2501 | 5372:49 | 27:00 | 96.541 | 96.2501
18 | VIJAYAPUR | 217 | 217 | 343:35 | 343:35 | 2136:27 | 3060:26 | 5196:53 | 5196:53 | 5540:28 | 25:32 | 96.6738 | 96.4539 | 5540:28 | 25:32 | 96.6738 | 96.4539
19 | INDI | 286 | 286 | 1877:44 | 1877:44 | 4547:46 | 7255:19 | 11803:05 | 11803:05 | 13680:49 | 47:50 | 94.2681 | 93.3562 | 13680:49 | 47:50 | 94.2681 | 93.3562
20 | B.BAGEWADI | 156 | 155 | 612:11 | 612:11 | 2279:05 | 3884:16 | 6163:21 | 6163:21 | 6775:32 | 43:26 | 94.5127 | 93.9677 | 6775:32 | 43:26 | 94.5127 | 93.9677
21 | BAGALKOT | 230 | 230 | 1111:51 | 1111:51 | 3969:57 | 5839:34 | 9809:31 | 9809:31 | 10921:22 | 47:29 | 94.0764 | 93.405 | 10921:22 | 47:29 | 94.0764 | 93.405
22 | JAMAKHANDI | 213 | 213 | 529:00 | 529:00 | 3207:22 | 1072:32 | 4279:54 | 4279:54 | 4808:54 | 22:35 | 97.2092 | 96.8643 | 4808:54 | 22:35 | 97.2092 | 96.8643
23 | MUDHOL | 213 | 213 | 756:42 | 756:42 | 2576:16 | 1947:07 | 4523:23 | 4523:23 | 5280:05 | 24:47 | 97.0505 | 96.5571 | 5280:05 | 24:47 | 97.0505 | 96.5571
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2023 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of May-2023 |  |  |  | Reliability for cumulative period from Apr-23 to May-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 50 | 50 | 295:01 | 473:09 | 1359:48 | 1983:01 | 3342:49 | 5169:42 | 3637:50 | 72:45 | 91.0139 | 90.2209 | 5642:51 | 112:51 | 92.9376 | 92.2912
2 | DHARWAD RURAL | 99 | 99 | 411:50 | 505:51 | 2498:29 | 4585:04 | 7083:33 | 10797:51 | 7495:23 | 75:43 | 90.3829 | 89.8238 | 11303:42 | 114:11 | 92.5499 | 92.2009
3 | GADAG | 115 | 114 | 231:04 | 696:36 | 1933:39 | 2649:44 | 4583:23 | 7589:09 | 4814:27 | 41:52 | 94.6431 | 94.373 | 8285:45 | 72:03 | 95.4923 | 95.0786
4 | RON | 59 | 59 | 56:50 | 241:55 | 812:20 | 1388:45 | 2201:05 | 4340:37 | 2257:55 | 38:16 | 94.9857 | 94.8562 | 4582:32 | 77:40 | 94.9747 | 94.6947
5 | HAVERI | 210 | 210 | 2475:28 | 3455:13 | 3695:35 | 11078:33 | 14774:08 | 20300:13 | 17249:36 | 82:08 | 90.5439 | 88.9595 | 23755:26 | 113:07 | 93.397 | 92.2731
6 | RANEBENNUR | 212 | 212 | 1390:19 | 2268:23 | 3821:53 | 9227:39 | 13049:32 | 17987:46 | 14439:51 | 68:07 | 91.7266 | 90.8451 | 20256:09 | 95:33 | 94.2044 | 93.4735
7 | SIRSI | 60 | 60 | 328:01 | 522:24 | 693:49 | 2374:31 | 3068:20 | 4544:11 | 3396:21 | 56:36 | 93.1265 | 92.3917 | 5066:35 | 84:27 | 94.8267 | 94.232
8 | DANDELI | 28 | 28 | 110:40 | 212:26 | 769:53 | 634:52 | 1404:45 | 2514:57 | 1515:25 | 54:07 | 93.2568 | 92.7255 | 2727:23 | 97:24 | 93.8648 | 93.3465
9 | KARWAR | 31 | 31 | 564:56 | 712:34 | 352:16 | 487:40 | 839:56 | 1176:22 | 1404:52 | 45:19 | 96.3582 | 93.9088 | 1888:56 | 60:56 | 97.408 | 95.8379
10 | HONNAVAR | 50 | 50 | 550:27 | 1114:54 | 696:56 | 683:52 | 1380:48 | 2269:44 | 1931:15 | 38:38 | 96.2882 | 94.8085 | 3384:38 | 67:42 | 96.8993 | 95.3762
11 | BELAGAVI RURAL | 152 | 149 | 586:22 | 1000:31 | 3512:03 | 4432:57 | 7945:00 | 14782:29 | 8531:22 | 56:08 | 92.9745 | 92.456 | 15783:00 | 103:50 | 93.357 | 92.9074
12 | BAILHONGAL | 215 | 215 | 2090:55 | 3641:40 | 4127:35 | 4758:40 | 8886:15 | 16794:04 | 10977:10 | 51:03 | 94.4447 | 93.1376 | 20435:44 | 95:03 | 94.6645 | 93.5075
13 | RAMDURG | 93 | 93 | 534:28 | 820:16 | 1544:34 | 2417:17 | 3961:51 | 7815:57 | 4496:19 | 48:21 | 94.2741 | 93.5017 | 8636:13 | 92:52 | 94.2594 | 93.6569
14 | GHATAPRABHA | 182 | 182 | 592:50 | 907:26 | 1982:34 | 4161:07 | 6143:41 | 10148:41 | 6736:31 | 37:01 | 95.4628 | 95.025 | 11056:07 | 60:45 | 96.1911 | 95.8506
15 | RAIBAG | 182 | 182 | 251:20 | 584:36 | 4492:00 | 2268:11 | 6760:11 | 11736:01 | 7011:31 | 38:31 | 95.0075 | 94.8219 | 12320:37 | 67:42 | 95.5954 | 95.376
16 | ATHANI | 209 | 209 | 1026:05 | 1794:57 | 3811:23 | 3230:14 | 7041:37 | 11935:22 | 8067:42 | 38:36 | 95.4715 | 94.8116 | 13730:19 | 65:42 | 96.0992 | 95.5126
17 | CHIKKODI | 199 | 199 | 436:00 | 852:45 | 2050:58 | 2337:36 | 4388:34 | 9344:38 | 4824:34 | 24:15 | 97.0359 | 96.7414 | 10197:23 | 51:15 | 96.7925 | 96.4998
18 | VIJAYAPUR | 214 | 214 | 512:30 | 856:05 | 2468:01 | 6045:07 | 8513:08 | 13710:01 | 9025:38 | 42:11 | 94.6531 | 94.3312 | 14566:06 | 68:04 | 95.6239 | 95.3507
19 | INDI | 289 | 288 | 1129:31 | 3007:15 | 4785:34 | 8258:28 | 13044:02 | 1035.2965 | 14173:33 | 49:03 | 93.9335 | 93.4081 | 1160.5986 | 96:23 | 94.1273 | 93.4165
20 | B.BAGEWADI | 155 | 155 | 486:45 | 1098:56 | 2439:29 | 3953:27 | 6392:56 | 12556:17 | 6879:41 | 44:23 | 94.4564 | 94.0343 | 13655:13 | 88:06 | 94.4666 | 93.9824
21 | BAGALKOT | 228 | 228 | 449:57 | 1561:48 | 2854:32 | 5337:27 | 8191:59 | 18001:30 | 8641:56 | 37:54 | 95.1707 | 94.9055 | 19563:18 | 85:48 | 94.607 | 94.1391
22 | JAMAKHANDI | 214 | 214 | 483:21 | 1012:21 | 3263:46 | 3056:32 | 6320:18 | 10600:12 | 6803:39 | 31:48 | 96.0304 | 95.7268 | 11612:33 | 54:16 | 96.6166 | 96.2934
23 | MUDHOL | 215 | 216 | 362:59 | 1119:41 | 2388:08 | 2928:08 | 5316:16 | 9839:39 | 5679:15 | 26:25 | 96.6765 | 96.4496 | 10959:20 | 50:58 | 96.8739 | 96.5182
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2023 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of June-2023 |  |  |  | Reliability for cumulative period from Apr-23 to June-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 50 | 50 | 255:02 | 728:11 | 1336:30 | 1485:27 | 2821:57 | 7991:39 | 3076:59 | 61:32 | 92.1613 | 91.4528 | 8719:50 | 174:24 | 92.6816 | 92.0148
2 | DHARWAD RURAL | 99 | 99 | 52:02 | 557:53 | 2402:40 | 3216:33 | 5619:13 | 16417:04 | 5671:15 | 57:17 | 92.1167 | 92.0437 | 16974:57 | 171:28 | 92.4071 | 92.1491
3 | GADAG | 115 | 114 | 549:14 | 1245:50 | 2121:08 | 2758:11 | 4879:19 | 12468:28 | 5428:33 | 47:12 | 94.1071 | 93.4438 | 13714:18 | 119:15 | 95.0356 | 94.5396
4 | RON | 60 | 60 | 174:28 | 416:23 | 1259:58 | 1266:02 | 2526:00 | 6866:37 | 2700:28 | 45:00 | 94.1528 | 93.7489 | 7283:00 | 121:23 | 94.7599 | 94.4422
5 | HAVERI | 211 | 211 | 1929:17 | 5384:30 | 4845:32 | 8939:01 | 13784:33 | 1420.1986 | 15713:50 | 74:28 | 90.9264 | 89.6565 | 1644.5528 | 187:03 | 92.6035 | 91.4351
6 | RANEBENNUR | 213 | 213 | 1057:56 | 3326:19 | 3758:48 | 5160:38 | 8919:26 | 1121.1333 | 9977:22 | 46:51 | 94.184 | 93.4942 | 1259.7299 | 141:56 | 94.2159 | 93.5009
7 | SIRSI | 61 | 61 | 413:26 | 935:50 | 767:41 | 2728:02 | 3495:43 | 8039:54 | 3909:09 | 64:05 | 92.0407 | 91.0994 | 8975:44 | 147:09 | 93.9651 | 93.2627
8 | DANDELI | 28 | 25 | 116:03 | 328:29 | 294:03 | 639:14 | 933:17 | 3448:14 | 1049:20 | 37:29 | 95.3706 | 94.795 | 3776:43 | 134:53 | 94.3612 | 93.8241
9 | KARWAR | 31 | 31 | 366:32 | 1079:06 | 375:30 | 831:50 | 1207:20 | 2383:42 | 1573:52 | 50:46 | 94.5908 | 92.9486 | 3462:48 | 111:42 | 96.4792 | 94.8854
10 | HONNAVAR | 52 | 51 | 766:50 | 1881:44 | 757:18 | 1245:10 | 2002:28 | 4272:12 | 2769:18 | 53:15 | 94.6515 | 92.6034 | 6153:56 | 118:21 | 96.2382 | 94.5813
11 | BELAGAVI RURAL | 153 | 153 | 431:25 | 1431:56 | 3584:12 | 3256:10 | 6840:22 | 21622:51 | 7271:47 | 47:32 | 93.7905 | 93.3989 | 23054:47 | 150:41 | 93.529 | 93.1005
12 | BAILHONGAL | 216 | 215 | 1741:08 | 5382:48 | 4382:11 | 4613:26 | 8995:37 | 1074.5701 | 10736:45 | 49:42 | 94.2158 | 93.0962 | 1298.8535 | 144:19 | 94.5331 | 93.3921
13 | RAMDURG | 95 | 95 | 754:02 | 1574:18 | 1727:10 | 1574:56 | 3302:06 | 11118:03 | 4056:08 | 42:42 | 95.1724 | 94.07 | 12692:21 | 133:36 | 94.6414 | 93.8826
14 | GHATAPRABHA | 185 | 185 | 431:43 | 1339:09 | 1874:11 | 2364:52 | 4239:03 | 14387:44 | 4670:46 | 25:15 | 96.8175 | 96.4934 | 15726:53 | 85:01 | 96.439 | 96.1076
15 | RAIBAG | 181 | 181 | 461:06 | 1045:42 | 5025:10 | 1037:47 | 6062:57 | 17798:58 | 6524:03 | 36:03 | 95.3476 | 94.9938 | 18844:40 | 104:07 | 95.4974 | 95.2329
16 | ATHANI | 209 | 209 | 731:45 | 2526:42 | 5826:41 | 2006:25 | 7833:06 | 19768:28 | 8564:51 | 40:59 | 94.7946 | 94.3083 | 22295:10 | 106:41 | 95.6691 | 95.1156
17 | CHIKKODI | 198 | 198 | 357:05 | 1209:50 | 1954:51 | 1475:05 | 3429:56 | 12774:34 | 3787:01 | 19:08 | 97.594 | 97.3436 | 13984:24 | 70:38 | 97.0459 | 96.7661
18 | VIJAYAPUR | 215 | 215 | 1226:49 | 2082:54 | 2550:52 | 3944:20 | 6495:12 | 20205:13 | 7722:01 | 35:55 | 95.8041 | 95.0116 | 22288:07 | 103:40 | 95.697 | 95.2534
19 | INDI | 292 | 291 | 1828:25 | 4835:40 | 4719:58 | 7284:41 | 12004:39 | 1535.4903 | 13833:04 | 47:22 | 94.29 | 93.4203 | 1736.9764 | 142:46 | 94.2214 | 93.4631
20 | B.BAGEWADI | 155 | 155 | 1048:08 | 2147:04 | 2799:12 | 3686:17 | 6485:29 | 19041:46 | 7533:37 | 48:36 | 94.1886 | 93.2494 | 21188:50 | 136:42 | 94.375 | 93.7407
21 | BAGALKOT | 230 | 229 | 1041:58 | 2603:46 | 4245:19 | 3942:32 | 8187:51 | 1091.2229 | 9229:49 | 40:08 | 95.0556 | 94.4264 | 1199.7132 | 125:11 | 94.7863 | 94.268
22 | JAMAKHANDI | 214 | 214 | 906:01 | 1918:22 | 5661:46 | 1421:10 | 7082:56 | 17683:08 | 7988:57 | 37:20 | 95.4031 | 94.8151 | 19601:30 | 91:36 | 96.2165 | 95.8061
23 | MUDHOL | 219 | 219 | 1359:43 | 2479:24 | 2388:49 | 1518:07 | 3906:56 | 13746:35 | 5266:39 | 24:03 | 97.5222 | 96.6599 | 16225:59 | 74:05 | 97.1259 | 96.6075
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of July-2023 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of July-2023 |  |  |  | Reliability for cumulative period from Apr-23 to July-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 50 | 50 | 250:02 | 978:13 | 1166:12 | 2406:39 | 3572:51 | 11564:30 | 3822:53 | 76:27 | 90.3956 | 89.7234 | 12542:43 | 250:51 | 92.1008 | 91.4326
2 | DHARWAD RURAL | 99 | 99 | 85:45 | 643:38 | 2608:47 | 4710:16 | 7319:03 | 23736:07 | 7404:48 | 74:48 | 90.0632 | 89.9468 | 1015.8229 | 246:16 | 91.8115 | 91.5895
3 | GADAG | 115 | 112 | 235:09 | 1480:59 | 2104:04 | 3336:38 | 5440:42 | 17909:10 | 5675:51 | 49:21 | 93.6411 | 93.3662 | 19390:09 | 168:37 | 94.6813 | 94.2415
4 | RON | 60 | 60 | 91:08 | 507:31 | 894:20 | 1344:40 | 2239:00 | 9105:37 | 2330:08 | 38:50 | 94.9843 | 94.7802 | 9613:08 | 160:13 | 94.8169 | 94.528
5 | HAVERI | 211 | 211 | 731:10 | 6115:40 | 4160:32 | 13275:53 | 17436:25 | 2146.716 | 18167:35 | 86:06 | 88.8929 | 88.4271 | 2401.5354 | 273:10 | 91.6606 | 90.6708
6 | RANEBENNUR | 213 | 213 | 477:27 | 3803:46 | 3554:50 | 11769:39 | 15324:29 | 1759.6535 | 15801:56 | 74:11 | 90.3298 | 90.0286 | 1918.1437 | 216:08 | 93.2285 | 92.6185
7 | SIRSI | 61 | 61 | 358:06 | 1293:56 | 1187:26 | 688:02 | 1875:28 | 9915:22 | 2233:34 | 36:37 | 95.8676 | 95.0785 | 11209:18 | 183:46 | 94.4485 | 93.7241
8 | DANDELI | 28 | 28 | 74:14 | 402:43 | 481:59 | 1362:27 | 1844:26 | 5292:40 | 1918:40 | 68:31 | 91.1462 | 90.7898 | 5695:23 | 203:24 | 93.5443 | 93.0531
9 | KARWAR | 31 | 31 | 509:56 | 1589:02 | 521:51 | 1159:56 | 1681:47 | 4065:29 | 2191:43 | 70:42 | 92.7082 | 90.4972 | 5654:31 | 182:24 | 95.521 | 93.7704
10 | HONNAVAR | 51 | 51 | 1219:05 | 3100:49 | 1446:41 | 2166:34 | 3613:15 | 7885:27 | 4832:20 | 94:45 | 90.4774 | 87.2646 | 10986:16 | 215:25 | 94.7194 | 92.6429
11 | BELAGAVI RURAL | 153 | 149 | 187:53 | 1619:49 | 4120:15 | 4620:30 | 8740:45 | 1265.15 | 8928:38 | 58:21 | 92.3214 | 92.1563 | 1332.6424 | 209:03 | 93.2222 | 92.8606
12 | BAILHONGAL | 212 | 211 | 1363:39 | 6746:27 | 3891:20 | 6526:17 | 10417:37 | 1508.6375 | 11781:16 | 55:34 | 93.3952 | 92.5306 | 1789.7396 | 202:37 | 94.167 | 93.0802
13 | RAMDURG | 93 | 93 | 528:04 | 2102:22 | 1179:51 | 2118:40 | 3298:31 | 14416:34 | 3826:35 | 41:09 | 95.2328 | 94.4696 | 16518:56 | 177:37 | 94.7057 | 93.9336
14 | GHATAPRABHA | 184 | 184 | 165:32 | 1504:41 | 1666:50 | 2259:55 | 3926:45 | 18314:29 | 4092:17 | 22:14 | 97.1316 | 97.0107 | 19819:10 | 107:43 | 96.6006 | 96.3213
15 | RAIBAG | 181 | 181 | 62:30 | 1108:12 | 3705:34 | 1289:38 | 4995:12 | 22794:10 | 5057:42 | 27:57 | 96.2906 | 96.2442 | 23902:22 | 132:03 | 95.699 | 95.4898
16 | ATHANI | 211 | 211 | 310:24 | 2837:06 | 3970:34 | 2156:04 | 6126:38 | 1078.9625 | 6437:02 | 30:30 | 96.0973 | 95.8996 | 1197.175 | 136:10 | 95.8086 | 95.3493
17 | CHIKKODI | 199 | 199 | 210:05 | 1419:55 | 2137:20 | 2872:49 | 5010:09 | 17784:43 | 5220:14 | 26:14 | 96.616 | 96.4741 | 19204:38 | 96:30 | 96.9477 | 96.704
18 | VIJAYAPUR | 218 | 218 | 334:52 | 2417:46 | 2964:59 | 5734:10 | 8699:09 | 1204.3486 | 9034:01 | 41:26 | 94.6365 | 94.43 | 1305.0889 | 143:41 | 95.4717 | 95.0929
19 | INDI | 295 | 295 | 1813:06 | 6648:46 | 5173:34 | 13102:37 | 18276:11 | 2296.9979 | 20089:17 | 68:06 | 91.673 | 90.8469 | 2574.0299 | 209:25 | 93.6177 | 92.8479
20 | B.BAGEWADI | 155 | 155 | 633:04 | 2780:08 | 3664:53 | 5231:09 | 8896:02 | 1164.075 | 9529:06 | 61:29 | 92.2858 | 91.7368 | 1279.9139 | 198:11 | 93.8441 | 93.2316
21 | BAGALKOT | 230 | 230 | 473:55 | 3077:41 | 3482:37 | 6596:10 | 10078:47 | 1511.1722 | 10552:42 | 45:53 | 94.1101 | 93.8332 | 1639.409 | 171:04 | 94.6145 | 94.1575
22 | JAMAKHANDI | 215 | 214 | 912:38 | 2831:00 | 4894:47 | 1401:38 | 6296:25 | 23979:33 | 7209:03 | 33:32 | 96.0638 | 95.4932 | 1117.1063 | 124:42 | 96.1908 | 95.7411
23 | MUDHOL | 219 | 219 | 232:12 | 2711:36 | 2045:37 | 2417:13 | 4462:50 | 18209:25 | 4695:02 | 21:26 | 97.261 | 97.1185 | 20921:01 | 95:32 | 97.1602 | 96.7374
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of August-2023 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of August-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Aug-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 52 | 52 | 113:18 | 1091:31 | 650:10 | 1355:00 | 2005:10 | 13569:40 | 2118:28 | 40:44 | 94.8171 | 94.5242 | 14661:11 | 281:57 | 92.8934 | 92.3217
2 | DHARWAD RURAL | 103 | 103 | 339:25 | 983:03 | 3738:19 | 1692:11 | 5430:30 | 1215.2757 | 5769:55 | 56:01 | 92.9135 | 92.4706 | 1256.2361 | 292:43 | 92.2884 | 92.0285
3 | GADAG | 117 | 116 | 137:55 | 1618:54 | 1753:23 | 2973:48 | 4727:11 | 22636:21 | 4865:06 | 41:35 | 94.5695 | 94.411 | 1010.6354 | 207:19 | 94.7311 | 94.3543
4 | RON | 60 | 60 | 86:45 | 594:16 | 748:56 | 774:25 | 1523:21 | 10628:58 | 1610:06 | 26:50 | 96.5875 | 96.3931 | 11223:14 | 187:03 | 95.1757 | 94.9059
5 | HAVERI | 212 | 212 | 1192:20 | 7308:00 | 3947:43 | 3838:43 | 7786:26 | 2471.1507 | 8978:46 | 42:21 | 95.0634 | 94.3074 | 2775.6507 | 314:13 | 92.3815 | 91.4427
6 | RANEBENNUR | 214 | 214 | 1903:58 | 5707:44 | 3784:17 | 2944:56 | 6729:13 | 2040.0375 | 8633:11 | 40:21 | 95.7735 | 94.5777 | 2277.8597 | 255:28 | 93.7694 | 93.043
7 | SIRSI | 61 | 61 | 326:47 | 1620:43 | 715:10 | 1581:58 | 2297:08 | 12212:30 | 2623:55 | 43:01 | 94.9385 | 94.2184 | 13833:13 | 226:46 | 94.5478 | 93.8242
8 | DANDELI | 28 | 28 | 100:06 | 502:49 | 299:39 | 512:20 | 811:59 | 6104:39 | 912:05 | 32:34 | 96.1022 | 95.6217 | 6607:28 | 235:59 | 94.0625 | 93.5735
9 | KARWAR | 31 | 31 | 153:37 | 1742:39 | 307:12 | 467:52 | 775:04 | 4840:33 | 928:41 | 29:57 | 96.6395 | 95.9735 | 6583:12 | 212:22 | 95.7476 | 94.2167
10 | HONNAVAR | 52 | 52 | 335:40 | 3436:29 | 543:06 | 487:33 | 1030:39 | 8916:06 | 1366:19 | 26:17 | 97.336 | 96.4684 | 12352:35 | 237:33 | 95.3305 | 93.5308
11 | BELAGAVI RURAL | 152 | 152 | 348:22 | 1968:11 | 4225:15 | 1910:57 | 6136:12 | 1520.825 | 6484:34 | 42:40 | 94.574 | 94.2659 | 1602.8326 | 253:05 | 93.4605 | 93.1079
12 | BAILHONGAL | 215 | 215 | 1266:16 | 8012:43 | 4422:26 | 2283:56 | 6706:22 | 1788.0694 | 7972:38 | 37:05 | 95.8075 | 95.0159 | 2121.9326 | 236:52 | 94.5643 | 93.5494
13 | RAMDURG | 96 | 96 | 546:40 | 2649:02 | 1149:57 | 1442:10 | 2592:07 | 17008:41 | 3138:47 | 32:42 | 96.3708 | 95.6054 | 19657:43 | 204:46 | 95.175 | 94.4235
14 | GHATAPRABHA | 185 | 185 | 390:01 | 1894:42 | 1480:35 | 995:36 | 2476:11 | 20790:40 | 2866:12 | 15:30 | 98.201 | 97.9176 | 22685:22 | 122:37 | 96.9395 | 96.6606
15 | RAIBAG | 186 | 186 | 308:31 | 1416:43 | 3696:58 | 697:56 | 4394:54 | 1132.8778 | 4703:25 | 25:17 | 96.8241 | 96.6012 | 1191.9076 | 153:48 | 96.0191 | 95.8117
16 | ATHANI | 214 | 214 | 914:47 | 3751:53 | 4462:10 | 959:29 | 5421:39 | 1304.8646 | 6336:26 | 29:37 | 96.5948 | 96.0202 | 1461.1931 | 163:52 | 96.0147 | 95.5373
17 | CHIKKODI | 198 | 198 | 941:43 | 2361:38 | 2557:44 | 1211:55 | 3769:39 | 21554:22 | 4711:22 | 23:48 | 97.441 | 96.8018 | 23916:00 | 120:47 | 97.0354 | 96.7106
18 | VIJAYAPUR | 219 | 219 | 692:45 | 3110:31 | 2755:31 | 2423:48 | 5179:19 | 1420.1535 | 5872:04 | 26:49 | 96.8213 | 96.3961 | 1549.7583 | 169:50 | 95.7616 | 95.3748
19 | INDI | 298 | 298 | 3032:09 | 9680:55 | 4122:31 | 5124:19 | 9246:50 | 2682.2826 | 12278:59 | 41:12 | 95.8293 | 94.4617 | 3085.6542 | 248:31 | 94.117 | 93.2323
20 | B.BAGEWADI | 164 | 164 | 2163:32 | 4943:40 | 2429:57 | 2748:41 | 5178:38 | 1379.8514 | 7342:10 | 44:46 | 95.7558 | 93.9826 | 1585.8375 | 232:04 | 94.5008 | 93.6799
21 | BAGALKOT | 232 | 232 | 731:15 | 3808:56 | 2830:24 | 3165:20 | 5995:44 | 1760.9944 | 6726:59 | 29:00 | 96.5264 | 96.1027 | 1919.7 | 198:35 | 95.0389 | 94.5918
22 | JAMAKHANDI | 218 | 218 | 1425:12 | 4256:12 | 4189:46 | 987:32 | 5177:18 | 1214.8688 | 6602:30 | 30:17 | 96.8079 | 95.9292 | 1392.2104 | 153:16 | 96.3577 | 95.826
23 | MUDHOL | 221 | 221 | 1711:02 | 4422:38 | 1667:46 | 961:14 | 2629:00 | 20838:25 | 4340:02 | 19:38 | 98.4011 | 97.3605 | 1052.5438 | 114:18 | 97.4321 | 96.8872
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of September-2023 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of Sept-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Sept-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 53 | 53 | 42:59 | 1134:30 | 822:10 | 799:54 | 1622:04 | 15191:44 | 1665:03 | 31:25 | 95.7493 | 95.6367 | 16326:14 | 308:03 | 93.4737 | 92.9863
2 | DHARWAD RURAL | 104 | 102 | 108:30 | 1091:33 | 1329:49 | 1502:04 | 2831:53 | 1333.2708 | 2940:23 | 28:16 | 96.2181 | 96.0732 | 1378.7521 | 318:10 | 92.9946 | 92.7556
3 | GADAG | 116 | 114 | 531:10 | 2150:04 | 1879:49 | 1680:38 | 3560:27 | 1091.5333 | 4091:37 | 35:16 | 95.737 | 95.101 | 1181.1194 | 244:22 | 94.858 | 94.436
4 | RON | 62 | 61 | 150:50 | 745:06 | 1032:39 | 692:47 | 1725:26 | 12354:24 | 1876:16 | 30:16 | 96.1348 | 95.7969 | 13099:30 | 211:17 | 95.463 | 95.1894
5 | HAVERI | 213 | 213 | 1585:13 | 8893:13 | 3157:13 | 3617:51 | 6775:04 | 2753.4451 | 8360:17 | 39:15 | 95.5822 | 94.5486 | 3123.9958 | 352:00 | 92.9361 | 91.9854
6 | RANEBENNUR | 214 | 214 | 578:18 | 6286:02 | 2292:35 | 2481:53 | 4774:28 | 2238.9736 | 5352:46 | 25:01 | 96.9013 | 96.526 | 2500.8917 | 280:28 | 94.2828 | 93.614
7 | SIRSI | 61 | 61 | 152:35 | 1773:18 | 634:32 | 1545:20 | 2179:52 | 14392:22 | 2332:27 | 38:14 | 95.0367 | 94.6893 | 16165:40 | 265:01 | 94.6279 | 93.9661
8 | DANDELI | 29 | 29 | 224:12 | 727:01 | 313:44 | 514:30 | 828:14 | 6932:53 | 1052:26 | 36:17 | 96.0334 | 94.9596 | 7659:54 | 264:08 | 94.5568 | 93.986
9 | KARWAR | 31 | 31 | 328:12 | 2070:51 | 373:47 | 638:21 | 1012:08 | 5852:41 | 1340:20 | 43:14 | 95.4654 | 93.9949 | 7923:32 | 255:36 | 95.7014 | 94.1804
10 | HONNAVAR | 52 | 52 | 824:08 | 4260:37 | 622:18 | 837:22 | 1459:40 | 10375:46 | 2283:48 | 43:55 | 96.1013 | 93.9001 | 14636:23 | 281:28 | 95.4569 | 93.5913
11 | BELAGAVI RURAL | 153 | 152 | 574:27 | 2542:38 | 2787:52 | 2025:44 | 4813:36 | 1721.3917 | 5388:03 | 35:13 | 95.6304 | 95.1089 | 1827.3347 | 286:38 | 93.852 | 93.4736
12 | BAILHONGAL | 223 | 223 | 1531:10 | 9543:53 | 3145:51 | 2708:42 | 5854:33 | 2032.009 | 7385:43 | 33:07 | 96.3537 | 95.4 | 2429.6708 | 261:29 | 95.0207 | 94.0462
13 | RAMDURG | 97 | 97 | 352:44 | 3001:46 | 1018:05 | 1558:50 | 2576:55 | 19585:36 | 2929:39 | 30:12 | 96.3103 | 95.8052 | 22587:22 | 232:52 | 95.4027 | 94.6981
14 | GHATAPRABHA | 190 | 190 | 202:17 | 2096:59 | 1413:28 | 1830:48 | 3244:16 | 1001.4556 | 3446:33 | 18:08 | 97.6285 | 97.4806 | 1088.8299 | 137:32 | 97.1198 | 96.8685
15 | RAIBAG | 188 | 188 | 276:37 | 1693:20 | 3606:44 | 1050:31 | 4657:15 | 1326.9299 | 4933:52 | 26:15 | 96.5594 | 96.355 | 1397.4854 | 178:24 | 96.1431 | 95.938
16 | ATHANI | 217 | 217 | 810:53 | 4562:46 | 3569:20 | 1638:31 | 5207:51 | 1521.8583 | 6018:44 | 27:44 | 96.6668 | 96.1478 | 1711.9736 | 189:21 | 96.1677 | 95.6889
17 | CHIKKODI | 198 | 198 | 446:45 | 2808:23 | 1363:44 | 1278:23 | 2642:07 | 1008.1868 | 3088:52 | 15:36 | 98.1467 | 97.8333 | 1125.2028 | 136:23 | 97.2176 | 96.8946
18 | VIJAYAPUR | 218 | 218 | 750:33 | 3861:04 | 1700:56 | 3528:01 | 5228:57 | 1638.0264 | 5979:30 | 27:26 | 96.6686 | 96.1904 | 1798.9042 | 198:03 | 95.8941 | 95.4908
19 | INDI | 299 | 299 | 2661:03 | 12341:58 | 3346:35 | 7816:49 | 11163:24 | 3147.4243 | 13824:27 | 46:14 | 94.8145 | 93.5784 | 3661.6729 | 293:55 | 94.2478 | 93.308
20 | B.BAGEWADI | 164 | 164 | 394:29 | 5338:09 | 1921:58 | 3256:57 | 5178:55 | 1595.6396 | 5573:24 | 33:59 | 95.6141 | 95.28 | 1818.0625 | 266:03 | 94.6833 | 93.9422
21 | BAGALKOT | 232 | 233 | 874:50 | 4683:46 | 2878:23 | 4552:39 | 7431:02 | 2070.6208 | 8305:52 | 35:48 | 95.5513 | 95.0276 | 2265.7778 | 234:23 | 95.1229 | 94.6632
22 | JAMAKHANDI | 219 | 219 | 337:06 | 4593:18 | 2327:10 | 1584:38 | 3911:48 | 1377.8604 | 4248:54 | 19:24 | 97.5192 | 97.3054 | 1569.2479 | 171:58 | 96.562 | 96.0844
23 | MUDHOL | 221 | 221 | 211:45 | 4634:23 | 1664:57 | 1950:33 | 3615:30 | 1018.9132 | 3827:15 | 17:19 | 97.7278 | 97.5947 | 1212.0125 | 131:37 | 97.4806 | 97.0032
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of October-2023 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of October-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Oct-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 53 | 53 | 50:26 | 1184:56 | 693:39 | 447:31 | 1141:10 | 16332:54 | 1191:36 | 22:29 | 97.106 | 96.9781 | 17517:50 | 330:32 | 93.9998 | 93.5645
2 | DHARWAD RURAL | 103 | 103 | 61:07 | 1152:40 | 1362:23 | 1570:42 | 2933:05 | 1455.4826 | 2994:12 | 29:04 | 96.1725 | 96.0928 | 1503.5104 | 350:20 | 93.3968 | 93.1789
3 | GADAG | 116 | 115 | 82:55 | 2232:59 | 1478:10 | 737:46 | 2215:56 | 1183.8639 | 2298:51 | 19:49 | 97.4324 | 97.3363 | 1276.9049 | 264:11 | 95.231 | 94.8562
4 | RON | 61 | 61 | 28:55 | 774:01 | 545:27 | 342:29 | 887:56 | 13242:20 | 916:51 | 15:02 | 98.0435 | 97.9798 | 14016:21 | 229:47 | 95.7732 | 95.5262
5 | HAVERI | 213 | 213 | 1460:44 | 10353:57 | 3097:10 | 2669:34 | 5766:44 | 2993.7257 | 7227:28 | 33:56 | 96.361 | 95.4393 | 3425.1403 | 385:56 | 93.4322 | 92.4858
6 | RANEBENNUR | 214 | 214 | 664:38 | 6950:40 | 2163:25 | 2022:45 | 4186:10 | 2413.3972 | 4850:48 | 22:40 | 97.3708 | 96.9533 | 2703.0083 | 303:08 | 94.7301 | 94.0977
7 | SIRSI | 61 | 61 | 341:30 | 2114:48 | 767:59 | 1534:01 | 2302:00 | 16694:22 | 2643:30 | 43:20 | 94.9277 | 94.1753 | 18809:10 | 308:21 | 94.6714 | 93.9964
8 | DANDELI | 30 | 30 | 224:55 | 951:56 | 185:50 | 543:02 | 728:52 | 7661:45 | 953:47 | 31:48 | 96.7345 | 95.7268 | 8613:41 | 287:07 | 95.0274 | 94.4096
9 | KARWAR | 31 | 31 | 189:32 | 2260:23 | 257:15 | 437:45 | 695:00 | 6547:41 | 884:32 | 28:32 | 96.9866 | 96.1649 | 8808:04 | 284:08 | 95.8875 | 94.4679
10 | HONNAVAR | 52 | 52 | 640:30 | 4901:07 | 623:16 | 684:02 | 1307:18 | 11683:04 | 1947:48 | 37:27 | 96.6209 | 94.9654 | 16584:11 | 318:56 | 95.6255 | 93.7904
11 | BELAGAVI RURAL | 153 | 151 | 387:51 | 2930:29 | 2551:45 | 1764:35 | 4316:20 | 1901.2389 | 4704:11 | 30:45 | 96.2082 | 95.8674 | 2023.3424 | 317:23 | 94.1933 | 93.8203
12 | BAILHONGAL | 227 | 227 | 1099:04 | 10642:57 | 3383:41 | 1731:20 | 5115:01 | 2245.1347 | 6214:05 | 27:22 | 96.9714 | 96.3206 | 2688.591 | 284:15 | 95.3783 | 94.4654
13 | RAMDURG | 97 | 97 | 277:38 | 3279:24 | 750:49 | 812:39 | 1563:28 | 21149:04 | 1841:06 | 18:59 | 97.8336 | 97.4489 | 1017.8528 | 251:50 | 95.7548 | 95.0966
14 | GHATAPRABHA | 190 | 190 | 311:18 | 2408:17 | 1837:44 | 900:08 | 2737:52 | 1115.5333 | 3049:10 | 16:03 | 98.0632 | 97.843 | 1215.8785 | 153:35 | 97.2564 | 97.0096
15 | RAIBAG | 189 | 189 | 262:13 | 1955:33 | 3847:21 | 660:19 | 4507:40 | 1514.7493 | 4769:53 | 25:14 | 96.7943 | 96.6079 | 1596.2306 | 202:42 | 96.2549 | 96.0534
16 | ATHANI | 219 | 219 | 605:48 | 5168:34 | 3373:31 | 1253:37 | 4627:08 | 1714.6556 | 5232:56 | 23:54 | 97.1602 | 96.7884 | 1930.0125 | 211:30 | 96.3414 | 95.8818
17 | CHIKKODI | 198 | 198 | 270:17 | 3078:40 | 1400:53 | 851:27 | 2252:20 | 1102.034 | 2522:37 | 12:44 | 98.471 | 98.2876 | 1230.3118 | 149:08 | 97.3991 | 97.0964
18 | VIJAYAPUR | 219 | 219 | 991:10 | 4852:14 | 4145:42 | 2003:15 | 6148:57 | 1894.2326 | 7140:07 | 32:36 | 96.2262 | 95.6178 | 2096.409 | 229:45 | 95.9582 | 95.5268
19 | INDI | 299 | 298 | 901:12 | 13243:10 | 2296:53 | 5111:35 | 7408:28 | 3456.1104 | 8309:40 | 27:47 | 96.6697 | 96.2646 | 4007.909 | 321:42 | 94.5986 | 93.7363
20 | B.BAGEWADI | 167 | 166 | 2629:08 | 7967:17 | 2253:56 | 1319:53 | 3573:49 | 1744.5486 | 6202:57 | 37:09 | 97.1236 | 95.0076 | 2076.5188 | 298:25 | 95.1185 | 94.1896
21 | BAGALKOT | 233 | 233 | 1287:22 | 5971:08 | 2387:51 | 2947:25 | 5335:16 | 2292.9236 | 6622:38 | 28:25 | 96.9223 | 96.1797 | 2541.7208 | 261:48 | 95.4015 | 94.9025
22 | JAMAKHANDI | 224 | 222 | 898:56 | 5492:14 | 6225:52 | 930:34 | 7156:26 | 1676.0451 | 8055:22 | 35:58 | 95.7059 | 95.1665 | 1904.8882 | 204:06 | 96.5036 | 96.0262
23 | MUDHOL | 222 | 222 | 627:50 | 5262:13 | 1735:56 | 1244:31 | 2980:27 | 1143.0986 | 3608:17 | 16:15 | 98.1955 | 97.8154 | 1362.3576 | 147:17 | 97.5939 | 97.1324
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of NOVEMBER-2023 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of November-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Nov23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 53 | 53 | 93:10 | 1278:06 | 539:01 | 586:34 | 1125:35 | 17458:29 | 1218:45 | 23:00 | 97.0504 | 96.8062 | 18736:35 | 353:31 | 94.3749 | 93.9631
2 | DHARWAD RURAL | 102 | 102 | 90:30 | 1243:10 | 1661:20 | 1235:54 | 2897:14 | 1576.2007 | 2987:44 | 29:17 | 96.055 | 95.9317 | 1627.9993 | 383:04 | 93.6668 | 93.4587
3 | GADAG | 116 | 116 | 112:40 | 2345:39 | 1250:20 | 1156:49 | 2407:09 | 1284.1618 | 2519:49 | 21:43 | 97.1179 | 96.983 | 1381.8972 | 285:55 | 95.463 | 95.1177
4 | RON | 61 | 61 | 125:22 | 899:23 | 599:11 | 477:24 | 1076:35 | 14318:55 | 1201:57 | 19:42 | 97.5488 | 97.2633 | 15218:18 | 249:29 | 95.9915 | 95.7397
5 | HAVERI | 213 | 213 | 1014:27 | 11368:24 | 3430:42 | 3549:15 | 6979:57 | 3284.5569 | 7994:24 | 37:32 | 95.4487 | 94.7872 | 3758.2403 | 423:28 | 93.6801 | 92.7687
6 | RANEBENNUR | 216 | 216 | 674:20 | 7625:00 | 2328:53 | 3124:22 | 5453:15 | 2640.616 | 6127:35 | 28:22 | 96.4935 | 96.0599 | 2958.3243 | 328:42 | 94.9897 | 94.3869
7 | SIRSI | 61 | 61 | 341:30 | 2456:18 | 767:59 | 1534:01 | 2302:00 | 18996:22 | 2643:30 | 43:20 | 94.7587 | 93.9811 | 21452:40 | 351:41 | 94.6821 | 93.9945
8 | DANDELI | 30 | 30 | 88:42 | 1040:38 | 189:47 | 288:52 | 478:39 | 8140:24 | 567:21 | 18:55 | 97.784 | 97.3734 | 9181:02 | 306:02 | 95.3663 | 94.774
9 | KARWAR | 31 | 31 | 226:59 | 2487:22 | 243:11 | 369:28 | 612:39 | 7160:20 | 839:38 | 27:05 | 97.2552 | 96.2382 | 9647:42 | 311:13 | 96.0557 | 94.6855
10 | HONNAVAR | 53 | 53 | 347:16 | 5248:23 | 552:50 | 481:42 | 1034:32 | 12717:36 | 1381:48 | 26:04 | 97.289 | 96.3789 | 17965:59 | 338:59 | 95.9024 | 94.2114
11 | BELAGAVI RURAL | 149 | 149 | 445:45 | 3376:14 | 2498:31 | 1372:35 | 3871:06 | 2062.5347 | 4316:51 | 28:58 | 96.3916 | 95.9761 | 2203.2111 | 354:53 | 94.3268 | 93.9399
12 | BAILHONGAL | 226 | 226 | 720:36 | 11363:33 | 4450:14 | 2100:35 | 6550:49 | 2518.0854 | 7271:25 | 32:10 | 95.9742 | 95.5313 | 2991.5667 | 317:41 | 95.4336 | 94.575
13 | RAMDURG | 97 | 97 | 206:56 | 3486:20 | 803:20 | 794:59 | 1598:19 | 22747:23 | 1805:15 | 18:37 | 97.7115 | 97.4152 | 1093.0715 | 270:27 | 95.9954 | 95.3816
14 | GHATAPRABHA | 191 | 191 | 127:37 | 2535:54 | 1091:51 | 1233:56 | 2325:47 | 1212.441 | 2453:24 | 12:51 | 98.3088 | 98.216 | 1318.1035 | 165:38 | 97.3984 | 97.1717
15 | RAIBAG | 189 | 189 | 472:53 | 2428:26 | 3059:30 | 488:40 | 3548:10 | 1662.5896 | 4021:03 | 21:17 | 97.3926 | 97.0451 | 1763.7743 | 223:58 | 96.3948 | 96.1754
16 | ATHANI | 221 | 221 | 308:10 | 5476:44 | 2483:53 | 911:11 | 3395:04 | 1856.1167 | 3703:14 | 16:45 | 97.8663 | 97.6727 | 2084.3139 | 226:21 | 96.5579 | 96.1347
17 | CHIKKODI | 198 | 198 | 327:24 | 3406:04 | 1150:18 | 1149:05 | 2299:23 | 1197.8417 | 2626:47 | 13:16 | 98.3871 | 98.1574 | 1339.7611 | 162:24 | 97.5206 | 97.2269
18 | VIJAYAPUR | 220 | 220 | 131:25 | 4983:39 | 1744:52 | 1731:52 | 3476:44 | 2039.0965 | 3608:09 | 16:24 | 97.8051 | 97.7221 | 2246.7486 | 245:06 | 96.2014 | 95.8146
19 | INDI | 299 | 299 | 595:22 | 13838:32 | 2138:27 | 3101:42 | 5240:09 | 3674.45 | 5835:31 | 19:31 | 97.5659 | 97.2893 | 4251.0556 | 341:13 | 94.9635 | 94.1731
20 | B.BAGEWADI | 168 | 168 | 342:31 | 8309:48 | 1522:06 | 1652:52 | 3174:58 | 1876.8389 | 3517:29 | 20:56 | 97.3752 | 97.092 | 2223.0806 | 317:35 | 95.4215 | 94.5768
21 | BAGALKOT | 233 | 233 | 250:34 | 6221:42 | 2100:26 | 2466:32 | 4566:58 | 2483.2139 | 4817:32 | 20:41 | 97.2777 | 97.1283 | 2742.4514 | 282:29 | 95.6321 | 95.1762
22 | JAMAKHANDI | 223 | 223 | 255:40 | 5747:54 | 1757:52 | 820:19 | 2578:11 | 1783.4694 | 2833:51 | 12:42 | 98.3943 | 98.235 | 2022.9653 | 217:43 | 96.7223 | 96.2821
23 | MUDHOL | 222 | 222 | 109:47 | 5372:00 | 1197:18 | 1098:33 | 2295:51 | 1238.759 | 2405:38 | 10:50 | 98.5637 | 98.495 | 1462.5924 | 158:07 | 97.7131 | 97.2999
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of DECEMBER-2023 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of December-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Dec-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 54 | 54 | 24:20 | 1302:26 | 421:29 | 195:27 | 616:56 | 18075:25 | 641:16 | 11:53 | 98.4644 | 98.4039 | 19377:51 | 358:51 | 94.9283 | 94.5629
2 | DHARWAD RURAL | 105 | 104 | 97:13 | 1340:23 | 2022:13 | 716:59 | 2739:12 | 1690.334 | 2836:25 | 27:01 | 96.4936 | 96.3692 | 1746.1833 | 399:08 | 94.146 | 93.9526
3 | GADAG | 117 | 117 | 197:50 | 2543:29 | 1329:40 | 555:39 | 1885:19 | 1362.7167 | 2083:09 | 17:48 | 97.8342 | 97.6069 | 1468.6951 | 301:16 | 95.7647 | 95.4353
4 | RON | 61 | 61 | 123:20 | 1022:43 | 415:25 | 489:12 | 904:37 | 15223:32 | 1027:57 | 16:51 | 98.0067 | 97.735 | 16246:15 | 266:20 | 96.2187 | 95.9647
5 | HAVERI | 213 | 213 | 1447:26 | 12815:50 | 3531:00 | 1642:54 | 5173:54 | 3500.1361 | 6621:20 | 31:05 | 96.7351 | 95.8218 | 4034.1292 | 454:33 | 94.0245 | 93.1129
6 | RANEBENNUR | 217 | 215 | 872:39 | 8497:39 | 2943:32 | 1572:01 | 4515:33 | 2828.7639 | 5388:12 | 24:50 | 97.2031 | 96.6626 | 3182.8326 | 352:01 | 95.2597 | 94.6664
7 | SIRSI | 63 | 63 | 199:20 | 2655:38 | 962:49 | 886:13 | 1849:02 | 20845:24 | 2048:22 | 32:31 | 96.0551 | 95.6299 | 23501:02 | 373:02 | 94.9867 | 94.348
8 | DANDELI | 30 | 30 | 54:43 | 1095:21 | 282:26 | 222:45 | 505:11 | 8645:35 | 559:54 | 18:40 | 97.7366 | 97.4915 | 9740:56 | 324:42 | 95.6335 | 95.0803
9 | KARWAR | 31 | 31 | 121:11 | 2608:33 | 186:14 | 290:53 | 477:07 | 7637:27 | 598:18 | 19:18 | 97.9313 | 97.4059 | 10246:00 | 330:31 | 96.2671 | 94.9922
10 | HONNAVAR | 53 | 53 | 858:48 | 6107:11 | 710:46 | 380:21 | 1091:07 | 13808:43 | 1949:55 | 36:47 | 97.2329 | 95.055 | 19915:54 | 375:46 | 96.0524 | 94.3065
11 | BELAGAVI RURAL | 150 | 150 | 110:03 | 3486:17 | 1702:56 | 773:21 | 2476:17 | 2165.7132 | 2586:20 | 17:15 | 97.7811 | 97.6825 | 2310.975 | 369:45 | 94.7498 | 94.3976
12 | BAILHONGAL | 226 | 226 | 1342:47 | 12706:20 | 4566:41 | 1475:40 | 6042:21 | 2769.85 | 7385:08 | 32:41 | 96.4064 | 95.6079 | 3299.2806 | 350:22 | 95.5433 | 94.6914
13 | RAMDURG | 97 | 97 | 469:45 | 3956:05 | 1097:14 | 323:17 | 1420:31 | 1006.9958 | 1890:16 | 19:29 | 98.0317 | 97.3807 | 1171.8326 | 289:56 | 96.2249 | 95.607
14 | GHATAPRABHA | 193 | 193 | 139:39 | 2675:33 | 1174:03 | 707:58 | 1882:01 | 1290.8583 | 2021:40 | 10:28 | 98.6893 | 98.5921 | 1402.3396 | 174:23 | 97.5679 | 97.3578
15 | RAIBAG | 190 | 190 | 158:36 | 2587:02 | 3903:35 | 436:38 | 4340:13 | 1843.4319 | 4498:49 | 23:41 | 96.9297 | 96.8175 | 1951.225 | 246:28 | 96.4719 | 96.2656
16 | ATHANI | 220 | 220 | 500:10 | 5976:54 | 3266:08 | 721:44 | 3987:52 | 2022.2778 | 4488:02 | 20:24 | 97.5636 | 97.258 | 2271.3153 | 247:47 | 96.6574 | 96.2458
17 | CHIKKODI | 198 | 198 | 165:40 | 3571:44 | 1145:10 | 662:20 | 1807:30 | 1273.1542 | 1973:10 | 9:58 | 98.773 | 98.6606 | 1421.9764 | 172:22 | 97.6618 | 97.3885
18 | VIJAYAPUR | 220 | 220 | 504:08 | 5487:47 | 1343:54 | 1193:22 | 2537:16 | 2144.816 | 3041:24 | 13:49 | 98.4499 | 98.1419 | 2373.4736 | 258:55 | 96.4548 | 96.0769
19 | INDI | 300 | 300 | 771:18 | 14609:50 | 2203:56 | 1676:44 | 3880:40 | 3836.1444 | 4651:58 | 15:30 | 98.2614 | 97.9158 | 4444.8875 | 355:35 | 95.3501 | 94.6123
20 | B.BAGEWADI | 168 | 168 | 428:44 | 8738:32 | 1530:11 | 824:34 | 2354:45 | 1974.9535 | 2783:29 | 16:34 | 98.1161 | 97.7731 | 2339.059 | 334:09 | 95.7252 | 94.9371
21 | BAGALKOT | 234 | 234 | 458:01 | 6679:43 | 2397:48 | 1547:19 | 3945:07 | 2647.5938 | 4403:08 | 18:49 | 97.7339 | 97.4709 | 2925.9153 | 300:06 | 95.8856 | 95.4531
22 | JAMAKHANDI | 223 | 223 | 180:46 | 5928:40 | 2196:46 | 395:46 | 2592:32 | 1891.4917 | 2773:18 | 12:26 | 98.4374 | 98.3285 | 2138.5194 | 230:09 | 96.9156 | 96.5128
23 | MUDHOL | 222 | 222 | 230:52 | 5602:52 | 1559:33 | 459:11 | 2018:44 | 1322.8729 | 2249:36 | 10:08 | 98.7778 | 98.638 | 1556.3257 | 168:15 | 97.8331 | 97.4507
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of JANUARY-2024 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of January-2024 |  |  |  | Reliability for cumulative period from Apr-23 to Jan-24
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 54 | 54 | 40:37 | 1343:03 | 420:18 | 219:26 | 639:44 | 18715:09 | 680:21 | 12:36 | 98.4077 | 98.3066 | 20058:12 | 371:27 | 95.2808 | 94.9422
2 | DHARWAD RURAL | 104 | 104 | 73:20 | 1413:43 | 2121:22 | 705:26 | 2826:48 | 1808.1174 | 2900:08 | 27:53 | 96.3467 | 96.2519 | 1867.0222 | 430:51 | 94.3184 | 94.1333
3 | GADAG | 117 | 117 | 41:15 | 2584:44 | 941:52 | 507:23 | 1449:15 | 1423.1021 | 1490:30 | 12:44 | 98.3351 | 98.2877 | 1530.7993 | 314:01 | 96.0251 | 95.7243
4 | RON | 61 | 61 | 18:44 | 1041:27 | 431:48 | 362:33 | 794:21 | 16017:53 | 813:05 | 13:20 | 98.2497 | 98.2084 | 17059:20 | 279:40 | 96.4245 | 96.192
5 | HAVERI | 214 | 214 | 1572:34 | 14388:24 | 3320:46 | 1862:09 | 5182:55 | 3716.091 | 6755:29 | 31:34 | 96.7447 | 95.757 | 4315.6076 | 484:00 | 94.3252 | 93.4097
6 | RANEBENNUR | 217 | 217 | 965:55 | 9463:34 | 2068:38 | 1543:33 | 3612:11 | 2979.2715 | 4578:06 | 21:06 | 97.7626 | 97.1644 | 3373.5868 | 373:07 | 95.5133 | 94.9195
7 | SIRSI | 62 | 62 | 254:06 | 2909:44 | 612:50 | 1389:27 | 2002:17 | 22847:41 | 2256:23 | 36:24 | 95.6593 | 95.1084 | 1073.2257 | 415:27 | 94.9821 | 94.3431
8 | DANDELI | 30 | 30 | 77:45 | 1173:06 | 166:15 | 287:06 | 453:21 | 9098:56 | 531:06 | 17:42 | 97.9689 | 97.6205 | 10272:02 | 342:24 | 95.8701 | 95.3377
9 | KARWAR | 31 | 29 | 216:01 | 2824:34 | 195:55 | 332:30 | 528:25 | 8165:52 | 744:26 | 24:01 | 97.7089 | 96.7723 | 10990:26 | 354:32 | 96.4132 | 95.1725
10 | HONNAVAR | 54 | 54 | 753:13 | 6860:24 | 650:01 | 579:15 | 1229:16 | 15037:59 | 1982:29 | 36:43 | 96.9403 | 95.0655 | 21898:23 | 405:32 | 96.208 | 94.4781
11 | BELAGAVI RURAL | 155 | 155 | 356:00 | 3842:17 | 2037:16 | 882:12 | 2919:28 | 2287.3576 | 3275:28 | 21:08 | 97.4684 | 97.1597 | 2447.4528 | 378:58 | 95.1774 | 94.8399
12 | BAILHONGAL | 226 | 226 | 329:04 | 13035:24 | 2727:23 | 1010:24 | 3737:47 | 2925.591 | 4066:51 | 18:00 | 97.777 | 97.5813 | 3468.7326 | 368:22 | 95.7696 | 94.9842
13 | RAMDURG | 101 | 101 | 87:02 | 4043:07 | 1238:07 | 372:45 | 1610:52 | 1074.1153 | 1697:54 | 16:49 | 97.8563 | 97.7405 | 1242.5785 | 295:16 | 96.5246 | 95.9795
14 | GHATAPRABHA | 194 | 194 | 171:48 | 2847:21 | 1130:05 | 734:32 | 1864:37 | 1368.5507 | 2036:25 | 10:30 | 98.7081 | 98.5891 | 1487.1903 | 183:59 | 97.6946 | 97.4948
15 | RAIBAG | 193 | 193 | 88:56 | 2675:58 | 3092:11 | 357:16 | 3449:27 | 1987.159 | 3538:23 | 18:20 | 97.5977 | 97.5358 | 2098.6576 | 260:58 | 96.6352 | 96.4464
16 | ATHANI | 221 | 221 | 367:20 | 6344:14 | 1871:41 | 427:55 | 2299:36 | 2118.0944 | 2666:56 | 12:04 | 98.6014 | 98.378 | 2382.4375 | 258:44 | 96.8679 | 96.477
17 | CHIKKODI | 198 | 198 | 71:30 | 3643:14 | 1434:14 | 556:33 | 1990:47 | 1356.1035 | 2062:17 | 10:25 | 98.6486 | 98.6001 | 1507.9049 | 182:47 | 97.7618 | 97.5112
18 | VIJAYAPUR | 221 | 221 | 269:16 | 5757:03 | 963:39 | 540:23 | 1504:02 | 2207.484 | 1773:18 | 8:01 | 99.0853 | 98.9215 | 2447.3611 | 265:47 | 96.7357 | 96.381
19 | INDI | 300 | 300 | 128:05 | 14737:55 | 1651:12 | 902:25 | 2553:37 | 3942.5451 | 2681:42 | 8:56 | 98.8559 | 98.7985 | 4556.625 | 364:32 | 95.7053 | 95.0364
20 | B.BAGEWADI | 168 | 168 | 428:44 | 9167:16 | 1530:11 | 824:34 | 2354:45 | 2073.0681 | 2783:29 | 16:34 | 98.1161 | 97.7731 | 2455.0375 | 350:43 | 95.9674 | 95.2244
21 | BAGALKOT | 234 | 234 | 337:07 | 7016:50 | 1769:47 | 1416:03 | 3185:50 | 2780.3368 | 3522:57 | 15:03 | 98.1701 | 97.9764 | 3072.7049 | 315:09 | 96.1171 | 95.7088
22 | JAMAKHANDI | 223 | 223 | 243:02 | 6171:42 | 2902:37 | 456:35 | 3359:12 | 2031.4583 | 3602:14 | 16:09 | 97.9753 | 97.8288 | 2288.6125 | 246:18 | 97.023 | 96.6461
23 | MUDHOL | 223 | 223 | 137:36 | 5740:28 | 1136:07 | 576:49 | 1712:56 | 1394.2451 | 1850:32 | 8:18 | 98.9676 | 98.8846 | 1633.4313 | 175:48 | 97.9568 | 97.6063
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of FEBRUARY-2024 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of February-2024 |  |  |  | Reliability for cumulative period from Apr-23 to Feb-24
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 54 | 54 | 90:30 | 1433:33 | 578:04 | 207:22 | 785:26 | 19500:35 | 875:56 | 16:13 | 97.9102 | 97.6694 | 20934:08 | 387:40 | 95.5084 | 95.1782
2 | DHARWAD RURAL | 106 | 106 | 96:10 | 1509:53 | 2754:05 | 770:13 | 3524:18 | 1954.9632 | 3620:28 | 34:09 | 95.223 | 95.0926 | 2017.875 | 456:53 | 94.4946 | 94.3174
3 | GADAG | 121 | 121 | 260:50 | 2845:34 | 1361:36 | 502:43 | 1864:19 | 1500.7819 | 2125:09 | 17:34 | 97.7863 | 97.4765 | 1619.3472 | 321:12 | 96.2976 | 96.0051
4 | RON | 61 | 61 | 121:54 | 1163:21 | 648:27 | 457:16 | 1105:43 | 17123:36 | 1227:37 | 20:07 | 97.3956 | 97.1085 | 18286:57 | 299:47 | 96.5085 | 96.2713
5 | HAVERI | 216 | 216 | 1144:40 | 15533:04 | 3399:45 | 1635:54 | 5035:39 | 3925.9097 | 6180:19 | 28:37 | 96.6504 | 95.889 | 4573.1208 | 508:07 | 94.5745 | 93.68
6 | RANEBENNUR | 218 | 218 | 1331:49 | 10795:23 | 2162:11 | 55:56 | 2218:07 | 3071.6931 | 3549:56 | 16:17 | 98.5381 | 97.6603 | 3521.5007 | 387:41 | 95.7939 | 95.178
7 | SIRSI | 64 | 64 | 319:32 | 3229:16 | 692:01 | 1077:37 | 1769:38 | 1025.7215 | 2089:10 | 32:39 | 96.0272 | 95.3099 | 1160.2743 | 435:06 | 95.2159 | 94.5883
8 | DANDELI | 30 | 30 | 21:01 | 1194:07 | 256:17 | 287:22 | 543:39 | 9642:35 | 564:40 | 18:49 | 97.3963 | 97.2957 | 10836:42 | 361:13 | 96.0022 | 95.5072
9 | KARWAR | 31 | 31 | 207:23 | 3031:57 | 203:16 | 162:40 | 365:56 | 8531:48 | 573:19 | 18:30 | 98.304 | 97.3428 | 11563:45 | 373:01 | 96.5769 | 95.3604
10 | HONNAVAR | 54 | 54 | 213:28 | 7073:52 | 531:15 | 313:27 | 844:42 | 15882:41 | 1058:10 | 19:36 | 97.7525 | 97.1845 | 22956:33 | 425:07 | 96.3417 | 94.7124
11 | BELAGAVI RURAL | 157 | 157 | 284:21 | 4126:38 | 2463:45 | 947:47 | 3411:32 | 2429.5049 | 3695:53 | 23:32 | 96.8779 | 96.6177 | 2601.4479 | 397:40 | 95.3807 | 95.0538
12 | BAILHONGAL | 226 | 226 | 854:54 | 13890:18 | 3447:06 | 1131:04 | 4578:10 | 3116.3479 | 5433:04 | 24:02 | 97.0895 | 96.546 | 3695.1104 | 392:24 | 95.8838 | 95.1194
13 | RAMDURG | 102 | 102 | 281:52 | 4324:59 | 1163:56 | 271:09 | 1435:05 | 1133.9104 | 1716:57 | 16:50 | 97.9785 | 97.5815 | 1314.1181 | 309:12 | 96.6816 | 96.1542
14 | GHATAPRABHA | 196 | 196 | 81:58 | 2929:19 | 1233:02 | 427:29 | 1660:31 | 1437.7389 | 1742:29 | 8:53 | 98.7828 | 98.7227 | 1559.7937 | 191:00 | 97.8103 | 97.6244
15 | RAIBAG | 196 | 196 | 301:45 | 2977:43 | 3710:48 | 311:06 | 4021:54 | 2154.7382 | 4323:39 | 22:04 | 97.0517 | 96.8305 | 2278.8097 | 279:02 | 96.7183 | 96.5294
16 | ATHANI | 225 | 225 | 753:42 | 7097:56 | 2363:50 | 535:21 | 2899:11 | 2238.8938 | 3652:53 | 16:14 | 98.1487 | 97.6674 | 2534.641 | 270:22 | 97.0297 | 96.6373
17 | CHIKKODI | 198 | 198 | 362:39 | 4005:53 | 1625:30 | 399:03 | 2024:33 | 1440.4597 | 2387:12 | 12:03 | 98.5309 | 98.2677 | 1607.3715 | 194:50 | 97.8283 | 97.5767
18 | VIJAYAPUR | 220 | 220 | 402:44 | 6159:47 | 1230:39 | 556:50 | 1787:29 | 2281.9625 | 2190:13 | 9:57 | 98.8326 | 98.5696 | 2538.6201 | 276:56 | 96.9037 | 96.5555
19 | INDI | 301 | 301 | 1274:21 | 16012:16 | 1827:04 | 857:27 | 2684:31 | 4054.4 | 3958:52 | 13:09 | 98.7186 | 98.1103 | 4721.5778 | 376:28 | 95.9792 | 95.3175
20 | B.BAGEWADI | 170 | 170 | 171:02 | 9338:18 | 1425:12 | 545:32 | 1970:44 | 2155.1819 | 2141:46 | 12:36 | 98.3344 | 98.1899 | 2544.2778 | 359:12 | 96.2157 | 95.5324
21 | BAGALKOT | 234 | 234 | 556:25 | 7573:15 | 2121:08 | 1525:26 | 3646:34 | 2932.2771 | 4202:59 | 17:58 | 97.761 | 97.4193 | 3247.8292 | 333:07 | 96.2594 | 95.8568
22 | JAMAKHANDI | 223 | 223 | 239:29 | 6411:11 | 1508:25 | 349:40 | 1858:05 | 2108.8785 | 2097:34 | 9:24 | 98.8028 | 98.6485 | 2376.0111 | 255:43 | 97.1771 | 96.8195
23 | MUDHOL | 224 | 224 | 125:31 | 5865:59 | 1569:07 | 586:18 | 2155:25 | 1484.0542 | 2280:56 | 10:11 | 98.6175 | 98.537 | 1728.4701 | 185:12 | 98.0223 | 97.6966
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of MARCH-2024 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of March-2024 |  |  |  | Reliability for cumulative period from Apr-23 to Mar-24
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 57 | 57 | 21:42 | 1455:15 | 483:04 | 320:45 | 803:49 | 20304:24 | 825:31 | 14:29 | 98.1046 | 98.0534 | 21759:39 | 381:45 | 95.9447 | 95.6541
2 | DHARWAD RURAL | 107 | 106 | 60:30 | 1570:23 | 1844:14 | 732:20 | 2576:34 | 2062.3201 | 2637:04 | 24:39 | 96.7634 | 96.6874 | 2127.7528 | 477:15 | 94.7339 | 94.5668
3 | GADAG | 120 | 120 | 32:30 | 2878:04 | 1337:12 | 583:15 | 1920:27 | 1580.8007 | 1952:57 | 16:16 | 97.849 | 97.8126 | 1700.7201 | 340:09 | 96.4007 | 96.1277
4 | RON | 61 | 61 | 136:31 | 1299:52 | 595:22 | 390:00 | 985:22 | 18108:58 | 1121:53 | 18:23 | 97.8288 | 97.528 | 19408:50 | 318:11 | 96.6204 | 96.3778
5 | HAVERI | 216 | 216 | 775:45 | 16308:49 | 3065:12 | 1606:24 | 4671:36 | 4120.5597 | 5447:21 | 25:13 | 97.093 | 96.6103 | 4800.0938 | 533:21 | 94.7878 | 93.9282
6 | RANEBENNUR | 218 | 218 | 717:56 | 11513:19 | 2145:47 | 1312:55 | 3458:42 | 3215.8056 | 4176:38 | 19:10 | 97.8675 | 97.4249 | 3695.5271 | 406:51 | 95.9696 | 95.3683
7 | SIRSI | 65 | 64 | 346:39 | 3575:55 | 701:20 | 1164:10 | 1865:30 | 1103.4507 | 2212:09 | 34:02 | 96.1425 | 95.4257 | 1252.4472 | 462:27 | 95.3617 | 94.7354
8 | DANDELI | 30 | 30 | 46:29 | 1240:36 | 283:06 | 238:47 | 521:53 | 10164:28 | 568:22 | 18:57 | 97.6618 | 97.4536 | 11405:04 | 380:10 | 96.1428 | 95.672
9 | KARWAR | 31 | 31 | 146:32 | 3178:29 | 286:34 | 134:13 | 420:47 | 8952:35 | 567:19 | 18:18 | 98.1756 | 97.5403 | 12131:04 | 391:19 | 96.7123 | 95.545
10 | HONNAVAR | 54 | 54 | 306:11 | 7380:03 | 475:41 | 356:35 | 832:16 | 16714:57 | 1138:27 | 21:05 | 97.9284 | 97.1663 | 1003.9583 | 446:12 | 96.4761 | 94.9203
11 | BELAGAVI RURAL | 157 | 151 | 329:20 | 4455:58 | 2694:58 | 1166:18 | 3861:16 | 2590.391 | 4190:36 | 26:42 | 96.6943 | 96.4124 | 2776.0562 | 424:22 | 95.492 | 95.1689
12 | BAILHONGAL | 229 | 229 | 1263:54 | 15154:12 | 3185:13 | 1213:34 | 4398:47 | 3299.6306 | 5662:41 | 24:44 | 97.4182 | 96.6764 | 3931.0556 | 411:59 | 96.0632 | 95.3098
13 | RAMDURG | 102 | 102 | 876:30 | 5201:29 | 1423:55 | 348:25 | 1772:20 | 1207.7576 | 2648:50 | 25:58 | 97.6645 | 96.5095 | 1424.4861 | 335:10 | 96.7648 | 96.1843
14 | GHATAPRABHA | 199 | 199 | 146:58 | 3076:17 | 1643:29 | 546:45 | 2190:14 | 1528.9986 | 2337:12 | 11:45 | 98.5207 | 98.4214 | 1657.1771 | 199:52 | 97.9007 | 97.7247
15 | RAIBAG | 199 | 199 | 315:10 | 3292:53 | 3507:22 | 401:23 | 3908:45 | 2317.6028 | 4223:55 | 21:14 | 97.36 | 97.1471 | 2454.8063 | 296:03 | 96.818 | 96.6296
16 | ATHANI | 225 | 225 | 854:30 | 7952:26 | 3737:44 | 538:58 | 4276:42 | 2417.0896 | 5131:12 | 22:48 | 97.4452 | 96.9348 | 2748.441 | 293:10 | 97.0649 | 96.6625
17 | CHIKKODI | 201 | 201 | 298:00 | 4303:53 | 1521:54 | 540:54 | 2062:48 | 1526.4097 | 2360:48 | 11:45 | 98.6206 | 98.4213 | 1705.7382 | 203:40 | 97.9251 | 97.6813
18 | VIJAYAPUR | 224 | 224 | 427:26 | 6587:13 | 1607:37 | 738:18 | 2345:55 | 2379.709 | 2773:21 | 12:23 | 98.5924 | 98.3359 | 2654.1764 | 284:23 | 97.0973 | 96.7626
19 | INDI | 301 | 301 | 562:50 | 16575:06 | 2103:56 | 1269:05 | 3373:01 | 4194.9424 | 3935:51 | 13:05 | 98.4938 | 98.2425 | 4885.5715 | 389:33 | 96.1922 | 95.5653
20 | B.BAGEWADI | 172 | 172 | 1000:53 | 10339:11 | 1693:11 | 580:45 | 2273:56 | 2249.9292 | 3274:49 | 19:02 | 98.223 | 97.4409 | 2680.7285 | 374:03 | 96.426 | 95.7416
21 | BAGALKOT | 234 | 234 | 1505:51 | 9079:06 | 2161:18 | 1608:20 | 3769:38 | 3089.3451 | 5275:29 | 22:33 | 97.8347 | 96.9698 | 3467.641 | 355:39 | 96.3928 | 95.9511
22 | JAMAKHANDI | 227 | 227 | 1257:26 | 7668:37 | 2507:02 | 524:00 | 3031:02 | 2235.1715 | 4288:28 | 18:54 | 98.2053 | 97.4608 | 2554.6972 | 270:06 | 97.3097 | 96.9251
23 | MUDHOL | 231 | 231 | 1305:08 | 7171:07 | 2305:36 | 667:43 | 2973:19 | 1607.9424 | 4278:27 | 18:31 | 98.27 | 97.5106 | 1906.7389 | 198:06 | 98.0981 | 97.7447
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]