## DHQ
Annex-1 | [13 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of April-2023
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Apr-23
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 41 | 41 | 10:05 | 10:05 | 589:57 | 188:44 | 778:41 | 778:41 | 788:46 | 19:14 | 97.3622 | 97.328 | 788:46 | 19:14 | 97.3622 | 97.328
2 | GADAG | 12 | 12 | 75:00 | 75:00 | 130:37 | 33:01 | 163:38 | 163:38 | 238:38 | 19:53 | 98.1061 | 97.238 | 238:38 | 19:53 | 98.1061 | 97.238
3 | HAVERI | 8 | 8 | 0:00 | 0:00 | 47:36 | 22:11 | 69:47 | 69:47 | 69:47 | 8:43 | 98.7885 | 98.7885 | 69:47 | 8:43 | 98.7885 | 98.7885
4 | KARWAR | 10 | 10 | 24:12 | 24:12 | 25:32 | 50:41 | 76:13 | 76:13 | 100:25 | 10:03 | 98.9414 | 98.6053 | 100:25 | 10:03 | 98.9414 | 98.6053
5 | BELAGAVI | 77 | 75 | 112:16 | 112:16 | 129:22 | 142:27 | 271:49 | 271:49 | 384:05 | 4:59 | 99.5097 | 99.3072 | 384:05 | 4:59 | 99.5097 | 99.3072
6 | VIJAYAPUR | 41 | 40 | 74:41 | 74:41 | 231:29 | 218:06 | 449:35 | 449:35 | 524:16 | 12:47 | 98.477 | 98.224 | 524:16 | 12:47 | 98.477 | 98.224
7 | BAGALKOT | 24 | 24 | 134:17 | 134:17 | 112:56 | 302:41 | 415:37 | 415:37 | 549:54 | 22:55 | 97.5948 | 96.8177 | 549:54 | 22:55 | 97.5948 | 96.8177
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
General Manager
Technical
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of May-2023
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2023 |  |  |  | Reliability for cumulative period from Apr-23 to May-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 41 | 41 | 32:33 | 42:38 | 645:02 | 296:09 | 941:11 | 1719:52 | 973:44 | 23:45 | 96.9146 | 96.8079 | 1762:30 | 42:59 | 97.1347 | 97.0637
2 | GADAG | 12 | 12 | 19:30 | 94:30 | 60:52 | 37:38 | 98:30 | 262:08 | 118:00 | 9:50 | 98.8967 | 98.6783 | 356:38 | 29:43 | 98.5079 | 97.97
3 | HAVERI | 8 | 8 | 0:00 | 0:00 | 14:44 | 41:41 | 56:25 | 126:12 | 56:25 | 7:03 | 99.0521 | 99.0521 | 126:12 | 15:47 | 98.9225 | 98.9225
4 | KARWAR | 10 | 10 | 162:38 | 186:50 | 74:46 | 95:35 | 170:21 | 246:34 | 332:59 | 33:18 | 97.7103 | 95.5244 | 433:24 | 43:20 | 98.3158 | 97.0396
5 | BELAGAVI | 76 | 76 | 240:01 | 352:17 | 271:29 | 316:53 | 588:22 | 860:11 | 828:23 | 10:54 | 98.9595 | 98.535 | 1212:28 | 15:57 | 99.2269 | 98.9103
6 | VIJAYAPUR | 41 | 41 | 9:27 | 84:08 | 211:07 | 227:48 | 438:55 | 888:30 | 448:22 | 10:56 | 98.5611 | 98.5301 | 972:38 | 23:43 | 98.5198 | 98.3796
7 | BAGALKOT | 24 | 24 | 0:00 | 134:17 | 68:01 | 46:59 | 115:00 | 530:37 | 115:00 | 4:48 | 99.356 | 99.356 | 664:54 | 27:42 | 98.4898 | 98.1076
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
General Manager
Technical
1: Annex-1 | [5 empty] | FORM-1
Reliability Indices for District Head Quarters in HESCOM for the month of June-2023
Sl.No | Name of District Head Quarters | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2023 |  |  |  | Reliability for cumulative period from Apr-23 to June-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders(in Hrs) | outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeder(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | DHARWAD | 41 | 41 | 4:21 | 46:59 | 589:26 | 192:53 | 782:19 | 2502:11 | 786:40 | 19:11 | 97.3499 | 97.3351 | 2549:10 | 62:10 | 97.2056 | 97.1532
2 | GADAG | 12 | 12 | 16:30 | 111:00 | 49:33 | 49:04 | 98:37 | 360:45 | 115:07 | 9:36 | 98.8586 | 98.6676 | 471:45 | 39:19 | 98.6235 | 98.2
3 | HAVERI | 8 | 8 | 0:00 | 0:00 | 113:49 | 37:14 | 151:03 | 277:15 | 151:03 | 18:53 | 97.3776 | 97.3776 | 277:15 | 34:39 | 98.4132 | 98.4132
4 | KARWAR | 10 | 10 | 10:30 | 197:20 | 70:49 | 135:26 | 206:15 | 452:49 | 216:45 | 21:40 | 97.1354 | 96.9896 | 650:09 | 65:01 | 97.9267 | 97.0231
5 | BELAGAVI | 76 | 76 | 99:17 | 451:34 | 261:12 | 143:25 | 404:37 | 1264:48 | 503:54 | 6:38 | 99.2606 | 99.0791 | 1716:22 | 22:35 | 99.238 | 98.9659
6 | VIJAYAPUR | 41 | 41 | 311:56 | 396:04 | 223:12 | 370:15 | 593:27 | 1481:57 | 905:23 | 22:05 | 97.9897 | 96.933 | 1878:01 | 45:48 | 98.345 | 97.9027
7 | BAGALKOT | 24 | 24 | 185:01 | 319:18 | 162:01 | 68:35 | 230:36 | 761:13 | 415:37 | 17:19 | 98.6655 | 97.5948 | 1080:31 | 45:01 | 98.5477 | 97.9386
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo.of days in the month]
General Manager
Technical

## URBAN
Annex-II | [13 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of April-2023
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Apr-23
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 84 | 84 | 20:55 | 20:55 | 210:13 | 177:10 | 387:23 | 387:23 | 408:18 | 4:52 | 99.3595 | 99.3249 | 408:18 | 4:52 | 99.3595 | 99.3249
2 | DHARWAD (RURAL) | 13 | 13 | 0:00 | 0:00 | 109:32 | 58:03 | 167:35 | 167:35 | 167:35 | 12:53 | 98.2096 | 98.2096 | 167:35 | 12:53 | 98.2096 | 98.2096
3 | KUNDAGOL | 1 | 1 | 19:45 | 19:45 | 5:40 | 1:42 | 7:22 | 7:22 | 27:07 | 27:07 | 98.9769 | 96.2338 | 27:07 | 27:07 | 98.9769 | 96.2338
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 2:39 | 14:26 | 17:05 | 17:05 | 17:05 | 17:05 | 97.6273 | 97.6273 | 17:05 | 17:05 | 97.6273 | 97.6273
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 11:40 | 7:36 | 19:16 | 19:16 | 19:16 | 19:16 | 97.3241 | 97.3241 | 19:16 | 19:16 | 97.3241 | 97.3241
6 | KALGHATAGI | 2 | 2 | 0:00 | 0:00 | 10:50 | 14:25 | 25:15 | 25:15 | 25:15 | 12:38 | 98.2465 | 98.2465 | 25:15 | 12:38 | 98.2465 | 98.2465
7 | ALNAVAR | 2 | 2 | 0:00 | 0:00 | 5:40 | 4:15 | 9:55 | 9:55 | 9:55 | 4:58 | 99.3113 | 99.3113 | 9:55 | 4:58 | 99.3113 | 99.3113
8 | NARAGUND | 2 | 2 | 13:00 | 13:00 | 18:10 | 16:25 | 34:35 | 34:35 | 47:35 | 23:48 | 97.5984 | 96.6956 | 47:35 | 23:48 | 97.5984 | 96.6956
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 5:50 | 4:05 | 9:55 | 9:55 | 9:55 | 9:55 | 98.6227 | 98.6227 | 9:55 | 9:55 | 98.6227 | 98.6227
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 18:54 | 11:48 | 30:42 | 30:42 | 30:42 | 10:14 | 98.5787 | 98.5787 | 30:42 | 10:14 | 98.5787 | 98.5787
11 | NAREGAL | 1 | 1 | 4:00 | 4:00 | 3:10 | 2:35 | 5:45 | 5:45 | 9:45 | 9:45 | 99.2014 | 98.6458 | 9:45 | 9:45 | 99.2014 | 98.6458
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 6:20 | 11:30 | 17:50 | 17:50 | 17:50 | 8:55 | 98.7616 | 98.7616 | 17:50 | 8:55 | 98.7616 | 98.7616
13 | RON | 3 | 3 | 0:00 | 0:00 | 14:20 | 25:34 | 39:54 | 39:54 | 39:54 | 13:18 | 98.1528 | 98.1528 | 39:54 | 13:18 | 98.1528 | 98.1528
14 | MUNDARAGI | 1 | 1 | 1:55 | 1:55 | 6:10 | 12:55 | 19:05 | 19:05 | 21:00 | 21:00 | 97.3495 | 97.0833 | 21:00 | 21:00 | 97.3495 | 97.0833
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 36:51 | 17:33 | 54:24 | 54:24 | 54:24 | 54:24 | 92.4444 | 92.4444 | 54:24 | 54:24 | 92.4444 | 92.4444
16 | SAVANUR | 2 | 2 | 3:25 | 3:25 | 19:50 | 3:35 | 23:25 | 23:25 | 26:50 | 13:25 | 98.3738 | 98.1366 | 26:50 | 13:25 | 98.3738 | 98.1366
17 | SHIGGAON | 3 | 3 | 11:10 | 11:10 | 9:15 | 7:40 | 16:55 | 16:55 | 28:05 | 9:22 | 99.2168 | 98.6998 | 28:05 | 9:22 | 99.2168 | 98.6998
18 | BANKAPUR | 1 | 1 | 7:50 | 7:50 | 7:25 | 8:00 | 15:25 | 15:25 | 23:15 | 23:15 | 97.8588 | 96.7708 | 23:15 | 23:15 | 97.8588 | 96.7708
19 | HANGAL | 2 | 2 | 13:30 | 13:30 | 6:45 | 5:35 | 12:20 | 12:20 | 25:50 | 12:55 | 99.1435 | 98.206 | 25:50 | 12:55 | 99.1435 | 98.206
20 | RANEBENNUR | 10 | 10 | 7:54 | 7:54 | 74:40 | 19:18 | 93:58 | 93:58 | 101:52 | 10:11 | 98.6949 | 98.5852 | 101:52 | 10:11 | 98.6949 | 98.5852
21 | TUMINAKATTI | 1 | 1 | 2:45 | 2:45 | 8:30 | 3:15 | 11:45 | 11:45 | 14:30 | 14:30 | 98.3681 | 97.9861 | 14:30 | 14:30 | 98.3681 | 97.9861
22 | RATTIHALLI | 1 | 1 | 1:50 | 1:50 | 11:40 | 6:30 | 18:10 | 18:10 | 20:00 | 20:00 | 97.4769 | 97.2222 | 20:00 | 20:00 | 97.4769 | 97.2222
23 | HIREKERUR | 1 | 1 | 2:20 | 2:20 | 4:50 | 5:40 | 10:30 | 10:30 | 12:50 | 12:50 | 98.5417 | 98.2176 | 12:50 | 12:50 | 98.5417 | 98.2176
24 | BYADAGI | 5 | 5 | 24:50 | 24:50 | 22:45 | 23:55 | 46:40 | 46:40 | 71:30 | 14:18 | 98.7037 | 98.0139 | 71:30 | 14:18 | 98.7037 | 98.0139
25 | SIRSI | 5 | 5 | 5:25 | 5:25 | 51:10 | 13:40 | 64:50 | 64:50 | 70:15 | 14:03 | 98.1991 | 98.0486 | 70:15 | 14:03 | 98.1991 | 98.0486
26 | YELLAPUR | 1 | 1 | 1:40 | 1:40 | 3:30 | 1:45 | 5:15 | 5:15 | 6:55 | 6:55 | 99.2708 | 99.0394 | 6:55 | 6:55 | 99.2708 | 99.0394
27 | MUNDAGOD | 1 | 1 | 2:20 | 2:20 | 2:55 | 3:40 | 6:35 | 6:35 | 8:55 | 8:55 | 99.0856 | 98.7616 | 8:55 | 8:55 | 99.0856 | 98.7616
28 | SIDDAPUR | 2 | 2 | 3:30 | 3:30 | 4:50 | 5:20 | 10:10 | 10:10 | 13:40 | 6:50 | 99.294 | 99.0509 | 13:40 | 6:50 | 99.294 | 99.0509
29 | DANDELI | 7 | 7 | 1:36 | 1:36 | 105:45 | 6:34 | 112:19 | 112:19 | 113:55 | 16:16 | 97.7715 | 97.7397 | 113:55 | 16:16 | 97.7715 | 97.7397
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 14:40 | 5:40 | 20:20 | 20:20 | 20:20 | 10:10 | 98.588 | 98.588 | 20:20 | 10:10 | 98.588 | 98.588
31 | ANKOLA | 2 | 2 | 6:38 | 6:38 | 9:43 | 0:22 | 10:05 | 10:05 | 16:43 | 8:22 | 99.2998 | 98.8391 | 16:43 | 8:22 | 99.2998 | 98.8391
32 | KUMTA | 3 | 3 | 7:36 | 7:36 | 7:29 | 7:13 | 14:42 | 14:42 | 22:18 | 7:26 | 99.3194 | 98.9676 | 22:18 | 7:26 | 99.3194 | 98.9676
33 | GOKARNA | 1 | 1 | 39:41 | 39:41 | 3:30 | 3:15 | 6:45 | 6:45 | 46:26 | 46:26 | 99.0625 | 93.5509 | 46:26 | 46:26 | 99.0625 | 93.5509
34 | HONNAVAR | 3 | 3 | 25:36 | 25:36 | 12:53 | 7:39 | 20:32 | 20:32 | 46:08 | 15:23 | 99.0494 | 97.8642 | 46:08 | 15:23 | 99.0494 | 97.8642
35 | BHATKAL | 3 | 3 | 3:36 | 3:36 | 9:32 | 5:29 | 15:01 | 15:01 | 18:37 | 6:12 | 99.3048 | 99.1381 | 18:37 | 6:12 | 99.3048 | 99.1381
36 | KHANAPUR | 2 | 2 | 0:50 | 0:50 | 123:20 | 14:45 | 138:05 | 138:05 | 138:55 | 69:28 | 90.4109 | 90.353 | 138:55 | 69:28 | 90.4109 | 90.353
37 | BAILHONGAL | 3 | 3 | 8:36 | 8:36 | 19:00 | 24:10 | 43:10 | 43:10 | 51:46 | 17:15 | 98.0015 | 97.6034 | 51:46 | 17:15 | 98.0015 | 97.6034
38 | KITTUR | 1 | 1 | 3:00 | 3:00 | 2:25 | 4:45 | 7:10 | 7:10 | 10:10 | 10:10 | 99.0046 | 98.588 | 10:10 | 10:10 | 99.0046 | 98.588
39 | M K HUBLI | 1 | 1 | 1:50 | 1:50 | 7:55 | 7:45 | 15:40 | 15:40 | 17:30 | 17:30 | 97.8241 | 97.5694 | 17:30 | 17:30 | 97.8241 | 97.5694
40 | SOUNDATTI | 3 | 3 | 3:30 | 3:30 | 15:16 | 8:42 | 23:58 | 23:58 | 27:28 | 9:09 | 98.8904 | 98.7284 | 27:28 | 9:09 | 98.8904 | 98.7284
41 | MUNAVALLI | 1 | 1 | 3:05 | 3:05 | 37:55 | 8:35 | 46:30 | 46:30 | 49:35 | 49:35 | 93.5417 | 93.1134 | 49:35 | 49:35 | 93.5417 | 93.1134
42 | YARAGATTI | 1 | 1 | 4:12 | 4:12 | 32:18 | 7:26 | 39:44 | 39:44 | 43:56 | 43:56 | 94.4815 | 93.8981 | 43:56 | 43:56 | 94.4815 | 93.8981
43 | RAMDURG | 2 | 2 | 4:18 | 4:18 | 29:05 | 10:05 | 39:10 | 39:10 | 43:28 | 21:44 | 97.2801 | 96.9815 | 43:28 | 21:44 | 97.2801 | 96.9815
44 | GOKAK | 10 | 10 | 34:58 | 34:58 | 9:57 | 35:24 | 45:21 | 45:21 | 80:19 | 8:02 | 99.3701 | 98.8845 | 80:19 | 8:02 | 99.3701 | 98.8845
45 | MUDALAGI | 2 | 2 | 0:10 | 0:10 | 17:55 | 4:10 | 22:05 | 22:05 | 22:15 | 11:08 | 98.4664 | 98.4549 | 22:15 | 11:08 | 98.4664 | 98.4549
46 | KONNUR | 1 | 1 | 1:05 | 1:05 | 23:16 | 1:40 | 24:56 | 24:56 | 26:01 | 26:01 | 96.537 | 96.3866 | 26:01 | 26:01 | 96.537 | 96.3866
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 26:00 | 10:00 | 36:00 | 36:00 | 36:00 | 36:00 | 95 | 95 | 36:00 | 36:00 | 95 | 95
48 | KUDACHI | 1 | 1 | 1:20 | 1:20 | 25:10 | 3:40 | 28:50 | 28:50 | 30:10 | 30:10 | 95.9954 | 95.8102 | 30:10 | 30:10 | 95.9954 | 95.8102
49 | ATHANI | 7 | 7 | 37:00 | 37:00 | 208:58 | 6:02 | 215:00 | 215:00 | 252:00 | 36:00 | 95.7341 | 95 | 252:00 | 36:00 | 95.7341 | 95
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 67:18 | 37:20 | 104:38 | 104:38 | 104:38 | 26:10 | 96.3669 | 96.3669 | 104:38 | 26:10 | 96.3669 | 96.3669
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 56:55 | 13:10 | 70:05 | 70:05 | 70:05 | 14:01 | 98.0532 | 98.0532 | 70:05 | 14:01 | 98.0532 | 98.0532
52 | SADALAGA | 1 | 1 | 0:00 | 0:00 | 13:10 | 6:25 | 19:35 | 19:35 | 19:35 | 19:35 | 97.2801 | 97.2801 | 19:35 | 19:35 | 97.2801 | 97.2801
53 | MUDDEBIHAL | 2 | 2 | 24:05 | 24:05 | 34:50 | 16:50 | 51:40 | 51:40 | 75:45 | 37:52 | 96.412 | 94.7396 | 75:45 | 37:52 | 96.412 | 94.7396
54 | TALIKOTI | 1 | 1 | 3:45 | 3:45 | 18:15 | 45:00 | 63:15 | 63:15 | 67:00 | 67:00 | 91.2153 | 90.6944 | 67:00 | 67:00 | 91.2153 | 90.6944
55 | B.BAGEWADI | 1 | 1 | 0:10 | 0:10 | 3:01 | 6:45 | 9:46 | 9:46 | 9:56 | 9:56 | 98.6435 | 98.6204 | 9:56 | 9:56 | 98.6435 | 98.6204
56 | INDI | 3 | 3 | 0:28 | 0:28 | 57:05 | 8:36 | 65:41 | 65:41 | 66:09 | 22:03 | 96.9591 | 96.9375 | 66:09 | 22:03 | 96.9591 | 96.9375
57 | SINDAGI | 2 | 2 | 4:50 | 4:50 | 42:55 | 23:35 | 66:30 | 66:30 | 71:20 | 35:40 | 95.3819 | 95.0463 | 71:20 | 35:40 | 95.3819 | 95.0463
58 | GULEDGUDDA | 2 | 2 | 1:55 | 1:55 | 57:10 | 15:45 | 72:55 | 72:55 | 74:50 | 37:25 | 94.9363 | 94.8032 | 74:50 | 37:25 | 94.9363 | 94.8032
59 | ILKAL | 7 | 7 | 18:17 | 18:17 | 85:53 | 182:28 | 268:21 | 268:21 | 286:38 | 40:57 | 94.6756 | 94.3128 | 286:38 | 40:57 | 94.6756 | 94.3128
60 | KERUR | 1 | 1 | 3:52 | 3:52 | 10:38 | 13:55 | 24:33 | 24:33 | 28:25 | 28:25 | 96.5903 | 96.0532 | 28:25 | 28:25 | 96.5903 | 96.0532
61 | HUNGUND | 4 | 4 | 23:56 | 23:56 | 31:56 | 50:12 | 82:08 | 82:08 | 106:04 | 26:31 | 97.1481 | 96.3171 | 106:04 | 26:31 | 97.1481 | 96.3171
62 | BADAMI | 2 | 2 | 4:22 | 4:22 | 13:00 | 42:07 | 55:07 | 55:07 | 59:29 | 29:45 | 96.1725 | 95.8692 | 59:29 | 29:45 | 96.1725 | 95.8692
63 | JAMKHANDI | 6 | 6 | 5:25 | 5:25 | 54:00 | 13:30 | 67:30 | 67:30 | 72:55 | 12:09 | 98.4375 | 98.3121 | 72:55 | 12:09 | 98.4375 | 98.3121
64 | MAHALINGAPUR | 2 | 2 | 1:10 | 1:10 | 33:50 | 9:13 | 43:03 | 43:03 | 44:13 | 22:07 | 97.0104 | 96.9294 | 44:13 | 22:07 | 97.0104 | 96.9294
65 | RABAKAVI | 2 | 2 | 4:20 | 4:20 | 18:40 | 3:50 | 22:30 | 22:30 | 26:50 | 13:25 | 98.4375 | 98.1366 | 26:50 | 13:25 | 98.4375 | 98.1366
66 | BANAHATTI | 2 | 2 | 1:40 | 1:40 | 13:20 | 0:45 | 14:05 | 14:05 | 15:45 | 7:52 | 99.022 | 98.9062 | 15:45 | 7:52 | 99.022 | 98.9062
67 | TERDAL | 2 | 2 | 2:00 | 2:00 | 24:10 | 4:35 | 28:45 | 28:45 | 30:45 | 15:22 | 98.0035 | 97.8646 | 30:45 | 15:22 | 98.0035 | 97.8646
68 | MUDHOL | 4 | 4 | 0:00 | 0:00 | 39:23 | 29:59 | 69:22 | 69:22 | 69:22 | 17:20 | 97.5914 | 97.5914 | 69:22 | 17:20 | 97.5914 | 97.5914
69 | BILAGI | 1 | 1 | 2:45 | 2:45 | 13:45 | 6:50 | 20:35 | 20:35 | 23:20 | 23:20 | 97.1412 | 96.7593 | 23:20 | 23:20 | 97.1412 | 96.7593
70 | LOKAPUR | 2 | 2 | 1:20 | 1:20 | 102:25 | 14:55 | 117:20 | 117:20 | 118:40 | 59:20 | 91.8519 | 91.7593 | 118:40 | 59:20 | 91.8519 | 91.7593
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
General Manager
Technical
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of May-2023
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2023 |  |  |  | Reliability for cumulative period from Apr-23 to May-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 86 | 82 | 93:48 | 114:43 | 214:53 | 436:15 | 651:08 | 1038:31 | 744:56 | 8:40 | 98.9823 | 98.8358 | 1153:14 | 13:25 | 99.1752 | 99.084
2 | DHARWAD (RURAL) | 13 | 13 | 2:52 | 2:52 | 188:59 | 108:22 | 297:21 | 464:56 | 300:13 | 23:06 | 96.9257 | 96.896 | 467:48 | 35:59 | 97.5571 | 97.542
3 | KUNDAGOL | 1 | 1 | 34:10 | 53:55 | 6:27 | 9:17 | 15:44 | 23:06 | 49:54 | 49:54 | 97.8853 | 93.293 | 77:01 | 77:01 | 98.4221 | 94.7393
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 3:34 | 12:41 | 16:15 | 33:20 | 16:15 | 16:15 | 97.8159 | 97.8159 | 33:20 | 33:20 | 97.7231 | 97.7231
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 8:40 | 10:35 | 19:15 | 38:31 | 19:15 | 19:15 | 97.4126 | 97.4126 | 38:31 | 38:31 | 97.3691 | 97.3691
6 | KALGHATAGI | 2 | 2 | 7:50 | 7:50 | 7:00 | 16:35 | 23:35 | 48:50 | 31:25 | 15:42 | 98.4151 | 97.8887 | 56:40 | 28:20 | 98.3322 | 98.0647
7 | ALNAVAR | 2 | 2 | 9:05 | 9:05 | 31:25 | 7:20 | 38:45 | 48:40 | 47:50 | 23:55 | 97.3958 | 96.7854 | 57:45 | 28:52 | 98.3379 | 98.0277
8 | NARAGUND | 2 | 2 | 2:40 | 15:40 | 15:10 | 31:20 | 46:30 | 81:05 | 49:10 | 24:35 | 96.875 | 96.6958 | 96:45 | 48:22 | 97.2308 | 96.6957
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 8:45 | 14:00 | 22:45 | 32:40 | 22:45 | 22:45 | 96.9422 | 96.9422 | 32:40 | 32:40 | 97.7687 | 97.7687
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 51:26 | 31:03 | 82:29 | 113:11 | 82:29 | 27:30 | 96.3045 | 96.3045 | 113:11 | 37:44 | 97.423 | 97.423
11 | NAREGAL | 1 | 1 | 0:20 | 4:20 | 1:30 | 2:20 | 3:50 | 9:35 | 4:10 | 4:10 | 99.4848 | 99.44 | 13:55 | 13:55 | 99.3454 | 99.0494
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 8:45 | 9:00 | 17:45 | 35:35 | 17:45 | 8:52 | 98.8071 | 98.8071 | 35:35 | 17:48 | 98.7847 | 98.7847
13 | RON | 3 | 3 | 0:00 | 0:00 | 15:55 | 11:07 | 27:02 | 66:56 | 27:02 | 9:01 | 98.7888 | 98.7888 | 66:56 | 22:19 | 98.476 | 98.476
14 | MUNDARAGI | 1 | 1 | 0:00 | 1:55 | 6:05 | 17:23 | 23:28 | 42:33 | 23:28 | 23:28 | 96.8459 | 96.8459 | 44:28 | 44:28 | 97.0936 | 96.9627
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 31:08 | 19:55 | 51:03 | 105:27 | 51:03 | 51:03 | 93.1384 | 93.1384 | 105:27 | 105:27 | 92.7971 | 92.7971
16 | SAVANUR | 2 | 2 | 2:40 | 6:05 | 53:25 | 36:00 | 89:25 | 112:50 | 92:05 | 46:02 | 93.9908 | 93.8116 | 118:55 | 59:28 | 96.1464 | 95.9386
17 | SHIGGAON | 3 | 3 | 24:30 | 35:40 | 21:35 | 27:50 | 49:25 | 66:20 | 73:55 | 24:38 | 97.786 | 96.6883 | 102:00 | 34:00 | 98.4897 | 97.6776
18 | BANKAPUR | 1 | 1 | 14:35 | 22:25 | 11:30 | 10:15 | 21:45 | 37:10 | 36:20 | 36:20 | 97.0766 | 95.1165 | 59:35 | 59:35 | 97.4613 | 95.9301
19 | HANGAL | 2 | 2 | 17:40 | 31:10 | 34:05 | 78:45 | 112:50 | 125:10 | 130:30 | 65:15 | 92.4171 | 91.2298 | 156:20 | 78:10 | 95.7252 | 94.6607
20 | RANEBENNUR | 10 | 10 | 5:40 | 13:34 | 84:44 | 83:08 | 167:52 | 261:50 | 173:32 | 17:21 | 97.7437 | 97.6676 | 275:24 | 27:32 | 98.2115 | 98.1189
21 | TUMINAKATTI | 1 | 1 | 1:15 | 4:00 | 13:20 | 4:45 | 18:05 | 29:50 | 19:20 | 19:20 | 97.5694 | 97.4014 | 33:50 | 33:50 | 97.9622 | 97.689
22 | RATTIHALLI | 1 | 1 | 1:10 | 3:00 | 27:25 | 14:20 | 41:45 | 59:55 | 42:55 | 42:55 | 94.3884 | 94.2316 | 62:55 | 62:55 | 95.9073 | 95.7024
23 | HIREKERUR | 1 | 1 | 1:20 | 3:40 | 8:15 | 15:00 | 23:15 | 33:45 | 24:35 | 24:35 | 96.875 | 96.6958 | 37:25 | 37:25 | 97.6947 | 97.4442
24 | BYADAGI | 5 | 5 | 42:29 | 67:19 | 45:50 | 70:13 | 116:03 | 162:43 | 158:32 | 31:42 | 96.8804 | 95.7384 | 230:02 | 46:00 | 97.7771 | 96.8575
25 | SIRSI | 5 | 5 | 35:00 | 40:25 | 49:15 | 35:05 | 84:20 | 149:10 | 119:20 | 23:52 | 97.733 | 96.7921 | 189:35 | 37:55 | 97.9622 | 97.4101
26 | YELLAPUR | 1 | 1 | 6:05 | 7:45 | 3:55 | 13:25 | 17:20 | 22:35 | 23:25 | 23:25 | 97.6703 | 96.8526 | 30:20 | 30:20 | 98.4574 | 97.9281
27 | MUNDAGOD | 1 | 1 | 0:00 | 2:20 | 4:40 | 4:50 | 9:30 | 16:05 | 9:30 | 9:30 | 98.7231 | 98.7231 | 18:25 | 18:25 | 98.9014 | 98.742
28 | SIDDAPUR | 2 | 2 | 1:30 | 5:00 | 8:15 | 11:01 | 19:16 | 29:26 | 20:46 | 10:23 | 98.7052 | 98.6044 | 34:26 | 17:13 | 98.9948 | 98.824
29 | DANDELI | 7 | 7 | 10:10 | 11:46 | 47:11 | 90:20 | 137:31 | 249:50 | 147:41 | 21:06 | 97.3595 | 97.1643 | 261:36 | 37:22 | 97.5621 | 97.4473
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 14:40 | 5:40 | 20:20 | 40:40 | 20:20 | 10:10 | 98.6335 | 98.6335 | 40:40 | 20:20 | 98.6111 | 98.6111
31 | ANKOLA | 2 | 2 | 30:56 | 37:34 | 15:38 | 14:28 | 30:06 | 40:11 | 61:02 | 30:31 | 97.9772 | 95.8983 | 77:45 | 38:52 | 98.6276 | 97.3446
32 | KUMTA | 3 | 3 | 1:33 | 9:09 | 22:49 | 12:00 | 34:49 | 49:31 | 36:22 | 12:07 | 98.4401 | 98.3707 | 58:40 | 19:33 | 98.8726 | 98.6642
33 | GOKARNA | 1 | 1 | 13:45 | 53:26 | 3:50 | 0:55 | 4:45 | 11:30 | 18:30 | 18:30 | 99.3616 | 97.5134 | 64:56 | 64:56 | 99.2145 | 95.5647
34 | HONNAVAR | 3 | 3 | 5:09 | 30:45 | 25:02 | 17:45 | 42:47 | 63:19 | 47:56 | 15:59 | 98.0832 | 97.8524 | 94:04 | 31:21 | 98.5584 | 97.8582
35 | BHATKAL | 3 | 3 | 7:03 | 10:39 | 31:02 | 0:00 | 31:02 | 46:03 | 38:05 | 12:42 | 98.6096 | 98.2938 | 56:42 | 18:54 | 98.9515 | 98.709
36 | KHANAPUR | 2 | 2 | 1:00 | 1:50 | 10:35 | 10:35 | 21:10 | 159:15 | 22:10 | 11:05 | 98.5775 | 98.5103 | 161:05 | 80:32 | 94.5611 | 94.4985
37 | BAILHONGAL | 3 | 3 | 0:00 | 8:36 | 18:00 | 14:00 | 32:00 | 75:10 | 32:00 | 10:40 | 98.5663 | 98.5663 | 83:46 | 27:55 | 98.2886 | 98.0927
38 | KITTUR | 1 | 1 | 0:55 | 3:55 | 3:20 | 6:00 | 9:20 | 16:30 | 10:15 | 10:15 | 98.7455 | 98.6223 | 20:25 | 20:25 | 98.873 | 98.6054
39 | M K HUBLI | 1 | 1 | 0:00 | 1:50 | 11:50 | 9:15 | 21:05 | 36:45 | 21:05 | 21:05 | 97.1662 | 97.1662 | 38:35 | 38:35 | 97.4898 | 97.3645
40 | SOUNDATTI | 3 | 3 | 19:51 | 23:21 | 31:02 | 28:39 | 59:41 | 83:39 | 79:32 | 26:31 | 97.326 | 96.4367 | 107:00 | 35:40 | 98.0954 | 97.5638
41 | MUNAVALLI | 1 | 1 | 12:20 | 15:25 | 32:40 | 4:35 | 37:15 | 83:45 | 49:35 | 49:35 | 94.9933 | 93.3356 | 99:10 | 99:10 | 94.2794 | 93.2263
42 | YARAGATTI | 1 | 1 | 4:28 | 8:40 | 28:47 | 9:37 | 38:24 | 78:08 | 42:52 | 42:52 | 94.8387 | 94.2384 | 86:48 | 86:48 | 94.663 | 94.071
43 | RAMDURG | 2 | 2 | 9:54 | 14:12 | 42:34 | 4:45 | 47:19 | 86:29 | 57:13 | 28:36 | 96.8201 | 96.1548 | 100:41 | 50:20 | 97.0463 | 96.5614
44 | GOKAK | 10 | 10 | 26:17 | 61:15 | 41:18 | 52:12 | 93:30 | 138:51 | 119:47 | 11:59 | 98.7433 | 98.39 | 200:06 | 20:01 | 99.0516 | 98.6332
45 | MUDALAGI | 2 | 2 | 1:40 | 1:50 | 18:25 | 24:40 | 43:05 | 65:10 | 44:45 | 22:22 | 97.1046 | 96.9926 | 67:00 | 33:30 | 97.7744 | 97.7117
46 | KONNUR | 1 | 1 | 0:10 | 1:15 | 21:10 | 2:55 | 24:05 | 49:01 | 24:15 | 24:15 | 96.763 | 96.7406 | 50:16 | 50:16 | 96.6519 | 96.5665
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 27:10 | 13:55 | 41:05 | 77:05 | 41:05 | 41:05 | 94.478 | 94.478 | 77:05 | 77:05 | 94.7347 | 94.7347
48 | KUDACHI | 1 | 1 | 1:15 | 2:35 | 7:35 | 24:50 | 32:25 | 61:15 | 33:40 | 33:40 | 95.6429 | 95.4749 | 63:50 | 63:50 | 95.8163 | 95.6398
49 | ATHANI | 7 | 7 | 63:15 | 100:15 | 174:55 | 133:11 | 308:06 | 523:06 | 371:21 | 53:03 | 94.0841 | 92.8696 | 623:21 | 89:03 | 94.8956 | 93.9173
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 25:50 | 20:26 | 46:16 | 150:54 | 46:16 | 11:34 | 98.4453 | 98.4453 | 150:54 | 37:44 | 97.4232 | 97.4232
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 45:45 | 53:00 | 98:45 | 168:50 | 98:45 | 19:45 | 97.3454 | 97.3454 | 168:50 | 33:46 | 97.6935 | 97.6935
52 | SADALAGA | 1 | 1 | 5:20 | 5:20 | 17:55 | 3:40 | 21:35 | 41:10 | 26:55 | 26:55 | 97.099 | 96.3822 | 46:30 | 46:30 | 97.1881 | 96.8238
53 | MUDDEBIHAL | 2 | 2 | 0:30 | 24:35 | 22:41 | 16:00 | 38:41 | 90:21 | 39:11 | 19:36 | 97.4003 | 97.3667 | 114:56 | 57:28 | 96.9143 | 96.0747
54 | TALIKOTI | 1 | 1 | 4:15 | 8:00 | 16:50 | 18:05 | 34:55 | 98:10 | 39:10 | 39:10 | 95.3069 | 94.7357 | 106:10 | 106:10 | 93.2946 | 92.7482
55 | B.BAGEWADI | 1 | 1 | 2:28 | 2:38 | 3:02 | 3:58 | 7:00 | 16:46 | 9:28 | 9:28 | 99.0591 | 98.7276 | 19:24 | 19:24 | 98.8547 | 98.6749
56 | INDI | 3 | 3 | 1:06 | 1:34 | 6:41 | 12:46 | 19:27 | 85:08 | 20:33 | 6:51 | 99.1286 | 99.0793 | 86:42 | 28:54 | 98.0616 | 98.026
57 | SINDAGI | 2 | 2 | 2:00 | 6:50 | 55:15 | 24:55 | 80:10 | 146:40 | 82:10 | 41:05 | 94.6125 | 94.478 | 153:30 | 76:45 | 94.9909 | 94.7575
58 | GULEDGUDDA | 2 | 2 | 0:00 | 1:55 | 9:30 | 15:00 | 24:30 | 97:25 | 24:30 | 12:15 | 98.3535 | 98.3535 | 99:20 | 49:40 | 96.6729 | 96.6075
59 | ILKAL | 7 | 7 | 10:27 | 28:44 | 49:15 | 126:14 | 175:29 | 443:50 | 185:56 | 26:34 | 96.6305 | 96.4299 | 472:34 | 67:31 | 95.6691 | 95.3887
60 | KERUR | 1 | 1 | 0:40 | 4:32 | 12:58 | 18:02 | 31:00 | 55:33 | 31:40 | 31:40 | 95.8333 | 95.7437 | 60:05 | 60:05 | 96.2056 | 95.8959
61 | HUNGUND | 4 | 4 | 10:12 | 34:08 | 23:17 | 31:30 | 54:47 | 136:55 | 64:59 | 16:15 | 98.1592 | 97.8164 | 171:03 | 42:46 | 97.6619 | 97.0791
62 | BADAMI | 2 | 2 | 2:16 | 6:38 | 19:04 | 18:06 | 37:10 | 92:17 | 39:26 | 19:43 | 97.5022 | 97.3499 | 98:55 | 49:28 | 96.8482 | 96.6217
63 | JAMKHANDI | 6 | 6 | 8:25 | 13:50 | 86:50 | 62:25 | 149:15 | 216:45 | 157:40 | 26:17 | 96.6566 | 96.468 | 230:35 | 38:26 | 97.5324 | 97.375
64 | MAHALINGAPUR | 2 | 2 | 1:18 | 2:28 | 29:59 | 6:04 | 36:03 | 79:06 | 37:21 | 18:40 | 97.5773 | 97.4899 | 81:34 | 40:47 | 97.2985 | 97.2143
65 | RABAKAVI | 2 | 2 | 2:20 | 6:40 | 25:35 | 4:20 | 29:55 | 52:25 | 32:15 | 16:08 | 97.9895 | 97.8327 | 59:05 | 29:33 | 98.2098 | 97.9821
66 | BANAHATTI | 2 | 2 | 2:42 | 4:22 | 32:57 | 4:15 | 37:12 | 51:17 | 39:54 | 19:57 | 97.5 | 97.3185 | 55:39 | 27:49 | 98.2485 | 98.0994
67 | TERDAL | 2 | 2 | 0:50 | 2:50 | 51:05 | 10:35 | 61:40 | 90:25 | 62:30 | 31:15 | 95.8557 | 95.7997 | 93:15 | 46:38 | 96.912 | 96.8152
68 | MUDHOL | 4 | 4 | 16:27 | 16:27 | 46:01 | 29:54 | 75:55 | 145:17 | 92:22 | 23:06 | 97.449 | 96.8963 | 161:44 | 40:26 | 97.5191 | 97.2382
69 | BILAGI | 1 | 1 | 3:45 | 6:30 | 18:00 | 4:50 | 22:50 | 43:25 | 26:35 | 26:35 | 96.931 | 96.427 | 49:55 | 49:55 | 97.0344 | 96.5904
70 | LOKAPUR | 2 | 2 | 0:00 | 1:20 | 40:20 | 33:10 | 73:30 | 190:50 | 73:30 | 36:45 | 95.0605 | 95.0605 | 192:10 | 96:05 | 93.4825 | 93.4369
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
General Manager
Technical
1: Annex-II | [5 empty] | FORM-2
Reliability Indices for Towns and Cities in HESCOM for the month of June-2023
Sl. No | Name of the Town/ City | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2023 |  |  |  | Reliability for cumulative period from Apr-23 to June-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumers in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumer in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI(U) | 84 | 84 | 134:01 | 248:44 | 629:05 | 258:52 | 887:57 | 1926:28 | 1021:58 | 12:10 | 98.5318 | 98.3102 | 2175:12 | 25:54 | 98.9499 | 98.8143
2 | DHARWAD (RURAL) | 14 | 14 | 7:44 | 10:36 | 102:29 | 73:41 | 176:10 | 641:06 | 183:54 | 13:08 | 98.2523 | 98.1756 | 651:42 | 46:33 | 97.9033 | 97.8686
3 | KUNDAGOL | 1 | 1 | 28:37 | 82:32 | 3:54 | 1:38 | 5:32 | 28:38 | 34:09 | 34:09 | 99.2315 | 95.2569 | 111:10 | 111:10 | 98.6889 | 94.91
4 | NAVALGUND | 1 | 1 | 0:00 | 0:00 | 14:57 | 8:02 | 22:59 | 56:19 | 22:59 | 22:59 | 96.8079 | 96.8079 | 56:19 | 56:19 | 97.4214 | 97.4214
5 | ANNIGERI | 1 | 1 | 0:00 | 0:00 | 6:10 | 16:42 | 22:52 | 61:23 | 22:52 | 22:52 | 96.8241 | 96.8241 | 61:23 | 61:23 | 97.1894 | 97.1894
6 | KALGHATAGI | 2 | 2 | 0:00 | 7:50 | 29:00 | 6:35 | 35:35 | 84:25 | 35:35 | 17:48 | 97.5289 | 97.5289 | 92:15 | 46:07 | 98.0674 | 97.888
7 | ALNAVAR | 2 | 2 | 0:00 | 9:05 | 2:40 | 5:05 | 7:45 | 56:25 | 7:45 | 3:52 | 99.4618 | 99.4618 | 65:30 | 32:45 | 98.7084 | 98.5005
8 | NARAGUND | 2 | 2 | 4:40 | 20:20 | 39:50 | 42:00 | 81:50 | 162:55 | 86:30 | 43:15 | 94.3171 | 93.9931 | 183:15 | 91:38 | 96.2702 | 95.8047
9 | SHIRAHATTI | 1 | 1 | 0:00 | 0:00 | 10:35 | 4:05 | 14:40 | 47:20 | 14:40 | 14:40 | 97.963 | 97.963 | 47:20 | 47:20 | 97.8327 | 97.8327
10 | LAXMESHWAR | 3 | 3 | 0:00 | 0:00 | 29:09 | 20:39 | 49:48 | 162:59 | 49:48 | 16:36 | 97.6944 | 97.6944 | 162:59 | 54:20 | 97.5125 | 97.5125
11 | NAREGAL | 1 | 1 | 1:15 | 5:35 | 11:25 | 2:10 | 13:35 | 23:10 | 14:50 | 14:50 | 98.1134 | 97.9398 | 28:45 | 28:45 | 98.9393 | 98.6836
12 | GAJENDRAGAD | 2 | 2 | 0:00 | 0:00 | 33:15 | 7:15 | 40:30 | 76:05 | 40:30 | 20:15 | 97.1875 | 97.1875 | 76:05 | 38:02 | 98.2582 | 98.2582
13 | RON | 3 | 3 | 0:00 | 0:00 | 62:35 | 10:28 | 73:03 | 139:59 | 73:03 | 24:21 | 96.6181 | 96.6181 | 139:59 | 46:40 | 97.8635 | 97.8635
14 | MUNDARAGI | 1 | 1 | 9:28 | 11:23 | 10:10 | 12:05 | 22:15 | 64:48 | 31:43 | 31:43 | 96.9097 | 95.5949 | 76:11 | 76:11 | 97.033 | 96.5118
15 | MULAGUND | 1 | 1 | 0:00 | 0:00 | 28:38 | 29:22 | 58:00 | 163:27 | 58:00 | 58:00 | 91.9444 | 91.9444 | 163:27 | 163:27 | 92.516 | 92.516
16 | SAVANUR | 2 | 2 | 1:15 | 7:20 | 25:20 | 8:55 | 34:15 | 147:05 | 35:30 | 17:45 | 97.6215 | 97.5347 | 154:25 | 77:13 | 96.6327 | 96.4648
17 | SHIGGAON | 3 | 3 | 10:30 | 46:10 | 6:05 | 14:40 | 20:45 | 87:05 | 31:15 | 10:25 | 99.0394 | 98.5532 | 133:15 | 44:25 | 98.6709 | 97.9663
18 | BANKAPUR | 1 | 1 | 21:30 | 43:55 | 12:40 | 19:20 | 32:00 | 69:10 | 53:30 | 53:30 | 95.5556 | 92.5694 | 113:05 | 113:05 | 96.833 | 94.8222
19 | HANGAL | 2 | 2 | 35:40 | 66:50 | 13:00 | 11:50 | 24:50 | 150:00 | 60:30 | 30:15 | 98.2755 | 95.7986 | 216:50 | 108:25 | 96.5659 | 95.0359
20 | RANEBENNUR | 10 | 10 | 7:19 | 20:53 | 144:38 | 48:30 | 193:08 | 454:58 | 200:27 | 20:03 | 97.3176 | 97.216 | 475:51 | 47:35 | 97.9168 | 97.8212
21 | TUMINAKATTI | 1 | 1 | 0:30 | 4:30 | 20:55 | 0:30 | 21:25 | 51:15 | 21:55 | 21:55 | 97.0255 | 96.956 | 55:45 | 55:45 | 97.6534 | 97.4473
22 | RATTIHALLI | 1 | 1 | 0:50 | 3:50 | 14:30 | 7:45 | 22:15 | 82:10 | 23:05 | 23:05 | 96.9097 | 96.794 | 86:00 | 86:00 | 96.2378 | 96.0623
23 | HIREKERUR | 1 | 1 | 0:50 | 4:30 | 20:25 | 11:25 | 31:50 | 65:35 | 32:40 | 32:40 | 95.5787 | 95.463 | 70:05 | 70:05 | 96.9971 | 96.7911
24 | BYADAGI | 5 | 5 | 19:42 | 87:01 | 85:25 | 71:50 | 157:15 | 319:58 | 176:57 | 35:23 | 95.6319 | 95.0847 | 406:59 | 81:24 | 97.0699 | 96.273
25 | SIRSI | 5 | 5 | 3:45 | 44:10 | 32:45 | 15:10 | 47:55 | 197:05 | 51:40 | 10:20 | 98.669 | 98.5648 | 241:15 | 48:15 | 98.1952 | 97.7908
26 | YELLAPUR | 1 | 1 | 3:45 | 11:30 | 2:00 | 13:30 | 15:30 | 38:05 | 19:15 | 19:15 | 97.8472 | 97.3264 | 49:35 | 49:35 | 98.2563 | 97.7297
27 | MUNDAGOD | 1 | 1 | 0:22 | 2:42 | 13:55 | 4:20 | 18:15 | 34:20 | 18:37 | 18:37 | 97.4653 | 97.4144 | 37:02 | 37:02 | 98.428 | 98.3043
28 | SIDDAPUR | 2 | 2 | 1:30 | 6:30 | 20:10 | 7:05 | 27:15 | 56:41 | 28:45 | 14:22 | 98.1076 | 98.0035 | 63:11 | 31:36 | 98.7023 | 98.5535
29 | DANDELI | 7 | 7 | 31:47 | 43:33 | 138:37 | 36:40 | 175:17 | 425:07 | 207:04 | 29:35 | 96.5222 | 95.8915 | 468:40 | 66:57 | 97.2193 | 96.9344
30 | HALIYAL | 2 | 2 | 0:00 | 0:00 | 5:30 | 10:40 | 16:10 | 56:50 | 16:10 | 8:05 | 98.8773 | 98.8773 | 56:50 | 28:25 | 98.6989 | 98.6989
31 | ANKOLA | 2 | 2 | 5:38 | 43:12 | 12:13 | 17:31 | 29:44 | 69:55 | 35:22 | 17:41 | 97.9352 | 97.544 | 113:07 | 56:34 | 98.3993 | 97.4103
32 | KUMTA | 3 | 3 | 1:12 | 10:21 | 38:27 | 25:21 | 63:48 | 113:19 | 65:00 | 21:40 | 97.0463 | 96.9907 | 123:40 | 41:13 | 98.2705 | 98.1125
33 | GOKARNA | 1 | 1 | 26:40 | 80:06 | 6:35 | 1:40 | 8:15 | 19:45 | 34:55 | 34:55 | 98.8542 | 95.1505 | 99:51 | 99:51 | 99.0957 | 95.4281
34 | HONNAVAR | 3 | 3 | 14:27 | 45:12 | 39:39 | 15:18 | 54:57 | 118:16 | 69:24 | 23:08 | 97.456 | 96.787 | 163:28 | 54:29 | 98.195 | 97.5051
35 | BHATKAL | 3 | 3 | 20:33 | 31:12 | 21:24 | 13:35 | 34:59 | 81:02 | 55:32 | 18:31 | 98.3804 | 97.429 | 112:14 | 37:25 | 98.7632 | 98.287
36 | KHANAPUR | 2 | 2 | 11:10 | 13:00 | 21:50 | 5:35 | 27:25 | 186:40 | 38:35 | 19:18 | 98.0961 | 97.3206 | 199:40 | 99:50 | 95.7265 | 95.4289
37 | BAILHONGAL | 3 | 3 | 0:00 | 8:36 | 73:10 | 13:00 | 86:10 | 161:20 | 86:10 | 28:43 | 96.0108 | 96.0108 | 169:56 | 56:39 | 97.5376 | 97.4064
38 | KITTUR | 1 | 1 | 0:45 | 4:40 | 10:50 | 3:10 | 14:00 | 30:30 | 14:45 | 14:45 | 98.0556 | 97.9514 | 35:10 | 35:10 | 98.6035 | 98.3898
39 | M K HUBLI | 1 | 1 | 0:00 | 1:50 | 15:35 | 10:15 | 25:50 | 62:35 | 25:50 | 25:50 | 96.412 | 96.412 | 64:25 | 64:25 | 97.1345 | 97.0505
40 | SOUNDATTI | 3 | 3 | 0:20 | 23:41 | 16:15 | 7:57 | 24:12 | 107:51 | 24:32 | 8:11 | 98.8796 | 98.8642 | 131:32 | 43:51 | 98.3539 | 97.9925
41 | MUNAVALLI | 1 | 1 | 4:10 | 19:35 | 48:05 | 5:05 | 53:10 | 136:55 | 57:20 | 57:20 | 92.6157 | 92.037 | 156:30 | 156:30 | 93.7309 | 92.8342
42 | YARAGATTI | 1 | 1 | 7:50 | 16:30 | 27:20 | 6:27 | 33:47 | 111:55 | 41:37 | 41:37 | 95.3079 | 94.2199 | 128:25 | 128:25 | 94.8756 | 94.1201
43 | RAMDURG | 2 | 2 | 11:25 | 25:37 | 22:26 | 6:40 | 29:06 | 115:35 | 40:31 | 20:16 | 97.9792 | 97.1863 | 141:12 | 70:36 | 97.3539 | 96.7674
44 | GOKAK | 10 | 10 | 2:44 | 63:59 | 31:49 | 36:49 | 68:38 | 207:29 | 71:22 | 7:08 | 99.0468 | 99.0088 | 271:28 | 27:09 | 99.05 | 98.757
45 | MUDALAGI | 2 | 2 | 0:10 | 2:00 | 24:00 | 5:35 | 29:35 | 94:45 | 29:45 | 14:52 | 97.9456 | 97.934 | 96:45 | 48:22 | 97.8308 | 97.785
46 | KONNUR | 1 | 1 | 0:10 | 1:25 | 26:55 | 3:05 | 30:00 | 79:01 | 30:10 | 30:10 | 95.8333 | 95.8102 | 80:26 | 80:26 | 96.382 | 96.3172
47 | RAIBAG | 1 | 1 | 0:00 | 0:00 | 35:15 | 7:20 | 42:35 | 119:40 | 42:35 | 42:35 | 94.0856 | 94.0856 | 119:40 | 119:40 | 94.5208 | 94.5208
48 | KUDACHI | 1 | 1 | 0:00 | 2:35 | 34:50 | 4:25 | 39:15 | 100:30 | 39:15 | 39:15 | 94.5486 | 94.5486 | 103:05 | 103:05 | 95.3984 | 95.2801
49 | ATHANI | 7 | 7 | 18:12 | 118:27 | 180:27 | 148:24 | 328:51 | 851:57 | 347:03 | 49:35 | 93.4752 | 93.1141 | 970:24 | 138:38 | 94.4273 | 93.6525
50 | CHIKKODI | 4 | 4 | 0:00 | 0:00 | 89:28 | 10:18 | 99:46 | 250:40 | 99:46 | 24:56 | 96.5359 | 96.5359 | 250:40 | 62:40 | 97.1306 | 97.1306
51 | NIPPANI | 5 | 5 | 0:00 | 0:00 | 78:10 | 18:25 | 96:35 | 265:25 | 96:35 | 19:19 | 97.3171 | 97.3171 | 265:25 | 53:05 | 97.5694 | 97.5694
52 | SADALAGA | 1 | 1 | 0:25 | 5:45 | 22:35 | 2:50 | 25:25 | 66:35 | 25:50 | 25:50 | 96.4699 | 96.412 | 72:20 | 72:20 | 96.9513 | 96.688
53 | MUDDEBIHAL | 2 | 2 | 16:15 | 40:50 | 50:15 | 21:25 | 71:40 | 162:01 | 87:55 | 43:58 | 95.0231 | 93.8947 | 202:51 | 101:26 | 96.2908 | 95.356
54 | TALIKOTI | 1 | 1 | 25:20 | 33:20 | 12:10 | 13:00 | 25:10 | 123:20 | 50:30 | 50:30 | 96.5046 | 92.9861 | 156:40 | 156:40 | 94.3529 | 92.8266
55 | B.BAGEWADI | 1 | 1 | 0:59 | 3:37 | 39:05 | 8:49 | 47:54 | 64:40 | 48:53 | 48:53 | 93.3472 | 93.2106 | 68:17 | 68:17 | 97.0391 | 96.8735
56 | INDI | 3 | 3 | 10:49 | 12:23 | 25:32 | 15:37 | 41:09 | 126:17 | 51:58 | 17:19 | 98.0949 | 97.5941 | 138:40 | 46:13 | 98.0726 | 97.8836
57 | SINDAGI | 2 | 2 | 0:00 | 6:50 | 42:55 | 28:25 | 71:20 | 218:00 | 71:20 | 35:40 | 95.0463 | 95.0463 | 224:50 | 112:25 | 95.0092 | 94.8527
58 | GULEDGUDDA | 2 | 2 | 17:40 | 19:35 | 11:27 | 15:30 | 26:57 | 124:22 | 44:37 | 22:19 | 98.1285 | 96.9016 | 143:57 | 71:58 | 97.1528 | 96.7044
59 | ILKAL | 7 | 7 | 2:06 | 30:50 | 101:38 | 156:39 | 258:17 | 702:07 | 260:23 | 37:12 | 94.8753 | 94.8337 | 732:57 | 104:42 | 95.4074 | 95.2057
60 | KERUR | 1 | 1 | 9:30 | 14:02 | 10:55 | 12:36 | 23:31 | 79:04 | 33:01 | 33:01 | 96.7338 | 95.4144 | 93:06 | 93:06 | 96.3797 | 95.7372
61 | HUNGUND | 4 | 4 | 4:05 | 38:13 | 53:58 | 55:04 | 109:02 | 245:57 | 113:07 | 28:17 | 96.2141 | 96.0723 | 284:10 | 71:02 | 97.1846 | 96.7472
62 | BADAMI | 2 | 2 | 4:48 | 11:26 | 23:55 | 19:45 | 43:40 | 135:57 | 48:28 | 24:14 | 96.9676 | 96.6343 | 147:23 | 73:42 | 96.8876 | 96.6258
63 | JAMKHANDI | 6 | 6 | 54:20 | 68:10 | 97:00 | 14:15 | 111:15 | 328:00 | 165:35 | 27:36 | 97.4248 | 96.1671 | 396:10 | 66:02 | 97.4969 | 96.9768
64 | MAHALINGAPUR | 2 | 2 | 1:38 | 4:06 | 105:22 | 16:17 | 121:39 | 200:45 | 123:17 | 61:38 | 91.5521 | 91.4387 | 204:51 | 102:26 | 95.4041 | 95.3102
65 | RABAKAVI | 2 | 2 | 1:30 | 8:10 | 23:40 | 4:00 | 27:40 | 80:05 | 29:10 | 14:35 | 98.0787 | 97.9745 | 88:15 | 44:08 | 98.1666 | 97.9796
66 | BANAHATTI | 2 | 2 | 4:36 | 8:58 | 36:57 | 3:25 | 40:22 | 91:39 | 44:58 | 22:29 | 97.1968 | 96.8773 | 100:37 | 50:18 | 97.9018 | 97.6965
67 | TERDAL | 2 | 2 | 3:35 | 6:25 | 83:55 | 4:05 | 88:00 | 178:25 | 91:35 | 45:47 | 93.8889 | 93.64 | 184:50 | 92:25 | 95.9154 | 95.7685
68 | MUDHOL | 4 | 4 | 19:37 | 36:04 | 61:54 | 9:50 | 71:44 | 217:01 | 91:21 | 22:50 | 97.5093 | 96.8281 | 253:05 | 63:16 | 97.5158 | 97.103
69 | BILAGI | 1 | 1 | 13:50 | 20:20 | 12:30 | 2:10 | 14:40 | 58:05 | 28:30 | 28:30 | 97.963 | 96.0417 | 78:25 | 78:25 | 97.3405 | 96.4095
70 | LOKAPUR | 2 | 2 | 0:20 | 1:40 | 72:15 | 20:25 | 92:40 | 283:30 | 93:00 | 46:30 | 93.5648 | 93.5417 | 285:10 | 142:35 | 93.5096 | 93.4715
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24hrsXNo. of days in the month]
General Manager
Technical

## RURAL (Incl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2023
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of April-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Apr-23
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 50 | 50 | 178:08 | 178:08 | 7978:12 | 1010:20 | 8988:32 | 8988:32 | 9166:40 | 183:20 | 75.0319 | 74.537 | 9166:40 | 183:20 | 75.0319 | 74.537
2 | DHARWAD RURAL | 99 | 99 | 94:01 | 94:01 | 15372:26 | 1712:43 | 17085:09 | 17085:09 | 17179:10 | 173:32 | 76.0309 | 75.899 | 17179:10 | 173:32 | 76.0309 | 75.899
3 | GADAG | 112 | 112 | 465:32 | 465:32 | 23690:22 | 1565:44 | 1052.3375 | 1052.3375 | 1071.7347 | 229:39 | 68.6804 | 68.1031 | 1071.7347 | 229:39 | 68.6804 | 68.1031
4 | RON | 61 | 61 | 185:05 | 185:05 | 15072:23 | 1316:04 | 16388:27 | 16388:27 | 16573:32 | 271:42 | 62.6857 | 62.2643 | 16573:32 | 271:42 | 62.6857 | 62.2643
5 | HAVERI | 210 | 210 | 979:45 | 979:45 | 2706.859 | 3311:05 | 2844.8208 | 2844.8208 | 2885.6437 | 329:47 | 54.8441 | 54.1961 | 2885.6437 | 329:47 | 54.8441 | 54.1961
6 | RANEBENNUR | 212 | 212 | 878:04 | 878:04 | 2803.5271 | 2441:52 | 2905.2715 | 2905.2715 | 2941.8576 | 333:02 | 54.3196 | 53.7444 | 2941.8576 | 333:02 | 54.3196 | 53.7444
7 | SIRSI | 59 | 58 | 194:23 | 194:23 | 381:11 | 1094:40 | 1475:51 | 1475:51 | 1670:14 | 28:19 | 96.5258 | 96.0682 | 1670:14 | 28:19 | 96.5258 | 96.0682
8 | DANDELI | 27 | 27 | 101:46 | 101:46 | 754:48 | 355:24 | 1110:12 | 1110:12 | 1211:58 | 44:53 | 94.2891 | 93.7656 | 1211:58 | 44:53 | 94.2891 | 93.7656
9 | KARWAR | 31 | 31 | 147:38 | 147:38 | 209:19 | 127:07 | 336:26 | 336:26 | 484:04 | 15:37 | 98.4927 | 97.8312 | 484:04 | 15:37 | 98.4927 | 97.8312
10 | HONNAVAR | 49 | 49 | 564:27 | 564:27 | 563:22 | 325:34 | 888:56 | 888:56 | 1453:23 | 29:40 | 97.4803 | 95.8804 | 1453:23 | 29:40 | 97.4803 | 95.8804
11 | BELAGAVI RURAL | 151 | 150 | 414:09 | 414:09 | 18437:48 | 3235:08 | 21672:56 | 21672:56 | 22087:05 | 146:16 | 80.0654 | 79.6844 | 22087:05 | 146:16 | 80.0654 | 79.6844
12 | BAILHONGAL | 206 | 205 | 1550:45 | 1550:45 | 2186.5257 | 3732:19 | 2342.0389 | 2342.0389 | 2406.6535 | 280:23 | 62.1029 | 61.0574 | 2406.6535 | 280:23 | 62.1029 | 61.0574
13 | RAMDURG | 95 | 95 | 285:48 | 285:48 | 1302.4285 | 1885:12 | 1380.9785 | 1380.9785 | 1392.8868 | 351:53 | 51.5446 | 51.1268 | 1392.8868 | 351:53 | 51.5446 | 51.1268
14 | GHATAPRABHA | 179 | 179 | 314:36 | 314:36 | 1808.8451 | 2224:06 | 1901.516 | 1901.516 | 1914.6243 | 256:43 | 64.59 | 64.3459 | 1914.6243 | 256:43 | 64.59 | 64.3459
15 | RAIBAG | 183 | 179 | 333:16 | 333:16 | 1883.5389 | 910:09 | 1921.4618 | 1921.4618 | 1935.3479 | 253:49 | 65.0007 | 64.7478 | 1935.3479 | 253:49 | 65.0007 | 64.7478
16 | ATHANI | 207 | 207 | 768:52 | 768:52 | 1901.0264 | 1347:41 | 1957.1799 | 1957.1799 | 1989.216 | 230:38 | 68.4834 | 67.9675 | 1989.216 | 230:38 | 68.4834 | 67.9675
17 | CHIKKODI | 199 | 199 | 416:45 | 416:45 | 2105.6576 | 2673:11 | 2217.0403 | 2217.0403 | 2234.4049 | 269:29 | 62.8636 | 62.5728 | 2234.4049 | 269:29 | 62.8636 | 62.5728
18 | VIJAYAPUR | 217 | 217 | 343:35 | 343:35 | 2496.2924 | 3060:26 | 2623.8104 | 2623.8104 | 2638.1264 | 291:46 | 59.6957 | 59.4758 | 2638.1264 | 291:46 | 59.6957 | 59.4758
19 | INDI | 286 | 286 | 1877:44 | 1877:44 | 2983.5035 | 7255:19 | 3285.8083 | 3285.8083 | 3364.0472 | 282:18 | 61.7039 | 60.792 | 3364.0472 | 282:18 | 61.7039 | 60.792
20 | B.BAGEWADI | 156 | 155 | 612:11 | 612:11 | 1603.7451 | 3884:16 | 1765.5896 | 1765.5896 | 1791.0972 | 275:33 | 62.2737 | 61.7287 | 1791.0972 | 275:33 | 62.2737 | 61.7287
21 | BAGALKOT | 230 | 230 | 1111:51 | 1111:51 | 2533.2056 | 5839:34 | 2776.5208 | 2776.5208 | 2822.8479 | 294:33 | 59.7606 | 59.0892 | 2822.8479 | 294:33 | 59.7606 | 59.0892
22 | JAMAKHANDI | 213 | 213 | 529:00 | 529:00 | 2390.4569 | 1072:32 | 2435.1458 | 2435.1458 | 2457.1875 | 276:52 | 61.8913 | 61.5464 | 2457.1875 | 276:52 | 61.8913 | 61.5464
23 | MUDHOL | 213 | 213 | 756:42 | 756:42 | 2915.134 | 1947:07 | 2996.2639 | 2996.2639 | 3027.7931 | 341:10 | 53.1101 | 52.6167 | 3027.7931 | 341:10 | 53.1101 | 52.6167
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
General Manager
Technical
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2023
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of May-2023 |  |  |  | Reliability for cumulative period from Apr-23 to May-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 50 | 50 | 295:01 | 473:09 | 8208:56 | 1983:01 | 10191:57 | 19180:29 | 10486:58 | 209:44 | 72.6023 | 71.8092 | 19653:38 | 393:04 | 73.7972 | 73.1508
2 | DHARWAD RURAL | 99 | 99 | 411:50 | 505:51 | 14294:44 | 4585:04 | 18879:48 | 1498.5396 | 19291:38 | 194:52 | 74.3676 | 73.8085 | 1519.6167 | 368:24 | 75.1856 | 74.8366
3 | GADAG | 115 | 114 | 231:04 | 696:36 | 1023.4618 | 2649:44 | 1133.8674 | 2186.2049 | 1143.4951 | 238:39 | 68.1945 | 67.9244 | 2215.2299 | 462:19 | 68.8353 | 68.4215
4 | RON | 59 | 59 | 56:50 | 241:55 | 15195:30 | 1388:45 | 16584:15 | 1373.8625 | 16641:05 | 282:03 | 62.2192 | 62.0898 | 1383.9424 | 562:58 | 61.8265 | 61.5465
5 | HAVERI | 210 | 210 | 2475:28 | 3455:13 | 2656.3688 | 11078:33 | 3117.975 | 5962.7958 | 3221.1194 | 368:08 | 52.1048 | 50.5204 | 6106.7632 | 697:55 | 53.452 | 52.3282
6 | RANEBENNUR | 212 | 212 | 1390:19 | 2268:23 | 2773.7792 | 9227:39 | 3158.2646 | 6063.5361 | 3216.1944 | 364:06 | 51.9436 | 51.0622 | 6158.0521 | 697:08 | 53.1122 | 52.3813
7 | SIRSI | 60 | 60 | 328:01 | 522:24 | 693:49 | 2374:31 | 3068:20 | 4544:11 | 3396:21 | 56:36 | 93.1265 | 92.3917 | 5066:35 | 84:27 | 94.8267 | 94.232
8 | DANDELI | 28 | 28 | 110:40 | 212:26 | 769:53 | 634:52 | 1404:45 | 2514:57 | 1515:25 | 54:07 | 93.2568 | 92.7255 | 2727:23 | 97:24 | 93.8648 | 93.3465
9 | KARWAR | 31 | 31 | 564:56 | 712:34 | 352:56 | 487:40 | 840:36 | 1177:02 | 1405:32 | 45:20 | 96.3554 | 93.9059 | 1889:36 | 60:57 | 97.4065 | 95.8364
10 | HONNAVAR | 50 | 50 | 550:27 | 1114:54 | 696:56 | 683:52 | 1380:48 | 2269:44 | 1931:15 | 38:38 | 96.2882 | 94.8085 | 3384:38 | 67:42 | 96.8993 | 95.3762
11 | BELAGAVI RURAL | 152 | 149 | 586:22 | 1000:31 | 17757:55 | 4432:57 | 22190:52 | 1827.6583 | 22777:14 | 149:51 | 80.3773 | 79.8588 | 1869.3465 | 295:10 | 80.2884 | 79.8388
12 | BAILHONGAL | 215 | 215 | 2090:55 | 3641:40 | 2371.0125 | 4758:40 | 2569.2903 | 4911.3292 | 2656.4118 | 296:32 | 61.451 | 60.1439 | 5063.0653 | 565:11 | 62.5518 | 61.3949
13 | RAMDURG | 93 | 93 | 534:28 | 820:16 | 1283.6646 | 2417:17 | 1384.3847 | 2765.3632 | 1406.6542 | 363:00 | 51.9811 | 51.2087 | 2799.541 | 722:28 | 51.254 | 50.6515
14 | GHATAPRABHA | 182 | 182 | 592:50 | 907:26 | 1885.6347 | 4161:07 | 2059.0146 | 3960.5306 | 2083.716 | 274:47 | 63.5056 | 63.0678 | 3998.3403 | 527:15 | 64.326 | 63.9854
15 | RAIBAG | 182 | 182 | 251:20 | 584:36 | 1945.5312 | 2268:11 | 2040.0389 | 3961.5007 | 2050.5111 | 270:24 | 63.8419 | 63.6563 | 3985.859 | 525:36 | 64.3172 | 64.0978
16 | ATHANI | 209 | 209 | 1026:05 | 1794:57 | 1968.8333 | 3230:14 | 2103.4264 | 4060.6063 | 2146.1799 | 246:27 | 67.5347 | 66.8748 | 4135.3958 | 474:53 | 68.1496 | 67.563
17 | CHIKKODI | 199 | 199 | 436:00 | 852:45 | 2163.4472 | 2337:36 | 2260.8472 | 4477.8875 | 2279.0139 | 274:51 | 63.3515 | 63.057 | 4513.4187 | 544:20 | 63.1116 | 62.8189
18 | VIJAYAPUR | 214 | 214 | 512:30 | 856:05 | 2523.0132 | 6045:07 | 2774.8931 | 5398.7035 | 2796.2472 | 313:36 | 58.1716 | 57.8498 | 5434.3736 | 609:28 | 58.6433 | 58.3701
19 | INDI | 289 | 288 | 1129:31 | 3007:15 | 3060.2063 | 8258:28 | 3404.309 | 6690.1174 | 3451.3722 | 286:37 | 62.0012 | 61.4759 | 6815.4194 | 565:59 | 62.0505 | 61.3397
20 | B.BAGEWADI | 155 | 155 | 486:45 | 1098:56 | 1647.3396 | 3953:27 | 1812.0667 | 3577.6562 | 1832.3479 | 283:43 | 62.2879 | 61.8658 | 3623.4451 | 561:03 | 62.1612 | 61.6769
21 | BAGALKOT | 228 | 228 | 449:57 | 1561:48 | 2565.7625 | 5337:27 | 2788.1562 | 5564.6771 | 2806.9042 | 295:28 | 60.5524 | 60.2872 | 5629.7521 | 592:36 | 59.9894 | 59.5215
22 | JAMAKHANDI | 214 | 214 | 483:21 | 1012:21 | 2471.8674 | 3056:32 | 2599.2229 | 5034.3687 | 2619.3625 | 293:46 | 60.8197 | 60.5161 | 5076.55 | 569:20 | 61.4343 | 61.1112
23 | MUDHOL | 215 | 216 | 362:59 | 1119:41 | 3044.4104 | 2928:08 | 3166.416 | 6162.6799 | 3181.5403 | 355:09 | 52.4919 | 52.265 | 6209.3333 | 693:08 | 53.0104 | 52.6547
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
General Manager
Technical
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2023 (Including Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level(in Hrs) |  |  |  | Reliability for the Month of June-2023 |  |  |  | Reliability for cumulative period from Apr-23 to June-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 50 | 50 | 255:02 | 728:11 | 8012:23 | 1485:27 | 9497:50 | 1194.9299 | 9752:52 | 195:03 | 73.6171 | 72.9087 | 1225.2708 | 588:08 | 73.7378 | 73.071
2 | DHARWAD RURAL | 99 | 99 | 52:02 | 557:53 | 14988:19 | 3216:33 | 18204:52 | 2257.0757 | 18256:54 | 184:25 | 74.4601 | 74.3871 | 2280.3208 | 552:48 | 74.9464 | 74.6884
3 | GADAG | 115 | 114 | 549:14 | 1245:50 | 23544:08 | 2758:11 | 1095.9299 | 3282.1347 | 1118.8146 | 233:30 | 68.2339 | 67.5706 | 3334.0444 | 695:48 | 68.637 | 68.141
4 | RON | 60 | 60 | 174:28 | 416:23 | 15348:53 | 1266:02 | 16614:55 | 2066.1507 | 16789:23 | 279:49 | 61.5395 | 61.1357 | 2083.5 | 833:24 | 62.1584 | 61.8407
5 | HAVERI | 211 | 211 | 1929:17 | 5384:30 | 2585.7271 | 8939:01 | 2958.1861 | 8920.9819 | 3038.5729 | 345:37 | 53.2672 | 51.9973 | 9145.3361 | 1040:14 | 53.539 | 52.3705
6 | RANEBENNUR | 213 | 213 | 1057:56 | 3326:19 | 2740.6722 | 5160:38 | 2955.6986 | 9019.2347 | 2999.7792 | 338:00 | 53.7449 | 53.0551 | 9157.8313 | 1031:52 | 53.4683 | 52.7533
7 | SIRSI | 61 | 61 | 413:26 | 935:50 | 767:41 | 2728:02 | 3495:43 | 8039:54 | 3909:09 | 64:05 | 92.0407 | 91.0994 | 8975:44 | 147:09 | 93.9651 | 93.2627
8 | DANDELI | 28 | 25 | 116:03 | 328:29 | 294:03 | 639:14 | 933:17 | 3448:14 | 1049:20 | 37:29 | 95.3706 | 94.795 | 3776:43 | 134:53 | 94.3612 | 93.8241
9 | KARWAR | 31 | 31 | 366:32 | 1079:06 | 376:10 | 831:50 | 1208:00 | 2385:02 | 1574:32 | 50:47 | 94.5878 | 92.9456 | 3464:08 | 111:45 | 96.4773 | 94.8834
10 | HONNAVAR | 52 | 51 | 766:50 | 1881:44 | 757:18 | 1245:10 | 2002:28 | 4272:12 | 2769:18 | 53:15 | 94.6515 | 92.6034 | 6153:56 | 118:21 | 96.2382 | 94.5813
11 | BELAGAVI RURAL | 153 | 153 | 431:25 | 1431:56 | 16949:32 | 3256:10 | 20205:42 | 2669.5625 | 20637:07 | 134:53 | 81.6579 | 81.2662 | 2729.2264 | 428:07 | 80.8262 | 80.3977
12 | BAILHONGAL | 216 | 215 | 1741:08 | 5382:48 | 2327.6694 | 4613:26 | 2519.8958 | 7431.225 | 2592.4431 | 288:03 | 61.1127 | 59.9932 | 7655.5083 | 850:37 | 62.1936 | 61.0526
13 | RAMDURG | 95 | 95 | 754:02 | 1574:18 | 1337.8451 | 1574:56 | 1403.4674 | 4168.8306 | 1434.8854 | 362:30 | 50.7555 | 49.6531 | 4234.4264 | 1069:45 | 51.7776 | 51.0188
14 | GHATAPRABHA | 185 | 185 | 431:43 | 1339:09 | 1907.8167 | 2364:52 | 2006.3528 | 5966.8833 | 2024.341 | 262:37 | 63.8495 | 63.5254 | 6022.6812 | 781:19 | 64.5567 | 64.2252
15 | RAIBAG | 181 | 181 | 461:06 | 1045:42 | 1866.3375 | 1037:47 | 1909.5785 | 5871.0792 | 1928.791 | 255:45 | 64.8328 | 64.479 | 5914.65 | 784:16 | 64.3551 | 64.0905
16 | ATHANI | 209 | 209 | 731:45 | 2526:42 | 1900.0111 | 2006:25 | 1983.6118 | 6044.2181 | 2014.1014 | 231:17 | 68.3634 | 67.8772 | 6149.4972 | 706:10 | 68.2201 | 67.6666
17 | CHIKKODI | 198 | 198 | 357:05 | 1209:50 | 2067.4292 | 1475:05 | 2128.891 | 6606.7785 | 2143.7694 | 259:51 | 64.1601 | 63.9096 | 6657.1882 | 806:56 | 63.3323 | 63.0526
18 | VIJAYAPUR | 215 | 215 | 1226:49 | 2082:54 | 2526.6736 | 3944:20 | 2691.0208 | 8089.7243 | 2742.1382 | 306:06 | 58.2787 | 57.4862 | 8176.5118 | 912:44 | 58.6521 | 58.2085
19 | INDI | 292 | 291 | 1828:25 | 4835:40 | 2948.2576 | 7284:41 | 3251.7861 | 9941.9035 | 3327.9701 | 273:32 | 62.8792 | 62.0095 | 10143.3896 | 833:42 | 62.585 | 61.8268
20 | B.BAGEWADI | 155 | 155 | 1048:08 | 2147:04 | 1611.0917 | 3686:17 | 1764.6868 | 5342.3431 | 1808.359 | 280:00 | 62.0497 | 61.1106 | 5431.8042 | 841:03 | 62.1245 | 61.4902
21 | BAGALKOT | 230 | 229 | 1041:58 | 2603:46 | 2568.0882 | 3942:32 | 2732.3604 | 8297.0375 | 2775.7757 | 289:39 | 60.4006 | 59.7714 | 8405.5278 | 877:06 | 60.3582 | 59.8398
22 | JAMAKHANDI | 214 | 214 | 906:01 | 1918:22 | 2566.7076 | 1421:10 | 2625.9229 | 7660.2917 | 2663.6736 | 298:44 | 59.0978 | 58.5098 | 7740.2236 | 868:04 | 60.664 | 60.2536
23 | MUDHOL | 219 | 219 | 1359:43 | 2479:24 | 3007.7 | 1518:07 | 3070.9549 | 9233.6347 | 3127.6097 | 342:45 | 53.2579 | 52.3956 | 9336.9431 | 1023:14 | 53.6673 | 53.149
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
General Manager
Technical

## RURAL(Excl LS)
Annex-III | [13 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of April-2023 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of April-2023 |  |  |  | Reliability for cumulative period from Apr-23 to Apr-23
[6 empty] | Scheduled Outage | UnScheduled Outage | Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 50 | 50 | 178:08 | 178:08 | 816:33 | 1010:20 | 1826:53 | 1826:53 | 2005:01 | 40:06 | 94.9253 | 94.4305 | 2005:01 | 40:06 | 94.9253 | 94.4305
2 | DHARWAD RURAL | 99 | 99 | 94:01 | 94:01 | 2001:35 | 1712:43 | 3714:18 | 3714:18 | 3808:19 | 38:28 | 94.7891 | 94.6572 | 3808:19 | 38:28 | 94.7891 | 94.6572
3 | GADAG | 112 | 112 | 465:32 | 465:32 | 1440:02 | 1565:44 | 3005:46 | 3005:46 | 3471:18 | 31:00 | 96.2726 | 95.6953 | 3471:18 | 31:00 | 96.2726 | 95.6953
4 | RON | 61 | 61 | 185:05 | 185:05 | 823:28 | 1316:04 | 2139:32 | 2139:32 | 2324:37 | 38:07 | 95.1286 | 94.7072 | 2324:37 | 38:07 | 95.1286 | 94.7072
5 | HAVERI | 210 | 210 | 979:45 | 979:45 | 2215:00 | 3311:05 | 5526:05 | 5526:05 | 6505:50 | 30:59 | 96.3452 | 95.6972 | 6505:50 | 30:59 | 96.3452 | 95.6972
6 | RANEBENNUR | 212 | 212 | 878:04 | 878:04 | 2496:22 | 2441:52 | 4938:14 | 4938:14 | 5816:18 | 27:26 | 96.7648 | 96.1895 | 5816:18 | 27:26 | 96.7648 | 96.1895
7 | SIRSI | 59 | 58 | 194:23 | 194:23 | 381:11 | 1094:40 | 1475:51 | 1475:51 | 1670:14 | 28:19 | 96.5258 | 96.0682 | 1670:14 | 28:19 | 96.5258 | 96.0682
8 | DANDELI | 27 | 27 | 101:46 | 101:46 | 754:48 | 355:24 | 1110:12 | 1110:12 | 1211:58 | 44:53 | 94.2891 | 93.7656 | 1211:58 | 44:53 | 94.2891 | 93.7656
9 | KARWAR | 31 | 31 | 147:38 | 147:38 | 209:19 | 127:07 | 336:26 | 336:26 | 484:04 | 15:37 | 98.4927 | 97.8312 | 484:04 | 15:37 | 98.4927 | 97.8312
10 | HONNAVAR | 49 | 49 | 564:27 | 564:27 | 563:22 | 325:34 | 888:56 | 888:56 | 1453:23 | 29:40 | 97.4803 | 95.8804 | 1453:23 | 29:40 | 97.4803 | 95.8804
11 | BELAGAVI RURAL | 151 | 150 | 414:09 | 414:09 | 3602:21 | 3235:08 | 6837:29 | 6837:29 | 7251:38 | 48:01 | 93.7109 | 93.33 | 7251:38 | 48:01 | 93.7109 | 93.33
12 | BAILHONGAL | 206 | 205 | 1550:45 | 1550:45 | 4175:30 | 3732:19 | 7907:49 | 7907:49 | 9458:34 | 45:55 | 94.6684 | 93.6229 | 9458:34 | 45:55 | 94.6684 | 93.6229
13 | RAMDURG | 95 | 95 | 285:48 | 285:48 | 1968:54 | 1885:12 | 3854:06 | 3854:06 | 4139:54 | 43:35 | 94.3654 | 93.9475 | 4139:54 | 43:35 | 94.3654 | 93.9475
14 | GHATAPRABHA | 179 | 179 | 314:36 | 314:36 | 1780:54 | 2224:06 | 4005:00 | 4005:00 | 4319:36 | 24:08 | 96.8925 | 96.6484 | 4319:36 | 24:08 | 96.8925 | 96.6484
15 | RAIBAG | 183 | 179 | 333:16 | 333:16 | 4065:41 | 910:09 | 4975:50 | 4975:50 | 5309:06 | 29:01 | 96.2236 | 95.9706 | 5309:06 | 29:01 | 96.2236 | 95.9706
16 | ATHANI | 207 | 207 | 768:52 | 768:52 | 3546:04 | 1347:41 | 4893:45 | 4893:45 | 5662:37 | 27:21 | 96.7165 | 96.2006 | 5662:37 | 27:21 | 96.7165 | 96.2006
17 | CHIKKODI | 199 | 199 | 416:45 | 416:45 | 2282:53 | 2673:11 | 4956:04 | 4956:04 | 5372:49 | 27:00 | 96.541 | 96.2501 | 5372:49 | 27:00 | 96.541 | 96.2501
18 | VIJAYAPUR | 217 | 217 | 343:35 | 343:35 | 2136:27 | 3060:26 | 5196:53 | 5196:53 | 5540:28 | 25:32 | 96.6738 | 96.4539 | 5540:28 | 25:32 | 96.6738 | 96.4539
19 | INDI | 286 | 286 | 1877:44 | 1877:44 | 4547:46 | 7255:19 | 11803:05 | 11803:05 | 13680:49 | 47:50 | 94.2681 | 93.3562 | 13680:49 | 47:50 | 94.2681 | 93.3562
20 | B.BAGEWADI | 156 | 155 | 612:11 | 612:11 | 2279:05 | 3884:16 | 6163:21 | 6163:21 | 6775:32 | 43:26 | 94.5127 | 93.9677 | 6775:32 | 43:26 | 94.5127 | 93.9677
21 | BAGALKOT | 230 | 230 | 1111:51 | 1111:51 | 3969:57 | 5839:34 | 9809:31 | 9809:31 | 10921:22 | 47:29 | 94.0764 | 93.405 | 10921:22 | 47:29 | 94.0764 | 93.405
22 | JAMAKHANDI | 213 | 213 | 529:00 | 529:00 | 3207:22 | 1072:32 | 4279:54 | 4279:54 | 4808:54 | 22:35 | 97.2092 | 96.8643 | 4808:54 | 22:35 | 97.2092 | 96.8643
23 | MUDHOL | 213 | 213 | 756:42 | 756:42 | 2576:16 | 1947:07 | 4523:23 | 4523:23 | 5280:05 | 24:47 | 97.0505 | 96.5571 | 5280:05 | 24:47 | 97.0505 | 96.5571
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
General Manager
Technical
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of May-2023 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of May-2023 |  |  |  | Reliability for cumulative period from Apr-23 to May-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 50 | 50 | 295:01 | 473:09 | 1359:48 | 1983:01 | 3342:49 | 5169:42 | 3637:50 | 72:45 | 91.0139 | 90.2209 | 5642:51 | 112:51 | 92.9376 | 92.2912
2 | DHARWAD RURAL | 99 | 99 | 411:50 | 505:51 | 2498:29 | 4585:04 | 7083:33 | 10797:51 | 7495:23 | 75:43 | 90.3829 | 89.8238 | 11303:42 | 114:11 | 92.5499 | 92.2009
3 | GADAG | 115 | 114 | 231:04 | 696:36 | 1933:39 | 2649:44 | 4583:23 | 7589:09 | 4814:27 | 41:52 | 94.6431 | 94.373 | 8285:45 | 72:03 | 95.4923 | 95.0786
4 | RON | 59 | 59 | 56:50 | 241:55 | 812:20 | 1388:45 | 2201:05 | 4340:37 | 2257:55 | 38:16 | 94.9857 | 94.8562 | 4582:32 | 77:40 | 94.9747 | 94.6947
5 | HAVERI | 210 | 210 | 2475:28 | 3455:13 | 3695:35 | 11078:33 | 14774:08 | 20300:13 | 17249:36 | 82:08 | 90.5439 | 88.9595 | 23755:26 | 113:07 | 93.397 | 92.2731
6 | RANEBENNUR | 212 | 212 | 1390:19 | 2268:23 | 3821:53 | 9227:39 | 13049:32 | 17987:46 | 14439:51 | 68:07 | 91.7266 | 90.8451 | 20256:09 | 95:33 | 94.2044 | 93.4735
7 | SIRSI | 60 | 60 | 328:01 | 522:24 | 693:49 | 2374:31 | 3068:20 | 4544:11 | 3396:21 | 56:36 | 93.1265 | 92.3917 | 5066:35 | 84:27 | 94.8267 | 94.232
8 | DANDELI | 28 | 28 | 110:40 | 212:26 | 769:53 | 634:52 | 1404:45 | 2514:57 | 1515:25 | 54:07 | 93.2568 | 92.7255 | 2727:23 | 97:24 | 93.8648 | 93.3465
9 | KARWAR | 31 | 31 | 564:56 | 712:34 | 352:16 | 487:40 | 839:56 | 1176:22 | 1404:52 | 45:19 | 96.3582 | 93.9088 | 1888:56 | 60:56 | 97.408 | 95.8379
10 | HONNAVAR | 50 | 50 | 550:27 | 1114:54 | 696:56 | 683:52 | 1380:48 | 2269:44 | 1931:15 | 38:38 | 96.2882 | 94.8085 | 3384:38 | 67:42 | 96.8993 | 95.3762
11 | BELAGAVI RURAL | 152 | 149 | 586:22 | 1000:31 | 3512:03 | 4432:57 | 7945:00 | 14782:29 | 8531:22 | 56:08 | 92.9745 | 92.456 | 15783:00 | 103:50 | 93.357 | 92.9074
12 | BAILHONGAL | 215 | 215 | 2090:55 | 3641:40 | 4127:35 | 4758:40 | 8886:15 | 16794:04 | 10977:10 | 51:03 | 94.4447 | 93.1376 | 20435:44 | 95:03 | 94.6645 | 93.5075
13 | RAMDURG | 93 | 93 | 534:28 | 820:16 | 1544:34 | 2417:17 | 3961:51 | 7815:57 | 4496:19 | 48:21 | 94.2741 | 93.5017 | 8636:13 | 92:52 | 94.2594 | 93.6569
14 | GHATAPRABHA | 182 | 182 | 592:50 | 907:26 | 1982:34 | 4161:07 | 6143:41 | 10148:41 | 6736:31 | 37:01 | 95.4628 | 95.025 | 11056:07 | 60:45 | 96.1911 | 95.8506
15 | RAIBAG | 182 | 182 | 251:20 | 584:36 | 4492:00 | 2268:11 | 6760:11 | 11736:01 | 7011:31 | 38:31 | 95.0075 | 94.8219 | 12320:37 | 67:42 | 95.5954 | 95.376
16 | ATHANI | 209 | 209 | 1026:05 | 1794:57 | 3811:23 | 3230:14 | 7041:37 | 11935:22 | 8067:42 | 38:36 | 95.4715 | 94.8116 | 13730:19 | 65:42 | 96.0992 | 95.5126
17 | CHIKKODI | 199 | 199 | 436:00 | 852:45 | 2050:58 | 2337:36 | 4388:34 | 9344:38 | 4824:34 | 24:15 | 97.0359 | 96.7414 | 10197:23 | 51:15 | 96.7925 | 96.4998
18 | VIJAYAPUR | 214 | 214 | 512:30 | 856:05 | 2468:01 | 6045:07 | 8513:08 | 13710:01 | 9025:38 | 42:11 | 94.6531 | 94.3312 | 14566:06 | 68:04 | 95.6239 | 95.3507
19 | INDI | 289 | 288 | 1129:31 | 3007:15 | 4785:34 | 8258:28 | 13044:02 | 1035.2965 | 14173:33 | 49:03 | 93.9335 | 93.4081 | 1160.5986 | 96:23 | 94.1273 | 93.4165
20 | B.BAGEWADI | 155 | 155 | 486:45 | 1098:56 | 2439:29 | 3953:27 | 6392:56 | 12556:17 | 6879:41 | 44:23 | 94.4564 | 94.0343 | 13655:13 | 88:06 | 94.4666 | 93.9824
21 | BAGALKOT | 228 | 228 | 449:57 | 1561:48 | 2854:32 | 5337:27 | 8191:59 | 18001:30 | 8641:56 | 37:54 | 95.1707 | 94.9055 | 19563:18 | 85:48 | 94.607 | 94.1391
22 | JAMAKHANDI | 214 | 214 | 483:21 | 1012:21 | 3263:46 | 3056:32 | 6320:18 | 10600:12 | 6803:39 | 31:48 | 96.0304 | 95.7268 | 11612:33 | 54:16 | 96.6166 | 96.2934
23 | MUDHOL | 215 | 216 | 362:59 | 1119:41 | 2388:08 | 2928:08 | 5316:16 | 9839:39 | 5679:15 | 26:25 | 96.6765 | 96.4496 | 10959:20 | 50:58 | 96.8739 | 96.5182
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
General Manager
Technical
1: Annex-III | [5 empty] | FORM-3
Reliability Indices for Rural Areas in HESCOM for the month of June-2023 (Excluding Load Shedding Period)
Sl.No | Name of Rural Area | Total No of 11 KV Feeders | Total No of 11 KV Feeders affected | Outage due to incoming supply failure (In Hrs) | Cumulative Outage due to incoming supply failure (in Hrs) for FY 23-24 | Outage of 11 KV level (in Hrs) |  |  |  | Reliability for the Month of June-2023 |  |  |  | Reliability for cumulative period from Apr-23 to June-23
Scheduled Outage 6: Scheduled Outage; UnScheduled Outage 7: UnScheduled Outage; Total 8=6+7: Total | Cumulative | Sum of outage duration of all feeders (in Hrs) | Outage duration of all feeders (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder level in % | Reliability supply of power to consumer in % | Cumulative outage duration of all feeders(in Hrs) for FY 23-24 | Cumulative outage duration per feeder(in Hrs/Fdr) | Cumulative feeder Reliability Index at 11 KV feeder level in % | Cumulative Reliability of supply of power to consumers in %
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 |  | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16
1 | HUBBALLI RURAL | 50 | 50 | 255:02 | 728:11 | 1336:30 | 1485:27 | 2821:57 | 7991:39 | 3076:59 | 61:32 | 92.1613 | 91.4528 | 8719:50 | 174:24 | 92.6816 | 92.0148
2 | DHARWAD RURAL | 99 | 99 | 52:02 | 557:53 | 2402:40 | 3216:33 | 5619:13 | 16417:04 | 5671:15 | 57:17 | 92.1167 | 92.0437 | 16974:57 | 171:28 | 92.4071 | 92.1491
3 | GADAG | 115 | 114 | 549:14 | 1245:50 | 2121:08 | 2758:11 | 4879:19 | 12468:28 | 5428:33 | 47:12 | 94.1071 | 93.4438 | 13714:18 | 119:15 | 95.0356 | 94.5396
4 | RON | 60 | 60 | 174:28 | 416:23 | 1259:58 | 1266:02 | 2526:00 | 6866:37 | 2700:28 | 45:00 | 94.1528 | 93.7489 | 7283:00 | 121:23 | 94.7599 | 94.4422
5 | HAVERI | 211 | 211 | 1929:17 | 5384:30 | 4845:32 | 8939:01 | 13784:33 | 1420.1986 | 15713:50 | 74:28 | 90.9264 | 89.6565 | 1644.5528 | 187:03 | 92.6035 | 91.4351
6 | RANEBENNUR | 213 | 213 | 1057:56 | 3326:19 | 3758:48 | 5160:38 | 8919:26 | 1121.1333 | 9977:22 | 46:51 | 94.184 | 93.4942 | 1259.7299 | 141:56 | 94.2159 | 93.5009
7 | SIRSI | 61 | 61 | 413:26 | 935:50 | 767:41 | 2728:02 | 3495:43 | 8039:54 | 3909:09 | 64:05 | 92.0407 | 91.0994 | 8975:44 | 147:09 | 93.9651 | 93.2627
8 | DANDELI | 28 | 25 | 116:03 | 328:29 | 294:03 | 639:14 | 933:17 | 3448:14 | 1049:20 | 37:29 | 95.3706 | 94.795 | 3776:43 | 134:53 | 94.3612 | 93.8241
9 | KARWAR | 31 | 31 | 366:32 | 1079:06 | 375:30 | 831:50 | 1207:20 | 2383:42 | 1573:52 | 50:46 | 94.5908 | 92.9486 | 3462:48 | 111:42 | 96.4792 | 94.8854
10 | HONNAVAR | 52 | 51 | 766:50 | 1881:44 | 757:18 | 1245:10 | 2002:28 | 4272:12 | 2769:18 | 53:15 | 94.6515 | 92.6034 | 6153:56 | 118:21 | 96.2382 | 94.5813
11 | BELAGAVI RURAL | 153 | 153 | 431:25 | 1431:56 | 3584:12 | 3256:10 | 6840:22 | 21622:51 | 7271:47 | 47:32 | 93.7905 | 93.3989 | 23054:47 | 150:41 | 93.529 | 93.1005
12 | BAILHONGAL | 216 | 215 | 1741:08 | 5382:48 | 4382:11 | 4613:26 | 8995:37 | 1074.5701 | 10736:45 | 49:42 | 94.2158 | 93.0962 | 1298.8535 | 144:19 | 94.5331 | 93.3921
13 | RAMDURG | 95 | 95 | 754:02 | 1574:18 | 1727:10 | 1574:56 | 3302:06 | 11118:03 | 4056:08 | 42:42 | 95.1724 | 94.07 | 12692:21 | 133:36 | 94.6414 | 93.8826
14 | GHATAPRABHA | 185 | 185 | 431:43 | 1339:09 | 1874:11 | 2364:52 | 4239:03 | 14387:44 | 4670:46 | 25:15 | 96.8175 | 96.4934 | 15726:53 | 85:01 | 96.439 | 96.1076
15 | RAIBAG | 181 | 181 | 461:06 | 1045:42 | 5025:10 | 1037:47 | 6062:57 | 17798:58 | 6524:03 | 36:03 | 95.3476 | 94.9938 | 18844:40 | 104:07 | 95.4974 | 95.2329
16 | ATHANI | 209 | 209 | 731:45 | 2526:42 | 5826:41 | 2006:25 | 7833:06 | 19768:28 | 8564:51 | 40:59 | 94.7946 | 94.3083 | 22295:10 | 106:41 | 95.6691 | 95.1156
17 | CHIKKODI | 198 | 198 | 357:05 | 1209:50 | 1954:51 | 1475:05 | 3429:56 | 12774:34 | 3787:01 | 19:08 | 97.594 | 97.3436 | 13984:24 | 70:38 | 97.0459 | 96.7661
18 | VIJAYAPUR | 215 | 215 | 1226:49 | 2082:54 | 2550:52 | 3944:20 | 6495:12 | 20205:13 | 7722:01 | 35:55 | 95.8041 | 95.0116 | 22288:07 | 103:40 | 95.697 | 95.2534
19 | INDI | 292 | 291 | 1828:25 | 4835:40 | 4719:58 | 7284:41 | 12004:39 | 1535.4903 | 13833:04 | 47:22 | 94.29 | 93.4203 | 1736.9764 | 142:46 | 94.2214 | 93.4631
20 | B.BAGEWADI | 155 | 155 | 1048:08 | 2147:04 | 2799:12 | 3686:17 | 6485:29 | 19041:46 | 7533:37 | 48:36 | 94.1886 | 93.2494 | 21188:50 | 136:42 | 94.375 | 93.7407
21 | BAGALKOT | 230 | 229 | 1041:58 | 2603:46 | 4245:19 | 3942:32 | 8187:51 | 1091.2229 | 9229:49 | 40:08 | 95.0556 | 94.4264 | 1199.7132 | 125:11 | 94.7863 | 94.268
22 | JAMAKHANDI | 214 | 214 | 906:01 | 1918:22 | 5661:46 | 1421:10 | 7082:56 | 17683:08 | 7988:57 | 37:20 | 95.4031 | 94.8151 | 19601:30 | 91:36 | 96.2165 | 95.8061
23 | MUDHOL | 219 | 219 | 1359:43 | 2479:24 | 2388:49 | 1518:07 | 3906:56 | 13746:35 | 5266:39 | 24:03 | 97.5222 | 96.6599 | 16225:59 | 74:05 | 97.1259 | 96.6075
* Feeder Reliability Index at 11 KV feeder level=(Total No of Feeders X 24 hrs X No. of days in the Month] - [outage duration of all 11 KV feeders during the month in hrs as in column 8)} x 100 / [ Total No of 11 KV Feeders x 24 hrs x No. of days in the month]
** Reliability of supply of power to consumers ={[ Total no of Feeders x 24 hrs x No .of days in the Month] -[ Sum of outage duration Including outage in higher voltages along with 11 KV outage during the month in hrs in column 9 ]} x 100 /[ Total No of FeedersX24HrsXNo. of days in the month]
General Manager
Technical